MV/LV Substation VI***547Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =469kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.892 | -8.5071
MV/LV Substation VI***554Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =236kVA. | --> | 0.38 | 0 | 0.054093 | 0 | 0 | Constrained,otherwise capacity available =424.2kW. | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9329 | -6.2495
MV/LV Substation VI***568X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =215kVA. | --> | 0.38 | 0 | 0 | 0.42715 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3562 | -6.4495
MV/LV Substation VI***588 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.134 | 3.4 |  | --> | 0.19 | 0 | 0 | 0.20978 | 0 |  | --> | C19 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.5868 | -7.5405
MV/LV Substation VI***589Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | C20 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.7794 | -8.2528
MV/LV Substation VI***590 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.6 |  | --> | 0.0475 | 0 | 0.004446 | 0 | 0 | Constrained,otherwise capacity available =51.2kW. | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0136 | -8.3994
MV/LV Substation VI***593Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0.20361 | 0 |  | --> | C14 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6466 | -7.2496
MV/LV Substation VI***595Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.398 | 14.3 |  | --> | 0.38 | 0 | 0 | 0.4003 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2422 | -7.165
MV/LV Substation VI***625X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex WATLING STREET | Watling Street [T41,T42] | FRANCIS STREET |  | 53.3497 | -6.282
MV/LV Substation VI***643Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =454kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8928 | -8.5027
MV/LV Substation VI***706Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0.014079 | 0.41049 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.7031 | -6.2565
MV/LV Substation VI***708X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0.00741 | 0.41681 | 0 |  | --> | C21 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2865 | -6.363
MV/LV Substation VI***716Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | E64 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0633 | -7.0861
MV/LV Substation VI***726X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0.02964 | 0.5 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8856 | -9.5447
MV/LV Substation VI***771X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2899 | -6.4242
MV/LV Substation VI***781 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 4 |  | --> | 0.19 | 0 | 0 | 0.20775 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.272 | -6.0969
MV/LV Substation VI***795 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E15 ex CLONROCHE | Clonroche [T421,T422] | WEXFORD |  | 52.4629 | -6.837
MV/LV Substation VI***796 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 3.5 |  | --> | 0.0475 | 0 | 0.002964 | 0.052806 | 0 |  | --> | C26 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.0029 | -6.58
MV/LV Substation VI***800 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.12 | 4 |  | --> | 0.19 | 0 | 0.003705 | 0.2118 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2753 | -6.1062
MV/LV Substation VI***809Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8926 | -8.5043
MV/LV Substation VI***810Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8925 | -8.5052
MV/LV Substation VI***828 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0.015561 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.0872 | -7.8491
MV/LV Substation VI***833 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 3.3 |  | --> | 0.38 | 0 | 0.003705 | 0.40438 | 0 |  | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5072 | -9.6758
MV/LV Substation VI***869X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 1.7 |  | --> | 0.095 | 0 | 0.005928 | 0.10704 | 0 |  | --> | E64 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0518 | -7.0855
MV/LV Substation VI***876Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9095 | -6.8481
MV/LV Substation VI***888X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.7 |  | --> | 0.095 | 0 | 0 | 0.1003 | 0 |  | --> | E64 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0668 | -7.069
MV/LV Substation VI***890X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.7 |  | --> | 0.0475 | 0 | 0.011856 | 0.051643 | 0 |  | --> | E64 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0586 | -7.0891
MV/LV Substation VI***909Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =303kVA. | --> | 0.38 | 0 | 0.024453 | 0.41447 | 0 |  | --> | C17 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2459 | -7.0783
MV/LV Substation VI***910Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =336kVA. | --> | 0.38 | 0 | 0.022971 | 0.4096 | 0 |  | --> | C17 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2448 | -7.0734
MV/LV Substation VI***969Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =368kVA. | --> | 0.38 | 0 | 0.00741 | 0.40483 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.513 | -7.1399
MV/LV Substation VI***970Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5141 | -7.1398
MV/LV Substation VI***972 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0.048165 | 0 | 0 | Constrained,otherwise capacity available =203.6kW. | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6328 | -8.3585
MV/LV Substation VI***975 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =153kVA. | --> | 0.19 | 0 | 0.034086 | 0.20701 | 0 |  | --> | C12 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8559 | -8.2751
MV/LV Substation VI***994Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =62kVA. | --> | 0.095 | 0 | 0 | 0.10561 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8592 | -8.5261
MV/LV Substation VI***995 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WATLING STREET | Watling Street [T41,T42] | FRANCIS STREET |  | 53.3462 | -6.2836
MV/LV Substation VO***008 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0.2048 | 0 |  | --> | C18 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6843 | -7.8263
MV/LV Substation VO***012 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =265kVA. | --> | 0.38 | 0 | 0.005928 | 0 | 0 | Constrained,otherwise capacity available =420kW. | --> | E16 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1353 | -7.458
MV/LV Substation VO***034X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =67kVA. | --> | 0.095 | 0 | 0.004446 | 0 | 0 | Constrained,otherwise capacity available =104.9kW. | --> | C21 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0932 | -7.7037
MV/LV Substation VO***054 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex GLEBE | Glebe [T41,T42] | RICHMOND |  | 53.7318 | -7.7859
MV/LV Substation VO***057 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.134 | 9.1 |  | --> | 0.19 | 0 | 0 | 0.20978 | 0 |  | --> | C14 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1133 | -9.1481
MV/LV Substation VO***058Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0.003705 | 0.20569 | 0 |  | --> | C12 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.4788 | -7.2118
MV/LV Substation VO***066 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.498 | 1.9 |  | --> | 0.5985 | 0 | 0.005928 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8575 | -9.2892
MV/LV Substation VO***071 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =363kVA. | --> | 0.38 | 0 | 0 | 0.40558 | 0 |  | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.478 | -8.1565
MV/LV Substation VO***077 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 0.4 |  | --> | 0.19 | 0 | 0.017784 | 0.20569 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1256 | -9.672
MV/LV Substation VO***092 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C40 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3254 | -6.3433
MV/LV Substation VO***104 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.8kW. | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1699 | -8.1366
MV/LV Substation VO***141 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.095 | 0 | 0.015561 | 0.10732 | 0 |  | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6128 | -8.3482
MV/LV Substation VO***148X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0.05179 | 0 |  | --> | C16 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8304 | -6.3915
MV/LV Substation VO***160 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =347kVA. | --> | 0.38 | 0 | 0.008892 | 0.40797 | 0 |  | --> | C16 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0626 | -9.5192
MV/LV Substation VO***160 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.163 | 5.3 |  | --> | 0.19 | 0 | 0 | 0.20554 | 0 |  | --> | C11 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2788 | -8.4582
MV/LV Substation VO***190 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =366kVA. | --> | 0.38 | 0 | 0 | 0.40513 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3452 | -6.3522
MV/LV Substation VO***194 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 2.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.1kW. | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8437 | -9.0059
MV/LV Substation VO***198 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =86kVA. | --> | 0.095 | 0 | 0 | 0.1021 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2686 | -6.3936
MV/LV Substation VO***341X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 1.4 |  | --> | 0.19 | 0 | 0.004446 | 0.20166 | 0 |  | --> | C11 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.0972 | -9.317
MV/LV Substation VO***345X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.363 | 4.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =405.6kW. | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.807 | -7.7737
MV/LV Substation VO***4052 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.14262 | 0.1 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0.20376 | 0 |  | --> | C17 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3429 | -6.4853
MV/LV Substation VO***4094 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | E11 ex MACROOM | Macroom [T422] | MACROOM |  | 51.9114 | -8.7752
MV/LV Substation VO***492Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.3 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8201 | -8.2386
MV/LV Substation VO***515Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =20kVA. | --> | 0.0475 | 0 | 0 | 0.054359 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.2977 | -6.4137
MV/LV Substation VO***521X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.258 | 5.5 |  | --> | 0.38 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =421kW. | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9633 | -7.7319
MV/LV Substation VO***531X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.14764 | 0.1 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0.20495 | 0 |  | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0537 | -6.6976
MV/LV Substation VO***532X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =22kVA. | --> | 0.0475 | 0 | 0 | 0.05408 | 0 |  | --> | C15 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.5173 | -7.1396
MV/LV Substation VO***631X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E16 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8508 | -9.2811
MV/LV Substation VO***654Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 0.4 |  | --> | 0.095 | 0 | 0 | 0.1027 | 0 |  | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.0991 | -7.4743
MV/LV Substation VO***736 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =394kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400.9kW. | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6395 | -8.4368
MV/LV Substation VO***750Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0 | 0.052949 | 0 |  | --> | C11 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2715 | -7.5022
MV/LV Substation VO***792X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =93kVA. | --> | 0.19 | 0 | 0.003705 | 0.21562 | 0 |  | --> | C12 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6246 | -8.1996
MV/LV Substation VO***818 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =143kVA. | --> | 0.19 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =208.5kW. | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.648 | -8.1136
MV/LV Substation VO***824Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1405 | -7.0574
MV/LV Substation VO***826 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.164 | 0.4 |  | --> | 0.19 | 0 | 0.004446 | 0.20539 | 0 |  | --> | E17 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1234 | -7.6766
MV/LV Substation VO***860 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 2.1 |  | --> | 0.19 | 0 | 0.020748 | 0 | 0 | Constrained,otherwise capacity available =203.9kW. | --> | C17 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6561 | -8.6326
MV/LV Substation VO***863Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | E12 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3339 | -7.0935
MV/LV Substation VO***866Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036794 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5489 | -7.3927
MV/LV Substation VO***897X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.095 | 0 | 0.013338 | 0.10195 | 0 |  | --> | C12 ex BRUFF | Bruff [T42,T421] | LIMERICK |  | 52.5219 | -8.3977
MV/LV Substation VO***906Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.5kW. | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9091 | -7.3244
MV/LV Substation VO***936Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =149kVA. | --> | 0.19 | 0 | 0.004446 | 0.2076 | 0 |  | --> | C17 ex VIRGINIA | Virginia [T41,T42] | MEATH HILL |  | 53.8319 | -7.0832
MV/LV Substation VO***939 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.7982 | -6.7319
MV/LV Substation W ***102 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0.050303 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.0891 | -7.7813
MV/LV Substation W ***437X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 11.9 |  | --> | 0.19 | 0 | 0.030381 | 0.20421 | 0 |  | --> | C34 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.278 | -9.0736
MV/LV Substation W ***479Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.43064 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8021 | -6.7505
MV/LV Substation W ***754X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1402 | -8.2607
MV/LV Substation W ***822Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1772 | -6.7979
MV/LV Substation W ***824Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1771 | -6.7979
MV/LV Substation W ***970Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1775 | -6.7964
MV/LV Substation W.***4115 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.139 | -6.6266
MV/LV Substation W/***489 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 5.3 |  | --> | 0.095 | 0 | 0.00741 | 0.10166 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3026 | -8.5199
MV/LV Substation W/***826 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1228 | -7.2039
MV/LV Substation W/***921 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.1 |  | --> | 0.0475 | 0 | 0.005928 | 0.050903 | 0 |  | --> | E12 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1025 | -7.802
MV/LV Substation W+***4181 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C11 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1985 | -6.1369
MV/LV Substation W+***663X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =465kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1733 | -6.7981
MV/LV Substation WA***002 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.063 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =219.8kW. | --> | C17 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3537 | -7.6943
MV/LV Substation WA***005 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.153 | 1.9 |  | --> | 0.19 | 0 | 0.01482 | 0 | 0 | Constrained,otherwise capacity available =207kW. | --> | C16 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8643 | -9.3003
MV/LV Substation WA***007 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =387kVA. | --> | 0.38 | 0 | 0 | 0.40197 | 0 |  | --> | C14 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2837 | -9.0575
MV/LV Substation WA***007 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 2 |  | --> | 0.095 | 0 | 0 | 0.10284 | 0 |  | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 54.0395 | -7.8301
MV/LV Substation WA***013Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0.052228 | 0 |  | --> | E12 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4381 | -6.5453
MV/LV Substation WA***014X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 4.5 |  | --> | 0.38 | 0 | 0 | 0.40931 | 0 |  | --> | C21 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.202 | -6.0978
MV/LV Substation WA***015X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 16.1 |  | --> | 0.19 | 0 | 0 | 0.20045 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3645 | -6.5147
MV/LV Substation WA***015Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 3.1 |  | --> | 0.19 | 0 | 0 | 0.2048 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6145 | -7.2084
MV/LV Substation WA***019 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.043 | 9.1 |  | --> | 0.19 | 0 | 0 | 0.2225 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.9027 | -8.4495
MV/LV Substation WA***024Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.4 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7326 | -7.5649
MV/LV Substation WA***025 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.45 | 9.5 |  | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C11 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7473 | -8.7323
MV/LV Substation WA***025 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.21119 | 0.5 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.895 | -8.5111
MV/LV Substation WA***025Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.4 |  | --> | 0.0475 | 0 | 0.01482 | 0.052949 | 0 |  | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2697 | -6.3977
MV/LV Substation WA***027 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.196 | 1.7 |  | --> | 0.19 | 0 | 0 | 0.20061 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0089 | -6.9919
MV/LV Substation WA***028X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0.051348 | 0 |  | --> | C13 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1588 | -6.7981
MV/LV Substation WA***030 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.332 | 1.6 |  | --> | 0.38 | 0 | 0.006669 | 0 | 0 | Constrained,otherwise capacity available =410.2kW. | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4807 | -8.2787
MV/LV Substation WA***031X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =317kVA. | --> | 0.38 | 0 | 0.005928 | 0.41241 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3078 | -6.3656
MV/LV Substation WA***034Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0.41005 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1388 | -7.0629
MV/LV Substation WA***035Y |  | 10 kV | _ | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0.10299 | 0 |  | --> | C30 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.247 | -7.1417
MV/LV Substation WA***036 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =341kVA. | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2694 | -9.7012
MV/LV Substation WA***037 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.375 | 1.4 |  | --> | 0.38 | 0 | 0 | 0.40378 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.6997 | -8.8963
MV/LV Substation WA***041Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0.001482 | 0.41271 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3481 | -6.5393
MV/LV Substation WA***041Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =348kVA. | --> | 0.38 | 0 | 0.005928 | 0.40782 | 0 |  | --> | C18 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3943 | -6.1239
MV/LV Substation WA***044Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5972 | -6.6386
MV/LV Substation WA***045 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E13 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.5242 | -6.6112
MV/LV Substation WA***046Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =259kVA. | --> | 0.38 | 0 | 0.009633 | 0.42086 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4011 | -6.3862
MV/LV Substation WA***047 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =435kVA. | --> | 0.5985 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.1376 | -8.2722
MV/LV Substation WA***057 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5156 | -6.1246
MV/LV Substation WA***057Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.19 | 0 | 0.026676 | 0.21506 | 0 |  | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8764 | -8.4171
MV/LV Substation WA***059Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =181kVA. | --> | 0.19 | 0 | 0 | 0.20286 | 0 |  | --> | C13 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8588 | -8.3146
MV/LV Substation WA***065X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.357 | 4.5 |  | --> | 0.38 | 0 | 0 | 0.40648 | 0 |  | --> | C19 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1834 | -6.1295
MV/LV Substation WA***067Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C12 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2445 | -7.1643
MV/LV Substation WA***068Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4639 | -6.2201
MV/LV Substation WA***070 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 0.4 |  | --> | 0.095 | 0 | 0 | 0.10373 | 0 |  | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1146 | -9.6894
MV/LV Substation WA***070Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =308kVA. | --> | 0.38 | 0 | 0.014079 | 0.41373 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.349 | -6.5404
MV/LV Substation WA***073X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2539 | -8.2979
MV/LV Substation WA***077X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.3 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3421 | -6.2351
MV/LV Substation WA***079X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.003705 | 0.4676 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2433 | -6.1394
MV/LV Substation WA***080Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.471 | 4.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3962 | -6.1955
MV/LV Substation WA***081 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 2.4 |  | --> | 0.0285 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =36.4kW. | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8673 | -8.9818
MV/LV Substation WA***083Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3218 | -6.3623
MV/LV Substation WA***086X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =133kVA. | --> | 0.19 | 0 | 0 | 0.20993 | 0 |  | --> | E25 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.6231 | -8.8088
MV/LV Substation WA***090X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 2.3 |  | --> | 0.19 | 0 | 0.011856 | 0.20613 | 0 |  | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1023 | -9.1626
MV/LV Substation WA***090Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =418kVA. | --> | 0.5985 | 0 | 0.002223 | 0.5 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3395 | -6.5381
MV/LV Substation WA***094 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C15 ex WATLING STREET | Watling Street [T41,T42] | FRANCIS STREET |  | 53.346 | -6.2845
MV/LV Substation WA***098Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | E16 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8598 | -9.2708
MV/LV Substation WA***099X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2652 | -9.7179
MV/LV Substation WA***099Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4027 | -6.29
MV/LV Substation WA***107 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.1069 | -7.5815
MV/LV Substation WA***110Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.6kW. | --> | C16 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1182 | -7.3113
MV/LV Substation WA***110Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.395 | 0.8 |  | --> | 0.38 | 0 | 0.003705 | 0.40076 | 0 |  | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2498 | -7.0735
MV/LV Substation WA***112 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.373 | 0.9 |  | --> | 0.5985 | 0 | 0.035568 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3068 | -6.3054
MV/LV Substation WA***112X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 0.7 |  | --> | 0.19 | 0 | 0 | 0.20361 | 0 |  | --> | C15 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.643 | -9.4804
MV/LV Substation WA***116X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =17kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.8kW. | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1007 | -7.5699
MV/LV Substation WA***119Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.095 | 0 | 0 | 0.10015 | 0 |  | --> | E30 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2437 | -8.6755
MV/LV Substation WA***125 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.265 | 7.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8971 | -8.4815
MV/LV Substation WA***126 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0 | 0.10402 | 0 |  | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1513 | -10.2412
MV/LV Substation WA***128Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.2kW. | --> | C11 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7589 | -7.8244
MV/LV Substation WA***129X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6546 | -8.107
MV/LV Substation WA***129Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 5.7 |  | --> | 0.38 | 0 | 0.008151 | 0.41564 | 0 |  | --> | C11 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.9926 | -6.398
MV/LV Substation WA***131Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =271kVA. | --> | 0.38 | 0 | 0.018525 | 0.41913 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6517 | -8.6002
MV/LV Substation WA***133 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.2 |  | --> | 0.095 | 0 | 0.03705 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E16 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2983 | -6.9567
MV/LV Substation WA***140X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.052518 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0945 | -8.2271
MV/LV Substation WA***148X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =77kVA. | --> | 0.095 | 0 | 0.004446 | 0.10343 | 0 |  | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7662 | -8.7671
MV/LV Substation WA***150Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 53.1043 | -9.1614
MV/LV Substation WA***163 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =170kVA. | --> | 0.19 | 0 | 0.017043 | 0.2045 | 0 |  | --> | C22 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2319 | -9.4427
MV/LV Substation WA***165Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1557 | -7.2731
MV/LV Substation WA***167 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 3 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1806 | -7.1606
MV/LV Substation WA***168Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0.006669 | 0.051937 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5196 | -6.1062
MV/LV Substation WA***174 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.021 | 3.4 |  | --> | 0.0285 | 0 | 0.003705 | 0.031337 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7311 | -7.5695
MV/LV Substation WA***176 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.026 | 3.4 |  | --> | 0.0285 | 0 | 0 | 0.030601 | 0 |  | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7389 | -7.5659
MV/LV Substation WA***184 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.3 |  | --> | 0.095 | 0 | 0.003705 | 0.1 | 0 |  | --> | C12 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.3745 | -9.303
MV/LV Substation WA***184 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.27 | 4.9 |  | --> | 0.38 | 0 | 0.024453 | 0.41927 | 0 |  | --> | C19 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3774 | -6.1769
MV/LV Substation WA***187Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | C12 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6388 | -8.1733
MV/LV Substation WA***188 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C20 ex KILMEADEN | Kilmeaden [T42] | BUTLERSTOWN |  | 52.2327 | -7.2315
MV/LV Substation WA***188X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5133 | -8.2377
MV/LV Substation WA***189Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =353kVA. | --> | 0.38 | 0 | 0 | 0.40707 | 0 |  | --> | C13 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8775 | -8.4334
MV/LV Substation WA***198 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =198kVA. | --> | 0.19 | 0 | 0 | 0.2003 | 0 |  | --> | C20 ex KILMEADEN | Kilmeaden [T42] | BUTLERSTOWN |  | 52.2292 | -7.2266
MV/LV Substation WA***200 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.066 | 12.2 |  | --> | 0.19 | 0 | 0.082251 | 0.21937 | 0 |  | --> | C20 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9735 | -6.0367
MV/LV Substation WA***202X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0.10045 | 0 |  | --> | E20 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4435 | -7.3715
MV/LV Substation WA***206 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.051 | 5.6 |  | --> | 0.095 | 0 | 0.00741 | 0.10718 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0666 | -6.0619
MV/LV Substation WA***207Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.2kW. | --> | E12 ex CASTLELYONS | Castlelyons [T421,T422] | BARRYMORE |  | 52.0211 | -8.3344
MV/LV Substation WA***217Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =350kVA. | --> | 0.38 | 0 | 0 | 0.40752 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3923 | -6.3756
MV/LV Substation WA***218Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =329kVA. | --> | 0.38 | 0 | 0 | 0.41064 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3926 | -6.3736
MV/LV Substation WA***219 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.246 | 1.8 |  | --> | 0.38 | 0 | 0.011115 | 0.42273 | 0 |  | --> | C13 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6769 | -8.6603
MV/LV Substation WA***220 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.487 | 0.9 |  | --> | 0.5985 | 0 | 0.045201 | 0.5 | 0 |  | --> | C22 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3096 | -6.3069
MV/LV Substation WA***220 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C18 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0886 | -8.4927
MV/LV Substation WA***223X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.9157 | -6.4047
MV/LV Substation WA***227Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0.017784 | 0.051348 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5158 | -7.1014
MV/LV Substation WA***228Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5802 | -6.2282
MV/LV Substation WA***229Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5833 | -6.2338
MV/LV Substation WA***231X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =366kVA. | --> | 0.38 | 0 | 0.011856 | 0.40513 | 0 |  | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5335 | -7.1966
MV/LV Substation WA***231Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0.052806 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5782 | -6.2227
MV/LV Substation WA***246Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0 | 0.2048 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5166 | -8.8513
MV/LV Substation WA***246Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | C16 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.2729 | -8.8882
MV/LV Substation WA***248 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.491 | 8.1 |  | --> | 0.95 | 0 | 0.009633 | 0.5 | 0 |  | --> | C23 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3325 | -6.2441
MV/LV Substation WA***248X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.5kW. | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5094 | -8.2413
MV/LV Substation WA***248Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =78kVA. | --> | 0.095 | 0 | 0 | 0.10329 | 0 |  | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3145 | -8.2225
MV/LV Substation WA***250X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =375kVA. | --> | 0.38 | 0 | 0.002223 | 0 | 0 | Constrained,otherwise capacity available =403.8kW. | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6293 | -8.4455
MV/LV Substation WA***255 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.24 | 2.8 |  | --> | 0.38 | 0 | 0.037791 | 0.42359 | 0 |  | --> | C18 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2977 | -6.1883
MV/LV Substation WA***259 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =389kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.7kW. | --> | C13 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8409 | -9.2926
MV/LV Substation WA***262X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =130kVA. | --> | 0.19 | 0 | 0.001482 | 0.21036 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3842 | -6.1761
MV/LV Substation WA***282 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.435 | 0.9 |  | --> | 0.5985 | 0 | 0.03705 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.309 | -6.303
MV/LV Substation WA***284Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =246kVA. | --> | 0.38 | 0 | 0 | 0.42273 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3927 | -6.3719
MV/LV Substation WA***287 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.19 | 0 | 0.008151 | 0.21506 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8287 | -10.1715
MV/LV Substation WA***287Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1645 | -6.7857
MV/LV Substation WA***298X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.6kW. | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6674 | -8.1285
MV/LV Substation WA***299Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.32 | 4.6 |  | --> | 0.38 | 0 | 0 | 0.41197 | 0 |  | --> | C13 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8937 | -8.3638
MV/LV Substation WA***301X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3396 | -6.3051
MV/LV Substation WA***313 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.423 | 8.1 |  | --> | 0.5985 | 0 | 0.008892 | 0.5 | 0 |  | --> | C23 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3311 | -6.2456
MV/LV Substation WA***314X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.5 |  | --> | 0.95 | 0 | 0.00741 | 0.5 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2589 | -9.079
MV/LV Substation WA***315X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =345kVA. | --> | 0.38 | 0 | 0.00741 | 0.40827 | 0 |  | --> | C14 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3892 | -6.1205
MV/LV Substation WA***326 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C16 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.2725 | -8.8898
MV/LV Substation WA***334 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =273kVA. | --> | 0.38 | 0 | 0 | 0.41884 | 0 |  | --> | C20 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2113 | -6.1123
MV/LV Substation WA***335 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.154 | 4.5 |  | --> | 0.19 | 0 | 0 | 0.20687 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3075 | -6.3357
MV/LV Substation WA***335Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =79kVA. | --> | 0.095 | 0 | 0 | 0.10314 | 0 |  | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2126 | -8.5125
MV/LV Substation WA***341 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0 | 0.052228 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8677 | -8.5465
MV/LV Substation WA***350X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 7.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.7kW. | --> | C18 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8585 | -7.6525
MV/LV Substation WA***352X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.375 | 0.4 |  | --> | 0.38 | 0 | 0 | 0.40378 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2412 | -6.1889
MV/LV Substation WA***353Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 3.5 |  | --> | 0.0475 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =51.8kW. | --> | E12 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4554 | -6.9014
MV/LV Substation WA***356Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0.03705 | 0.4 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6196 | -7.0717
MV/LV Substation WA***367 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | E22 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6276 | -6.4187
MV/LV Substation WA***371Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.23865 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C27 ex ROSBERCON | Rosbercon [T41,T42] | WATERFORD |  | 52.3971 | -6.9481
MV/LV Substation WA***372X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3659 | -6.2485
MV/LV Substation WA***373Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C15 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8298 | -6.2685
MV/LV Substation WA***373Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5819 | -6.1368
MV/LV Substation WA***381Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3929 | -6.3705
MV/LV Substation WA***382 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =174kVA. | --> | 0.19 | 0 | 0 | 0.20391 | 0 |  | --> | E14 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1889 | -7.0809
MV/LV Substation WA***384X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.3 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C02 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3412 | -6.2314
MV/LV Substation WA***385 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =185kVA. | --> | 0.19 | 0 | 0 | 0.20226 | 0 |  | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2359 | -7.139
MV/LV Substation WA***398 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =203.6kW. | --> | E20 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6487 | -8.4491
MV/LV Substation WA***4002 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3321 | -6.2452
MV/LV Substation WA***4015 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4497 | -8.057
MV/LV Substation WA***4016 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4392 | -6.545
MV/LV Substation WA***4022 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =22kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =54.1kW. | --> | E20 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6475 | -8.4488
MV/LV Substation WA***403 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =81kVA. | --> | 0.19 | 0 | 0 | 0.2173 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8272 | -10.1705
MV/LV Substation WA***403 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.6 |  | --> | 0.0475 | 0 | 0.004446 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.465 | -8.2818
MV/LV Substation WA***4035 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E19 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.4962 | -7.1281
MV/LV Substation WA***4036 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1498 | -6.0864
MV/LV Substation WA***4057 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 0.5 |  | --> | 0.19 | 0 | 0 | 0.2048 | 0 |  | --> | E11 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3249 | -8.1036
MV/LV Substation WA***4058 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.5 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E11 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3352 | -8.1132
MV/LV Substation WA***4062 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =490kVA. | --> | 0.5985 | 0 | 0.03705 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2949 | -6.4257
MV/LV Substation WA***406X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | C16 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6071 | -8.2674
MV/LV Substation WA***4075 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 4.4 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8989 | -6.8136
MV/LV Substation WA***408 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.6 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4532 | -8.2103
MV/LV Substation WA***4087 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.7918 | -6.8684
MV/LV Substation WA***408X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =178kVA. | --> | 0.19 | 0 | 0 | 0.20331 | 0 |  | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.344 | -8.2437
MV/LV Substation WA***408X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0.052806 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6182 | -6.5604
MV/LV Substation WA***4093 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0.003705 | 0.40737 | 0 |  | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1437 | -8.9446
MV/LV Substation WA***4098 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.309 | 3 |  | --> | 0.5985 | 0 | 0.040014 | 0.5 | 0 |  | --> | C14 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.3199 | -6.3359
MV/LV Substation WA***4099 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.155 | -7.5218
MV/LV Substation WA***409X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =16kVA. | --> | 0.0475 | 0 | 0 | 0.05491 | 0 |  | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3927 | -8.3313
MV/LV Substation WA***4115 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.195 | 4.6 |  | --> | 0.19 | 0 | 0.00741 | 0.20076 | 0 |  | --> | C31 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8942 | -8.3681
MV/LV Substation WA***412 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =104.2kW. | --> | C11 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.2334 | -7.2215
MV/LV Substation WA***4127 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =368kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2976 | -6.3627
MV/LV Substation WA***4130 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.8 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.281 | -6.2407
MV/LV Substation WA***4140 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | E12 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4628 | -8.9233
MV/LV Substation WA***4140 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 6.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.3558 | -8.8566
MV/LV Substation WA***4142 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.5 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E11 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7019 | -6.9805
MV/LV Substation WA***4147 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =377kVA. | --> | 0.38 | 0 | 0 | 0.40348 | 0 |  | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2422 | -7.1338
MV/LV Substation WA***416 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =171kVA. | --> | 0.19 | 0 | 0 | 0.20436 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7377 | -6.3453
MV/LV Substation WA***4160 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =464kVA. | --> | 0.5985 | 0 | 0.025935 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4071 | -6.1814
MV/LV Substation WA***4161 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =367kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =405kW. | --> | C17 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4039 | -8.5885
MV/LV Substation WA***4162 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =327kVA. | --> | 0.38 | 0 | 0.004446 | 0.41094 | 0 |  | --> | C15 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0625 | -8.811
MV/LV Substation WA***4163 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.8kW. | --> | C14 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7471 | -7.7217
MV/LV Substation WA***4164 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.2 |  | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | C19 ex CASTLETOWNROCHE | Castletownroche [T41] | MALLOW |  | 52.2105 | -8.5015
MV/LV Substation WA***4165 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 3 |  | --> | 0.38 | 0 | 0 | 0.40468 | 0 |  | --> | C11 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.3174 | -6.3374
MV/LV Substation WA***4166 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E23 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.2809 | -7.7375
MV/LV Substation WA***4171 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2877 | -6.3043
MV/LV Substation WA***4176 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =498kVA. | --> | 0.5985 | 0 | 0.053352 | 0.5 | 0 |  | --> | C22 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4036 | -6.1663
MV/LV Substation WA***4183 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C16 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9413 | -9.3908
MV/LV Substation WA***4183 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E30 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2044 | -8.6893
MV/LV Substation WA***4184 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0.05179 | 0 |  | --> | E17 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6267 | -6.8581
MV/LV Substation WA***4184 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =336kVA. | --> | 0.38 | 0 | 0 | 0.4096 | 0 |  | --> | C11 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.1844 | -6.606
MV/LV Substation WA***4185 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 12.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9854 | -6.0788
MV/LV Substation WA***4187 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4073 | -6.1846
MV/LV Substation WA***4195 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 0.8 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C16 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2577 | -7.107
MV/LV Substation WA***4206 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1644 | -6.7859
MV/LV Substation WA***4229 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3412 | -6.239
MV/LV Substation WA***423 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.095 | 0 | 0 | 0.10045 | 0 |  | --> | C12 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8591 | -8.2853
MV/LV Substation WA***4231 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0.00741 | 0.052662 | 0 |  | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1447 | -6.9178
MV/LV Substation WA***4232 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7917 | -8.0312
MV/LV Substation WA***4232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0.40182 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6541 | -8.6184
MV/LV Substation WA***4243 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.6 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C31 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8999 | -8.3684
MV/LV Substation WA***4245 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.4159 | -6.4819
MV/LV Substation WA***4248 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1611 | -8.2689
MV/LV Substation WA***4250 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 53.1194 | -9.1586
MV/LV Substation WA***4251 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3926 | -8.3285
MV/LV Substation WA***4252 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0.020748 | 0 | 0 | Constrained,otherwise capacity available =52.5kW. | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2161 | -6.9229
MV/LV Substation WA***4285 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E19 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6382 | -6.2977
MV/LV Substation WA***4303 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 52.0074 | -8.3241
MV/LV Substation WA***4305 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E19 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6408 | -6.2956
MV/LV Substation WA***431Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E13 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.9193 | -7.6098
MV/LV Substation WA***4326 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 3.9 |  | --> | 0.38 | 0 | 0 | 0.40618 | 0 |  | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9625 | -6.3944
MV/LV Substation WA***4331 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =310kVA. | --> | 0.38 | 0 | 0.1319 | 0.41344 | 0 |  | --> | C19 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1635 | -6.9214
MV/LV Substation WA***4332 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.15339 | 0.5 | 0 |  | --> | C19 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1645 | -6.9239
MV/LV Substation WA***434 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3235 | -6.9669
MV/LV Substation WA***4345 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C17 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6187 | -8.3631
MV/LV Substation WA***4349 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3918 | -6.4957
MV/LV Substation WA***4350 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex WATLING STREET | Watling Street [T41,T42] | FRANCIS STREET |  | 53.3459 | -6.284
MV/LV Substation WA***4371 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4631 | -6.2221
MV/LV Substation WA***4430 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8151 | -8.3722
MV/LV Substation WA***4432 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3762 | -6.3102
MV/LV Substation WA***4447 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8715 | -8.5308
MV/LV Substation WA***4448 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8705 | -8.5321
MV/LV Substation WA***4449 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8706 | -8.5347
MV/LV Substation WA***4467 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 6.4 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4178 | -7.9358
MV/LV Substation WA***449 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =105kVA. | --> | 0.19 | 0 | 0.003705 | 0.21393 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 52.0122 | -8.344
MV/LV Substation WA***450 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0.01482 | 0.053092 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4408 | -6.5102
MV/LV Substation WA***4538 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.8862 | -6.6848
MV/LV Substation WA***453Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 0.8 |  | --> | 0.19 | 0 | 0 | 0.20271 | 0 |  | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.249 | -7.0741
MV/LV Substation WA***457Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | C18 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.976 | -8.1593
MV/LV Substation WA***458Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3466 | -6.4956
MV/LV Substation WA***466Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =379kVA. | --> | 0.38 | 0 | 0 | 0.40318 | 0 |  | --> | C11 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3576 | -6.3718
MV/LV Substation WA***468Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8358 | -6.9371
MV/LV Substation WA***474Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =198kVA. | --> | 0.19 | 0 | 0 | 0.2003 | 0 |  | --> | C19 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6411 | -7.248
MV/LV Substation WA***479 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0.000741 | 0.20628 | 0 |  | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8268 | -6.8987
MV/LV Substation WA***479X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8766 | -7.1888
MV/LV Substation WA***481 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0.05179 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4288 | -6.2275
MV/LV Substation WA***481X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.34 | 1.1 |  | --> | 0.38 | 0 | 0 | 0.40901 | 0 |  | --> | C16 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.6829 | -9.6458
MV/LV Substation WA***482Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.376 | 4.6 |  | --> | 0.38 | 0 | 0 | 0.40363 | 0 |  | --> | C31 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.893 | -8.3708
MV/LV Substation WA***485X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2958 | -6.3554
MV/LV Substation WA***485Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4089 | -6.2877
MV/LV Substation WA***488X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 11.1 |  | --> | 0.95 | 0 | 0.004446 | 0.5 | 0 |  | --> | C12 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3759 | -6.3169
MV/LV Substation WA***496X |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 4.2 |  | --> | 0.02375 | 0 | 0 | 0.028909 | 0 |  | --> | C19 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0773 | -7.0623
MV/LV Substation WA***498 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =305kVA. | --> | 0.38 | 0 | 0.017043 | 0.41417 | 0 |  | --> | C19 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4635 | -6.2241
MV/LV Substation WA***499 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.189 | 1 |  | --> | 0.38 | 0 | 0.018525 | 0.42857 | 0 |  | --> | C11 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3375 | -6.2749
MV/LV Substation WA***505Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.1kW. | --> | C11 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9298 | -6.2232
MV/LV Substation WA***507Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =385kVA. | --> | 0.38 | 0 | 0 | 0.40227 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4522 | -6.1977
MV/LV Substation WA***508X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0.05179 | 0 |  | --> | C19 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.726 | -6.3831
MV/LV Substation WA***508Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =309kVA. | --> | 0.38 | 0 | 0.065949 | 0.41359 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4525 | -6.2004
MV/LV Substation WA***509 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 1.4 |  | --> | 0.0475 | 0 | 0.00741 | 0.05394 | 0 |  | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2593 | -6.4837
MV/LV Substation WA***509Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0 | 0.40363 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.451 | -6.2001
MV/LV Substation WA***510Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.1383 | -8.2768
MV/LV Substation WA***510Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =344kVA. | --> | 0.38 | 0 | 0.065208 | 0.40841 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4506 | -6.202
MV/LV Substation WA***512 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.2 |  | --> | 0.95 | 0 | 0.023712 | 0.5 | 0 |  | --> | C14 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3213 | -6.3301
MV/LV Substation WA***519Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4742 | -6.2327
MV/LV Substation WA***524Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.377 | 0.8 |  | --> | 0.38 | 0 | 0 | 0.40348 | 0 |  | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.248 | -7.072
MV/LV Substation WA***529 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.19 | 0 | 0.005928 | 0 | 0 | Constrained,otherwise capacity available =216.5kW. | --> | C14 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6562 | -8.1121
MV/LV Substation WA***531Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =60kVA. | --> | 0.095 | 0 | 0 | 0.1059 | 0 |  | --> | E14 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8618 | -8.8392
MV/LV Substation WA***534X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3247 | -6.3705
MV/LV Substation WA***536Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =382kVA. | --> | 0.38 | 0 | 0 | 0.40272 | 0 |  | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6749 | -7.9987
MV/LV Substation WA***569 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =294kVA. | --> | 0.38 | 0 | 0.027417 | 0.41578 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2612 | -6.1376
MV/LV Substation WA***570 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =222kVA. | --> | 0.38 | 0 | 0.087438 | 0.42616 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2598 | -6.1339
MV/LV Substation WA***570Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C23 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2766 | -7.4598
MV/LV Substation WA***572 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 3.1 |  | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6324 | -7.2224
MV/LV Substation WA***577X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1534 | -7.1597
MV/LV Substation WA***588 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 2.2 |  | --> | 0.095 | 0 | 0 | 0.10091 | 0 |  | --> | C19 ex CASTLETOWNROCHE | Castletownroche [T41] | MALLOW |  | 52.2154 | -8.4956
MV/LV Substation WA***593X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C18 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0874 | -9.5517
MV/LV Substation WA***595Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1813 | -6.798
MV/LV Substation WA***598 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 3.9 |  | --> | 0.095 | 0 | 0 | 0.10446 | 0 |  | --> | C17 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2943 | -9.0172
MV/LV Substation WA***602 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 3.3 |  | --> | 0.095 | 0 | 0 | 0.1003 | 0 |  | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.468 | -9.5357
MV/LV Substation WA***603Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =117kVA. | --> | 0.19 | 0 | 0.040755 | 0.21223 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1631 | -6.7849
MV/LV Substation WA***604 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =300kVA. | --> | 0.38 | 0 | 0.018525 | 0.41491 | 0 |  | --> | C17 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3774 | -6.2542
MV/LV Substation WA***605 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =267kVA. | --> | 0.38 | 0 | 0.045201 | 0.41971 | 0 |  | --> | C17 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.379 | -6.2524
MV/LV Substation WA***605X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.1 |  | --> | 0.0475 | 0 | 0.008151 | 0.0512 | 0 |  | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.628 | -7.2156
MV/LV Substation WA***609X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =84kVA. | --> | 0.095 | 0 | 0.02223 | 0.1024 | 0 |  | --> | E11 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9025 | -8.6687
MV/LV Substation WA***614Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.016 | 1.3 |  | --> | 0.0475 | 0 | 0.002223 | 0.05491 | 0 |  | --> | C17 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.6842 | -7.2965
MV/LV Substation WA***625X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0.035568 | 0.41651 | 0 |  | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3734 | -6.3912
MV/LV Substation WA***630X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9391 | -7.7576
MV/LV Substation WA***635Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0 | 0.052662 | 0 |  | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.277 | -6.8531
MV/LV Substation WA***636 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =188kVA. | --> | 0.19 | 0 | 0.004446 | 0.20181 | 0 |  | --> | C14 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4068 | -6.4131
MV/LV Substation WA***636Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.011115 | 0.5 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 52.006 | -8.3237
MV/LV Substation WA***637Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0.00741 | 0.05179 | 0 |  | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2917 | -6.8486
MV/LV Substation WA***637Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =476kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 52.0066 | -8.323
MV/LV Substation WA***640 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.4 |  | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | C19 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4288 | -7.9464
MV/LV Substation WA***646X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 5.9 |  | --> | 0.0475 | 0 | 0 | 0.052949 | 0 |  | --> | C20 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5116 | -7.875
MV/LV Substation WA***648X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0 | 0.053235 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6081 | -6.5564
MV/LV Substation WA***660Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.269 | 17.7 |  | --> | 0.38 | 0 | 0.019266 | 0.41942 | 0 |  | --> | E11 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8898 | -8.5965
MV/LV Substation WA***663X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 0.8 |  | --> | 0.38 | 0 | 0.006669 | 0.40528 | 0 |  | --> | C19 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2541 | -7.105
MV/LV Substation WA***676 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.008 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.055993 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0843 | -8.2204
MV/LV Substation WA***682Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =151kVA. | --> | 0.19 | 0 | 0.006669 | 0 | 0 | Constrained,otherwise capacity available =207.3kW. | --> | C11 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.2299 | -7.224
MV/LV Substation WA***683 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.371 | 0.9 |  | --> | 0.5985 | 0 | 0.026676 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3069 | -6.3109
MV/LV Substation WA***688Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E12 ex CASTLELYONS | Castlelyons [T421,T422] | BARRYMORE |  | 52.0317 | -8.3256
MV/LV Substation WA***692Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0.02223 | 0.20376 | 0 |  | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3247 | -7.0984
MV/LV Substation WA***693X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C24 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.5459 | -10.0199
MV/LV Substation WA***699 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.1 |  | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | E11 ex LUMCLOON | Lumcloon [T421,T422] | DALLOW |  | 53.2243 | -7.9533
MV/LV Substation WA***699Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9122 | -8.1769
MV/LV Substation WA***707 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.3kW. | --> | E17 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.1942 | -7.9676
MV/LV Substation WA***708 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.5kW. | --> | E14 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1496 | -7.4462
MV/LV Substation WA***713X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =366kVA. | --> | 0.38 | 0 | 0 | 0.40513 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.834 | -10.1733
MV/LV Substation WA***722Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =164kVA. | --> | 0.19 | 0 | 0 | 0.20539 | 0 |  | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9096 | -8.0737
MV/LV Substation WA***727Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2748 | -7.4972
MV/LV Substation WA***729X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8966 | -8.3782
MV/LV Substation WA***736Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2458 | -6.664
MV/LV Substation WA***737Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2464 | -6.6615
MV/LV Substation WA***738X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.4 |  | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C12 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.1666 | -9.3459
MV/LV Substation WA***738Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2472 | -6.6592
MV/LV Substation WA***744X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =175kVA. | --> | 0.19 | 0 | 0 | 0.20376 | 0 |  | --> | C19 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 53.0245 | -9.3102
MV/LV Substation WA***752X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3374 | -6.2414
MV/LV Substation WA***752Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C19 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9191 | -8.1985
MV/LV Substation WA***754 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0.070765 | 0.1046 | 0 |  | --> | E13 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.5231 | -6.614
MV/LV Substation WA***754Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0.020007 | 0.40363 | 0 |  | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4263 | -8.0053
MV/LV Substation WA***755Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 1.4 |  | --> | 0.38 | 0 | 0.002223 | 0.41256 | 0 |  | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.26 | -6.4798
MV/LV Substation WA***763X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 17.8 |  | --> | 0.19 | 0 | 0.008151 | 0.2 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.649 | -6.229
MV/LV Substation WA***783 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.001 | 8.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =56.9kW. | --> | E16 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7551 | -9.5557
MV/LV Substation WA***787 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3352 | -6.334
MV/LV Substation WA***789 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C19 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.8534 | -6.5554
MV/LV Substation WA***794X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =82kVA. | --> | 0.095 | 0 | 0 | 0.1027 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4458 | -6.3395
MV/LV Substation WA***797 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =55kVA. | --> | 0.095 | 0 | 0.038532 | 0.10661 | 0 |  | --> | C11 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.8261 | -9.1179
MV/LV Substation WA***797X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =395kVA. | --> | 0.38 | 0 | 0 | 0.40076 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.936 | -6.6941
MV/LV Substation WA***801X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =471kVA. | --> | 0.5985 | 0 | 0.03705 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2796 | -6.3618
MV/LV Substation WA***810Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =108kVA. | --> | 0.19 | 0 | 0.011856 | 0.21351 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1628 | -6.7917
MV/LV Substation WA***812 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0.02223 | 0.1046 | 0 |  | --> | C15 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8164 | -8.3808
MV/LV Substation WA***813X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 6.4 |  | --> | 0.19 | 0 | 0 | 0.20331 | 0 |  | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4634 | -7.8038
MV/LV Substation WA***819Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 1.4 |  | --> | 0.19 | 0 | 0 | 0.2045 | 0 |  | --> | E12 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2452 | -6.3309
MV/LV Substation WA***830 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.051348 | 0 |  | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.525 | -6.8889
MV/LV Substation WA***832 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.425 | 3.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3367 | -6.2427
MV/LV Substation WA***832 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.9 |  | --> | 0.95 | 0 | 0.01482 | 0.5 | 0 |  | --> | C15 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3074 | -6.3094
MV/LV Substation WA***836 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.2kW. | --> | C15 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0632 | -8.2767
MV/LV Substation WA***837 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =308kVA. | --> | 0.38 | 0 | 0 | 0.41373 | 0 |  | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8283 | -6.8991
MV/LV Substation WA***837X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0.004446 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | C20 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.8072 | -7.8303
MV/LV Substation WA***845 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 17.8 |  | --> | 0.095 | 0 | 0.005187 | 0.10343 | 0 |  | --> | E22 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6233 | -6.4212
MV/LV Substation WA***863Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 3.8 |  | --> | 0.19 | 0 | 0.002964 | 0.20465 | 0 |  | --> | C14 ex WATERFORD | Waterford [T41,T42] | WATERFORD |  | 52.2697 | -7.1372
MV/LV Substation WA***864 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =197kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200.5kW. | --> | C14 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.662 | -8.0931
MV/LV Substation WA***881X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.14262 | 0.1 | Constrained,otherwise capacity available =308kVA. | --> | 0.38 | 0 | 0.001482 | 0.41373 | 0 |  | --> | C17 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3424 | -6.4771
MV/LV Substation WA***884X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.3 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C02 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3412 | -6.2314
MV/LV Substation WA***899X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4482 | -8.06
MV/LV Substation WA***902Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =133kVA. | --> | 0.19 | 0 | 0.015561 | 0.20993 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1622 | -6.788
MV/LV Substation WA***918X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0.40287 | 0 |  | --> | C20 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.8692 | -9.1545
MV/LV Substation WA***920Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 1.3 |  | --> | 0.19 | 0 | 0.02223 | 0.20745 | 0 |  | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.8306 | -7.9307
MV/LV Substation WA***921Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 5.9 |  | --> | 0.19 | 0 | 0.00741 | 0.20166 | 0 |  | --> | C17 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5113 | -7.8807
MV/LV Substation WA***924 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103kW. | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.518 | -8.1689
MV/LV Substation WA***925Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =83kVA. | --> | 0.095 | 0 | 0 | 0.10255 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6245 | -7.0568
MV/LV Substation WA***927 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0.087438 | 0.4 | 0 |  | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9086 | -8.464
MV/LV Substation WA***932 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0.002223 | 0.05179 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8553 | -8.5431
MV/LV Substation WA***934Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.262 | 1.8 |  | --> | 0.38 | 0 | 0 | 0.41637 | 0 |  | --> | C14 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6781 | -8.6391
MV/LV Substation WA***934Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C18 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.1535 | -6.7089
MV/LV Substation WA***935 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7929 | -8.7702
MV/LV Substation WA***937 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2312 | -8.6633
MV/LV Substation WA***938 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.145 | 1.3 |  | --> | 0.19 | 0 | 0.006669 | 0.20818 | 0 |  | --> | C16 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.6811 | -7.2963
MV/LV Substation WA***939 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =294kVA. | --> | 0.38 | 0 | 0.005187 | 0 | 0 | Constrained,otherwise capacity available =415.8kW. | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.682 | -6.2944
MV/LV Substation WA***942X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =357kVA. | --> | 0.38 | 0 | 0 | 0.40648 | 0 |  | --> | E12 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6267 | -9.2213
MV/LV Substation WA***953X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C19 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9287 | -8.1953
MV/LV Substation WA***954 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8584 | -8.9953
MV/LV Substation WA***957Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8316 | -8.5805
MV/LV Substation WA***958X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =179kVA. | --> | 0.19 | 0 | 0 | 0.20316 | 0 |  | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6231 | -8.8994
MV/LV Substation WA***976 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =291kVA. | --> | 0.38 | 0 | 0.010374 | 0.41622 | 0 |  | --> | C16 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2829 | -6.3646
MV/LV Substation WA***978X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0 | 0.40737 | 0 |  | --> | C15 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8506 | -8.2897
MV/LV Substation WA***981X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 14.3 |  | --> | 0.19 | 0 | 0.00741 | 0.20181 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2291 | -7.1452
MV/LV Substation WA***990X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0 | 0.40916 | 0 |  | --> | C15 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.849 | -8.2985
MV/LV Substation WA***991Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 5.9 |  | --> | 0.19 | 0 | 0.008151 | 0.2045 | 0 |  | --> | C20 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.512 | -7.8751
MV/LV Substation WA***992Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6252 | -6.6104
MV/LV Substation WA***995X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1011 | -8.0088
MV/LV Substation WC***082X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 4.5 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1795 | -6.0935
MV/LV Substation WC***4357 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 8.2 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C13 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2635 | -7.1028
MV/LV Substation WD***224X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3378 | -7.2423
MV/LV Substation WE***001 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.6 |  | --> | 0.5985 | 0 | 0.013338 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5003 | -8.196
MV/LV Substation WE***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =193kVA. | --> | 0.5985 | 0 | 0.002964 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C23 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0334 | -7.2949
MV/LV Substation WE***003Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =128kVA. | --> | 0.19 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =210.6kW. | --> | E20 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1685 | -6.5408
MV/LV Substation WE***004 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.446 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7976 | -9.5125
MV/LV Substation WE***004 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.19 | 0 | 0.003705 | 0.2229 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5128 | -8.8593
MV/LV Substation WE***005 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 2.8 |  | --> | 0.19 | 0 | 0.011115 | 0.21022 | 0 |  | --> | E14 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3407 | -7.6203
MV/LV Substation WE***005 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =61kVA. | --> | 0.095 | 0 | 0.00741 | 0 | 0 | Constrained,otherwise capacity available =105.8kW. | --> | E16 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1401 | -7.454
MV/LV Substation WE***009 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.036794 | 0 | Constrained,otherwise capacity available =55kVA. | --> | 0.19 | 0 | 0.012597 | 0.22087 | 0 |  | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5455 | -7.3953
MV/LV Substation WE***009Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3568 | -6.447
MV/LV Substation WE***012 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.279 | 0.9 |  | --> | 0.5985 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C16 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3528 | -7.6978
MV/LV Substation WE***014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 2.3 |  | --> | 0.38 | 0 | 0.004446 | 0.41049 | 0 |  | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2736 | -9.7143
MV/LV Substation WE***015 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.19 | 0 | 0.008892 | 0.21478 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9401 | -6.7058
MV/LV Substation WE***017Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =245kVA. | --> | 0.38 | 0 | 0.028158 | 0.42288 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6101 | -6.1956
MV/LV Substation WE***018 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.352 | 7.8 |  | --> | 0.38 | 0 | 0.004446 | 0.40722 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7965 | -9.5382
MV/LV Substation WE***018 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.177 | 1.3 |  | --> | 0.19 | 0 | 0.002223 | 0.20346 | 0 |  | --> | C17 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7617 | -8.4808
MV/LV Substation WE***018 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.341 | 8.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3278 | -6.2436
MV/LV Substation WE***020 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.095 | 4.3 |  | --> | 0.38 | 0 | 0.040014 | 0.44378 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2701 | -6.1741
MV/LV Substation WE***021 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =294kVA. | --> | 0.38 | 0 | 0.017784 | 0.41578 | 0 |  | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6218 | -8.9007
MV/LV Substation WE***022 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =68kVA. | --> | 0.095 | 0 | 0.016302 | 0 | 0 | Constrained,otherwise capacity available =104.7kW. | --> | C19 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.848 | -9.3139
MV/LV Substation WE***025 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 1.6 |  | --> | 0.38 | 0 | 0.00741 | 0 | 0 | Constrained,otherwise capacity available =415.6kW. | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4757 | -8.2981
MV/LV Substation WE***026Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =412kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8939 | -8.4973
MV/LV Substation WE***027Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 6 |  | --> | 0.38 | 0 | 0.002964 | 0.41403 | 0 |  | --> | C12 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8863 | -8.4625
MV/LV Substation WE***030 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =264kVA. | --> | 0.38 | 0 | 0.002964 | 0.42014 | 0 |  | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.716 | -6.3583
MV/LV Substation WE***036Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0.004446 | 0.0512 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3042 | -6.4801
MV/LV Substation WE***038 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 4.4 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E13 ex CRANE | Crane [T122] | CRANE |  | 52.4268 | -6.3778
MV/LV Substation WE***041 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 0.6 |  | --> | 0.38 | 0 | 0.005928 | 0 | 0 | Constrained,otherwise capacity available =408.6kW. | --> | C16 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3543 | -7.7113
MV/LV Substation WE***044 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.15247 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.18525 | 0.5 | 0 |  | --> | C14 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2776 | -6.2431
MV/LV Substation WE***044X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =184kVA. | --> | 0.19 | 0 | 0 | 0.20241 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.6189 | -8.9144
MV/LV Substation WE***045X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.365 | 4.6 |  | --> | 0.38 | 0 | 0 | 0.40528 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2955 | -6.1447
MV/LV Substation WE***046Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0.01482 | 0.20495 | 0 |  | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4076 | -7.9829
MV/LV Substation WE***048 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 3 |  | --> | 0.095 | 0 | 0.00741 | 0.1024 | 0 |  | --> | C24 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6733 | -6.311
MV/LV Substation WE***052Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8941 | -8.3612
MV/LV Substation WE***056X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.5985 | 0 | 0.0741 | 0.5 | 0 |  | --> | C18 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6714 | -6.296
MV/LV Substation WE***059 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 9.5 |  | --> | 0.38 | 0 | 0.030381 | 0.40975 | 0 |  | --> | C17 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7672 | -8.6639
MV/LV Substation WE***059X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 17.7 |  | --> | 0.19 | 0 | 0.020007 | 0.2076 | 0 |  | --> | E11 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8869 | -8.6187
MV/LV Substation WE***061X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0 | 0.20346 | 0 |  | --> | C22 ex ROCHES STREET | Roches Street [T41,T42] | LIMERICK |  | 52.6666 | -8.6311
MV/LV Substation WE***063 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =219kVA. | --> | 0.38 | 0 | 0.01482 | 0.42659 | 0 |  | --> | C12 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3853 | -6.3097
MV/LV Substation WE***077Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036794 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5488 | -7.3966
MV/LV Substation WE***085X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5158 | -8.8641
MV/LV Substation WE***089X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.396 | 9.1 |  | --> | 0.38 | 0 | 0 | 0.40061 | 0 |  | --> | E19 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1193 | -9.13
MV/LV Substation WE***092Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3916 | -6.384
MV/LV Substation WE***093Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3901 | -6.3859
MV/LV Substation WE***095Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =379kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =403.2kW. | --> | C19 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0888 | -7.6227
MV/LV Substation WE***097Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.9 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2493 | -6.9696
MV/LV Substation WE***099 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 2.2 |  | --> | 0.19 | 0 | 0.036309 | 0.20406 | 0 |  | --> | C17 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.321 | -8.2186
MV/LV Substation WE***101Z |  | 10 kV | _ | LV | 25 kVA :Kiosk Substation | 0.025 | --> | 0.025 | 0 | 0 |  | --> | 0.02375 | 0 | 0 |  | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3891 | -6.3902
MV/LV Substation WE***104Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =243kVA. | --> | 0.38 | 0 | 0.018525 | 0.42316 | 0 |  | --> | C19 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.399 | -6.1648
MV/LV Substation WE***110 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =442kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3317 | -6.3976
MV/LV Substation WE***113 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C17 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7118 | -8.8886
MV/LV Substation WE***114 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 4.4 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E11 ex CRANE | Crane [T122] | CRANE |  | 52.5199 | -6.5572
MV/LV Substation WE***120 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =365kVA. | --> | 0.38 | 0 | 0.01482 | 0.40528 | 0 |  | --> | C11 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6488 | -8.6448
MV/LV Substation WE***123X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.267 | 1 |  | --> | 0.38 | 0 | 0 | 0.41971 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3372 | -6.283
MV/LV Substation WE***123Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =286kVA. | --> | 0.38 | 0 | 0.036309 | 0.41695 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6093 | -6.1987
MV/LV Substation WE***125X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =451kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2488 | -6.1447
MV/LV Substation WE***128Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0 | 0.2048 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8859 | -8.5877
MV/LV Substation WE***152 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.284 | 2.9 |  | --> | 0.38 | 0 | 0.04446 | 0.41724 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.276 | -6.2276
MV/LV Substation WE***153 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =263kVA. | --> | 0.38 | 0 | 0 | 0.42029 | 0 |  | --> | C12 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8903 | -8.535
MV/LV Substation WE***157 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =335kVA. | --> | 0.38 | 0 | 0.003705 | 0.40975 | 0 |  | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2721 | -9.6972
MV/LV Substation WE***162 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.38 | 0 | 0.017784 | 0.43208 | 0 |  | --> | C20 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8789 | -8.5215
MV/LV Substation WE***168 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 2.9 |  | --> | 0.38 | 0 | 0.002223 | 0.41417 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.278 | -6.2256
MV/LV Substation WE***169X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3294 | -6.4919
MV/LV Substation WE***170X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3294 | -6.4929
MV/LV Substation WE***171X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3288 | -6.4922
MV/LV Substation WE***172X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3282 | -6.493
MV/LV Substation WE***177 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 2.9 |  | --> | 0.38 | 0 | 0.02223 | 0.4099 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2804 | -6.2258
MV/LV Substation WE***178Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.39 | -6.3894
MV/LV Substation WE***185X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 18.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3445 | -6.2691
MV/LV Substation WE***188Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0.00741 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.326 | -6.3628
MV/LV Substation WE***192 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.205 | 9.1 |  | --> | 0.38 | 0 | 0.002223 | 0.42857 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.9022 | -8.4653
MV/LV Substation WE***196Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =390kVA. | --> | 0.38 | 0 | 0 | 0.40151 | 0 |  | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7146 | -6.3535
MV/LV Substation WE***201 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =353kVA. | --> | 0.38 | 0 | 0 | 0.40707 | 0 |  | --> | C15 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8494 | -8.2975
MV/LV Substation WE***201Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8012 | -9.5201
MV/LV Substation WE***202 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.128 | 0.3 |  | --> | 0.19 | 0 | 0.003705 | 0.21065 | 0 |  | --> | C12 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3945 | -6.2465
MV/LV Substation WE***202X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C23 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4022 | -6.2278
MV/LV Substation WE***204 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.112 | 19.8 |  | --> | 0.19 | 0 | 0.018525 | 0.21294 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2786 | -6.239
MV/LV Substation WE***211Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9243 | -8.487
MV/LV Substation WE***211Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0 | 0.20421 | 0 |  | --> | C17 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1774 | -6.8028
MV/LV Substation WE***214 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.355 | 4 |  | --> | 0.95 | 0 | 0.036309 | 0.5 | 0 |  | --> | C18 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3557 | -6.2666
MV/LV Substation WE***216 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =281kVA. | --> | 0.38 | 0 | 0.014079 | 0.41768 | 0 |  | --> | C18 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3989 | -6.1295
MV/LV Substation WE***221X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0.00741 | 0.41197 | 0 |  | --> | C13 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3375 | -6.3448
MV/LV Substation WE***222Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 13.5 |  | --> | 0.38 | 0 | 0.003705 | 0.40856 | 0 |  | --> | C17 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8504 | -8.9876
MV/LV Substation WE***225 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 1.8 |  | --> | 0.095 | 0 | 0.002964 | 0.10373 | 0 |  | --> | C12 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6628 | -8.6472
MV/LV Substation WE***240X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.119 | 1.1 |  | --> | 0.38 | 0 | 0.017043 | 0.44052 | 0 |  | --> | C16 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.6832 | -8.6024
MV/LV Substation WE***242Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4056 | -7.9837
MV/LV Substation WE***245X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3456 | -6.2579
MV/LV Substation WE***247X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =166kVA. | --> | 0.19 | 0 | 0 | 0.2051 | 0 |  | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5136 | -8.8612
MV/LV Substation WE***249X |  | 10 kV | _ | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0.039 | 0.8 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C17 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.7981 | -9.3399
MV/LV Substation WE***256X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =493kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2697 | -8.4739
MV/LV Substation WE***270X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7502 | -8.7714
MV/LV Substation WE***271 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0.002964 | 0.21079 | 0 |  | --> | C18 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2818 | -9.0263
MV/LV Substation WE***273Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =253kVA. | --> | 0.38 | 0 | 0 | 0.42173 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3487 | -6.3452
MV/LV Substation WE***274Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3487 | -6.3452
MV/LV Substation WE***293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 6 |  | --> | 0.38 | 0 | 0.002223 | 0.41608 | 0 |  | --> | C20 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3828 | -6.3186
MV/LV Substation WE***301Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.395 | 1 |  | --> | 0.38 | 0 | 0 | 0.40076 | 0 |  | --> | E11 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7149 | -7.8119
MV/LV Substation WE***302 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =308kVA. | --> | 0.38 | 0 | 0.005928 | 0.41373 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4003 | -6.3696
MV/LV Substation WE***305X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8777 | -8.396
MV/LV Substation WE***313 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8926 | -9.5472
MV/LV Substation WE***327Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3917 | -6.384
MV/LV Substation WE***336Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =294kVA. | --> | 0.38 | 0 | 0.027417 | 0.41578 | 0 |  | --> | C15 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8192 | -8.4042
MV/LV Substation WE***347Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =279kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =418kW. | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0955 | -7.6319
MV/LV Substation WE***350Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.456 | 14.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2489 | -7.1636
MV/LV Substation WE***350Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =302kVA. | --> | 0.38 | 0 | 0.032604 | 0.41461 | 0 |  | --> | C11 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5264 | -6.1589
MV/LV Substation WE***351Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 14.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2492 | -7.1625
MV/LV Substation WE***355X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15247 | 0.2 | Constrained,otherwise capacity available =368kVA. | --> | 0.38 | 0 | 0 | 0.40483 | 0 |  | --> | C14 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2754 | -6.2421
MV/LV Substation WE***356Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.036794 | 0 | Constrained,otherwise capacity available =144kVA. | --> | 0.19 | 0 | 0.002964 | 0.20833 | 0 |  | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5485 | -7.3926
MV/LV Substation WE***361Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =307kVA. | --> | 0.38 | 0 | 0.009633 | 0.41388 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1782 | -6.7808
MV/LV Substation WE***368 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1392 | -7.1818
MV/LV Substation WE***373 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.4 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2704 | -6.423
MV/LV Substation WE***382Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =327kVA. | --> | 0.38 | 0 | 0 | 0.41094 | 0 |  | --> | C18 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3461 | -6.3988
MV/LV Substation WE***383 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C22 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2295 | -6.6168
MV/LV Substation WE***383 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.9 |  | --> | 0.5985 | 0 | 0.064467 | 0.5 | 0 |  | --> | C33 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2611 | -9.1195
MV/LV Substation WE***384X |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0.017 | 7.9 |  | --> | 0.02375 | 0 | 0 | 0.026187 | 0 |  | --> | C17 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7222 | -9.0275
MV/LV Substation WE***385Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =275kVA. | --> | 0.38 | 0 | 0.028158 | 0.41855 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6744 | -7.2554
MV/LV Substation WE***387X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =169kVA. | --> | 0.19 | 0 | 0 | 0.20465 | 0 |  | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6907 | -8.7551
MV/LV Substation WE***398Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5522 | -6.3626
MV/LV Substation WE***4004 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.4 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7098 | -8.8956
MV/LV Substation WE***4012 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5807 | -6.3054
MV/LV Substation WE***4019 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5215 | -8.8823
MV/LV Substation WE***4031 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5764 | -6.31
MV/LV Substation WE***4033 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7132 | -8.8926
MV/LV Substation WE***4037 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3102 | -6.3578
MV/LV Substation WE***4052 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.095 | 0 | 0.00741 | 0.10195 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5189 | -8.876
MV/LV Substation WE***4078 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2963 | -6.373
MV/LV Substation WE***407Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3923 | -6.3842
MV/LV Substation WE***409 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =301kVA. | --> | 0.38 | 0 | 0.006669 | 0.41476 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.886 | -8.6151
MV/LV Substation WE***409X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =110kVA. | --> | 0.19 | 0 | 0.04446 | 0.21322 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.7031 | -6.2599
MV/LV Substation WE***4100 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 4.3 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2732 | -6.1736
MV/LV Substation WE***411Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3567 | -6.4903
MV/LV Substation WE***4123 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 16.1 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3419 | -6.5379
MV/LV Substation WE***4124 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 14.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2496 | -7.1628
MV/LV Substation WE***4134 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =384kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =402.4kW. | --> | C14 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6585 | -8.1159
MV/LV Substation WE***4135 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =349kVA. | --> | 0.38 | 0 | 0 | 0.40767 | 0 |  | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3823 | -6.4182
MV/LV Substation WE***4136 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3557 | -6.2667
MV/LV Substation WE***415 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =222kVA. | --> | 0.38 | 0 | 0.002964 | 0.42616 | 0 |  | --> | C14 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4093 | -6.3956
MV/LV Substation WE***4150 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =343kVA. | --> | 0.5985 | 0 | 0.12004 | 0.5 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3668 | -6.5222
MV/LV Substation WE***4158 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1401 | -8.9239
MV/LV Substation WE***415Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =398kVA. | --> | 0.38 | 0 | 0 | 0.4003 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5074 | -8.874
MV/LV Substation WE***4162 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.1541 | -7.4242
MV/LV Substation WE***4162 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.5 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2967 | -6.3259
MV/LV Substation WE***416Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =370kVA. | --> | 0.38 | 0 | 0.00741 | 0.40453 | 0 |  | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8214 | -6.8946
MV/LV Substation WE***4178 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 14.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.282 | -6.372
MV/LV Substation WE***4179 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.408 | -6.1664
MV/LV Substation WE***417Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0 | 0.40737 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8848 | -8.5805
MV/LV Substation WE***4180 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4083 | -6.1651
MV/LV Substation WE***4183 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 11.9 |  | --> | 0.19 | 0 | 0 | 0.20346 | 0 |  | --> | C34 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2772 | -9.0754
MV/LV Substation WE***418Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =398kVA. | --> | 0.38 | 0 | 0 | 0.4003 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8859 | -8.581
MV/LV Substation WE***418Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.393 | 1.3 |  | --> | 0.38 | 0 | 0 | 0.40106 | 0 |  | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7743 | -8.1029
MV/LV Substation WE***4193 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0.40182 | 0 |  | --> | E16 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5187 | -6.4085
MV/LV Substation WE***4203 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 2.2 |  | --> | 0.38 | 0 | 0 | 0.40871 | 0 |  | --> | C17 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3189 | -8.2222
MV/LV Substation WE***420Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =341kVA. | --> | 0.38 | 0 | 0 | 0.40886 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8841 | -8.5827
MV/LV Substation WE***421Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3533 | -6.4936
MV/LV Substation WE***4243 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.052518 | 0 |  | --> | C21 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7412 | -8.4002
MV/LV Substation WE***425Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WATERFORD | Waterford [T41,T42] | WATERFORD |  | 52.2612 | -7.1167
MV/LV Substation WE***4275 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 17.7 |  | --> | 0.38 | 0 | 0 | 0.40588 | 0 |  | --> | E18 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8867 | -8.6086
MV/LV Substation WE***4288 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 11 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C14 ex CLOON | Cloon [T42,T421] | CLOON |  | 53.4784 | -8.8306
MV/LV Substation WE***4296 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.057798 | 0.5 | 0 |  | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.474 | -6.2451
MV/LV Substation WE***4302 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =360kVA. | --> | 0.38 | 0 | 0.003705 | 0.40603 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3653 | -6.5255
MV/LV Substation WE***431 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C17 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.642 | -7.2687
MV/LV Substation WE***434 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.131 | 0.9 |  | --> | 0.19 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =210.2kW. | --> | E15 ex CASTLETOWNBERE | Castletownbere [T421] | BALLYLICKY |  | 51.6512 | -9.9147
MV/LV Substation WE***436 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C17 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6419 | -7.267
MV/LV Substation WE***4361 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | E16 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9272 | -8.7444
MV/LV Substation WE***4381 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 14.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.249 | -7.1637
MV/LV Substation WE***4392 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 14.3 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2481 | -7.1633
MV/LV Substation WE***4392 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036794 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5552 | -7.4084
MV/LV Substation WE***4404 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 17.7 |  | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | E18 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8885 | -8.5995
MV/LV Substation WE***4421 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.4987 | -6.455
MV/LV Substation WE***4442 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 17.7 |  | --> | 0.19 | 0 | 0 | 0.2045 | 0 |  | --> | E11 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8876 | -8.6173
MV/LV Substation WE***4464 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.656 | -6.4235
MV/LV Substation WE***4465 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6567 | -6.423
MV/LV Substation WE***454Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5263 | -6.3025
MV/LV Substation WE***455X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =311kVA. | --> | 0.38 | 0 | 0.004446 | 0.41329 | 0 |  | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3521 | -6.3565
MV/LV Substation WE***468Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0.018525 | 0.41666 | 0 |  | --> | C15 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8198 | -8.3984
MV/LV Substation WE***471 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =71kVA. | --> | 0.095 | 0 | 0.005928 | 0.10431 | 0 |  | --> | C17 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6422 | -7.2658
MV/LV Substation WE***478Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3895 | -6.3872
MV/LV Substation WE***480 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 7.8 |  | --> | 0.0475 | 0 | 0 | 0.052228 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8022 | -9.5356
MV/LV Substation WE***480 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =313kVA. | --> | 0.38 | 0 | 0.01482 | 0.413 | 0 |  | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8212 | -6.8964
MV/LV Substation WE***481 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8061 | -9.5397
MV/LV Substation WE***485 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.106 | 1.3 |  | --> | 0.19 | 0 | 0.00741 | 0.21379 | 0 |  | --> | C26 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4902 | -10.0192
MV/LV Substation WE***489X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.7 |  | --> | 0.0475 | 0 | 0 | 0.052949 | 0 |  | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.8112 | -6.9151
MV/LV Substation WE***494Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.146 | -7.1824
MV/LV Substation WE***495X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =353kVA. | --> | 0.38 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =402.4kW. | --> | C14 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6804 | -6.276
MV/LV Substation WE***500X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0.10078 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3224 | -6.3694
MV/LV Substation WE***500X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0.003705 | 0.20628 | 0 |  | --> | C12 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1618 | -7.1674
MV/LV Substation WE***500Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =84kVA. | --> | 0.19 | 0 | 0.034086 | 0.21688 | 0 |  | --> | C15 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3572 | -6.4716
MV/LV Substation WE***503Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0.00741 | 0.20406 | 0 |  | --> | C17 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9133 | -8.1799
MV/LV Substation WE***508X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.133 | 4.4 |  | --> | 0.19 | 0 | 0 | 0.20993 | 0 |  | --> | E11 ex CRANE | Crane [T122] | CRANE |  | 52.521 | -6.5584
MV/LV Substation WE***509 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =317kVA. | --> | 0.38 | 0 | 0.031122 | 0.41241 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8302 | -8.9766
MV/LV Substation WE***509X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0.02223 | 0.40916 | 0 |  | --> | C17 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8619 | -8.4339
MV/LV Substation WE***515X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3798 | -6.4427
MV/LV Substation WE***516X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =379kVA. | --> | 0.38 | 0 | 0 | 0.40318 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3222 | -6.3686
MV/LV Substation WE***521Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =172kVA. | --> | 0.19 | 0 | 0.03705 | 0.20421 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6762 | -7.2544
MV/LV Substation WE***523X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =321kVA. | --> | 0.5985 | 0 | 0.027417 | 0.5 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3223 | -6.4192
MV/LV Substation WE***523Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =244kVA. | --> | 0.38 | 0 | 0 | 0.42302 | 0 |  | --> | C16 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8738 | -8.5105
MV/LV Substation WE***533 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0.02223 | 0.5 | 0 |  | --> | C16 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7135 | -8.8916
MV/LV Substation WE***545X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 7.8 |  | --> | 0.19 | 0 | 0 | 0.20241 | 0 |  | --> | C14 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8128 | -9.5633
MV/LV Substation WE***546 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0.019266 | 0.0538 | 0 |  | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.7978 | -8.2768
MV/LV Substation WE***550 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7092 | -8.8935
MV/LV Substation WE***552X |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =17kVA. | --> | 0.02375 | 0 | 0 | 0.026187 | 0 |  | --> | C12 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3689 | -6.3798
MV/LV Substation WE***555Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =321kVA. | --> | 0.38 | 0 | 0.011115 | 0.41182 | 0 |  | --> | C18 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8697 | -8.4302
MV/LV Substation WE***556 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.26 | 2.1 |  | --> | 0.38 | 0 | 0.012597 | 0 | 0 | Constrained,otherwise capacity available =420.7kW. | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9961 | -7.5174
MV/LV Substation WE***562Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.288 | 3.1 |  | --> | 0.38 | 0 | 0.003705 | 0.41666 | 0 |  | --> | C14 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5132 | -6.5763
MV/LV Substation WE***563Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =164kVA. | --> | 0.19 | 0 | 0.013338 | 0.20539 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8867 | -8.6146
MV/LV Substation WE***567X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =323kVA. | --> | 0.38 | 0 | 0 | 0.41153 | 0 |  | --> | C13 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3362 | -6.3424
MV/LV Substation WE***568 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | E18 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8798 | -8.7632
MV/LV Substation WE***569Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =81kVA. | --> | 0.19 | 0 | 0.021489 | 0.2173 | 0 |  | --> | C15 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3561 | -6.4717
MV/LV Substation WE***570 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.71 | -8.8932
MV/LV Substation WE***570Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =110kVA. | --> | 0.19 | 0 | 0.025935 | 0.21322 | 0 |  | --> | C15 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.355 | -6.4736
MV/LV Substation WE***576Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 12.2 |  | --> | 0.38 | 0 | 0.003705 | 0.40287 | 0 |  | --> | C22 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.982 | -6.0451
MV/LV Substation WE***582 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | E11 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7653 | -9.8067
MV/LV Substation WE***590Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =113kVA. | --> | 0.19 | 0 | 0.020007 | 0.2128 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6723 | -7.2564
MV/LV Substation WE***596 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.271 | 4.5 |  | --> | 0.38 | 0 | 0.020007 | 0.41913 | 0 |  | --> | C20 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2875 | -6.3179
MV/LV Substation WE***597X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.5 |  | --> | 0.0475 | 0 | 0 | 0.052373 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9777 | -10.0842
MV/LV Substation WE***597Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =84kVA. | --> | 0.095 | 0 | 0 | 0.1024 | 0 |  | --> | C12 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3691 | -6.3777
MV/LV Substation WE***598Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.108 | 0.9 |  | --> | 0.19 | 0 | 0.004446 | 0 | 0 | Constrained,otherwise capacity available =213.5kW. | --> | E15 ex CASTLETOWNBERE | Castletownbere [T421] | BALLYLICKY |  | 51.6484 | -9.9151
MV/LV Substation WE***612X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104kW. | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0228 | -7.287
MV/LV Substation WE***630X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 12.2 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C23 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9642 | -6.099
MV/LV Substation WE***631 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.276 | 1.5 |  | --> | 0.38 | 0 | 0.050388 | 0.4184 | 0 |  | --> | C21 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2766 | -6.1893
MV/LV Substation WE***632X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 17.7 |  | --> | 0.19 | 0 | 0.016302 | 0.20672 | 0 |  | --> | E11 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8873 | -8.6211
MV/LV Substation WE***638X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =317kVA. | --> | 0.38 | 0 | 0.00741 | 0.41241 | 0 |  | --> | C14 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8946 | -8.504
MV/LV Substation WE***644Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =193kVA. | --> | 0.19 | 0 | 0 | 0.20106 | 0 |  | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3499 | -6.4923
MV/LV Substation WE***645Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0.002964 | 0.20495 | 0 |  | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2131 | -6.6868
MV/LV Substation WE***647X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 17.7 |  | --> | 0.38 | 0 | 0.022971 | 0.41256 | 0 |  | --> | E13 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8818 | -8.6221
MV/LV Substation WE***647X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0.008151 | 0.4 | 0 |  | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1072 | -9.7902
MV/LV Substation WE***654X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =278kVA. | --> | 0.38 | 0 | 0.012597 | 0.41811 | 0 |  | --> | C22 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8733 | -8.5024
MV/LV Substation WE***665 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =118kVA. | --> | 0.19 | 0 | 0 | 0.21208 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.374 | -6.44
MV/LV Substation WE***666Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.1 |  | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C16 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3508 | -6.4892
MV/LV Substation WE***670Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8853 | -8.5824
MV/LV Substation WE***671 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.201 | 18.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C46 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3453 | -6.2672
MV/LV Substation WE***683X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =355kVA. | --> | 0.38 | 0 | 0.003705 | 0.40212 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5286 | -6.303
MV/LV Substation WE***688Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.869 | -8.4923
MV/LV Substation WE***702 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2771 | -8.9246
MV/LV Substation WE***706X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =221kVA. | --> | 0.38 | 0 | 0.031122 | 0.4263 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8306 | -8.9968
MV/LV Substation WE***721Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.378 | 1.8 |  | --> | 0.38 | 0 | 0.003705 | 0.40333 | 0 |  | --> | C20 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6748 | -8.6875
MV/LV Substation WE***722X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =434kVA. | --> | 0.5985 | 0 | 0.015561 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3134 | -6.3479
MV/LV Substation WE***731X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.095 | 0 | 0 | 0.10941 | 0 |  | --> | C17 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7803 | -8.6372
MV/LV Substation WE***734X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2813 | -9.0319
MV/LV Substation WE***735X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2813 | -9.0319
MV/LV Substation WE***737 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.106 | 0.2 |  | --> | 0.19 | 0 | 0.02223 | 0 | 0 | Constrained,otherwise capacity available =213.8kW. | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2652 | -6.7479
MV/LV Substation WE***738 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.2kW. | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1476 | -6.6235
MV/LV Substation WE***739Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0.016302 | 0.20495 | 0 |  | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6754 | -7.2567
MV/LV Substation WE***743X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6956 | -6.9874
MV/LV Substation WE***760 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =145kVA. | --> | 0.19 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =208.2kW. | --> | C23 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7619 | -8.4157
MV/LV Substation WE***760X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 6.5 |  | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | C17 ex OUGHTERARD | Oughterard [T41,T42] | SCREEB |  | 53.4236 | -9.3102
MV/LV Substation WE***762X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 2.9 |  | --> | 0.095 | 0 | 0 | 0.1027 | 0 |  | --> | C16 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6553 | -6.696
MV/LV Substation WE***763X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.9 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3438 | -6.2505
MV/LV Substation WE***765 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =151kVA. | --> | 0.19 | 0 | 0.008151 | 0.20731 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4007 | -6.4178
MV/LV Substation WE***777X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0.41005 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3143 | -6.349
MV/LV Substation WE***778 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =174kVA. | --> | 0.19 | 0 | 0.003705 | 0.20391 | 0 |  | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1455 | -6.9935
MV/LV Substation WE***779Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0 | 0.40363 | 0 |  | --> | C13 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3076 | -6.4593
MV/LV Substation WE***783Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8976 | -8.4643
MV/LV Substation WE***785 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.8 |  | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C17 ex DONNYBROOK | Donnybrook [T41,T42] | MILLTOWN (DR) |  | 53.3258 | -6.2088
MV/LV Substation WE***789X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0.003705 | 0.41005 | 0 |  | --> | C16 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8418 | -8.9947
MV/LV Substation WE***793Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =380kVA. | --> | 0.38 | 0 | 0 | 0.40302 | 0 |  | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6417 | -6.662
MV/LV Substation WE***796X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =457kVA. | --> | 0.5985 | 0 | 0.001482 | 0.5 | 0 |  | --> | C17 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.29 | -6.4385
MV/LV Substation WE***798Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =370kVA. | --> | 0.38 | 0 | 0.002223 | 0.40453 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5203 | -6.3156
MV/LV Substation WE***804Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400kW. | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9129 | -7.3484
MV/LV Substation WE***805Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E18 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7739 | -7.2991
MV/LV Substation WE***805Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 1.4 |  | --> | 0.38 | 0 | 0.0741 | 0.40438 | 0 |  | --> | E12 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2422 | -6.3421
MV/LV Substation WE***806Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 5.9 |  | --> | 0.095 | 0 | 0.017043 | 0.10417 | 0 |  | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5676 | -7.8889
MV/LV Substation WE***810 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2962 | -6.1488
MV/LV Substation WE***810X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0.003705 | 0.4 | 0 |  | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8311 | -8.9807
MV/LV Substation WE***821X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2812 | -9.0318
MV/LV Substation WE***837Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex GLEBE | Glebe [T41,T42] | RICHMOND |  | 53.7258 | -7.8005
MV/LV Substation WE***837Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C13 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3181 | -6.468
MV/LV Substation WE***839X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C11 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2823 | -8.9751
MV/LV Substation WE***857 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.5 |  | --> | 0.0475 | 0 | 0.00741 | 0.051052 | 0 |  | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6856 | -6.9943
MV/LV Substation WE***860Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0.011115 | 0.20569 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7077 | -6.3231
MV/LV Substation WE***869Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.001482 | 0.5 | 0 |  | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3368 | -6.4733
MV/LV Substation WE***870Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.14262 | 0.1 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0 | 0.41049 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.341 | -6.4684
MV/LV Substation WE***881 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.7 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SOUTH KING STREET | South King Street [T41,T42] | FRANCIS STREET |  | 53.3417 | -6.2609
MV/LV Substation WE***883 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.47 | 11.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C34 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2766 | -9.0772
MV/LV Substation WE***889 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.9 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.593 | -9.0749
MV/LV Substation WE***893 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 5.6 |  | --> | 0.38 | 0 | 0.015561 | 0.40528 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1077 | -6.0613
MV/LV Substation WE***893X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =209kVA. | --> | 0.38 | 0 | 0.005187 | 0.428 | 0 |  | --> | C21 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1376 | -8.6504
MV/LV Substation WE***905 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =378kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =403.3kW. | --> | C16 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.672 | -9.4738
MV/LV Substation WE***907 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =283kVA. | --> | 0.38 | 0 | 0 | 0.41739 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3242 | -6.3628
MV/LV Substation WE***908 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =260kVA. | --> | 0.38 | 0 | 0 | 0.42072 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3232 | -6.3642
MV/LV Substation WE***909 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.165 | 10 |  | --> | 0.38 | 0 | 0 | 0.43418 | 0 |  | --> | C25 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3309 | -6.2761
MV/LV Substation WE***919 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.03705 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3221 | -6.3663
MV/LV Substation WE***926X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.8 |  | --> | 0.5985 | 0 | 0.049647 | 0.5 | 0 |  | --> | C14 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8097 | -9.5393
MV/LV Substation WE***929X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.1kW. | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.268 | -6.7558
MV/LV Substation WE***934X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 1.1 |  | --> | 0.095 | 0 | 0.002964 | 0.10358 | 0 |  | --> | E20 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0884 | -7.9105
MV/LV Substation WE***940 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =63kVA. | --> | 0.095 | 0 | 0.004446 | 0.10547 | 0 |  | --> | C18 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.2119 | -8.8963
MV/LV Substation WE***942 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.8617 | -7.9192
MV/LV Substation WE***943 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =297kVA. | --> | 0.38 | 0 | 0.05928 | 0.41535 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3233 | -6.3659
MV/LV Substation WE***944 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =192kVA. | --> | 0.38 | 0 | 0 | 0.4304 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3216 | -6.3619
MV/LV Substation WE***950 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5408 | -6.3512
MV/LV Substation WE***955 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.9 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3439 | -6.247
MV/LV Substation WE***958X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0.037791 | 0.41608 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7217 | -6.3326
MV/LV Substation WE***968 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 4.4 |  | --> | 0.095 | 0 | 0 | 0.10255 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5296 | -6.3454
MV/LV Substation WE***972 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =62kVA. | --> | 0.095 | 0 | 0.008151 | 0.10561 | 0 |  | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3268 | -6.4657
MV/LV Substation WE***984X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =363kVA. | --> | 0.38 | 0 | 0 | 0.40558 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.291 | -6.3573
MV/LV Substation WE***985X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =130kVA. | --> | 0.19 | 0 | 0 | 0.21036 | 0 |  | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3058 | -6.4596
MV/LV Substation WE***992X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =390kVA. | --> | 0.38 | 0 | 0 | 0.40151 | 0 |  | --> | C15 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8496 | -8.2929
MV/LV Substation WE***994X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0.00741 | 0.051052 | 0 |  | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.8373 | -8.9568
MV/LV Substation WE***997Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.134 | 6 |  | --> | 0.19 | 0 | 0.030381 | 0.20978 | 0 |  | --> | C19 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8638 | -8.4406
MV/LV Substation WF***306Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.2kW. | --> | C25 ex ROSBERCON | Rosbercon [T41,T42] | WATERFORD |  | 52.4006 | -6.948
MV/LV Substation WH***001 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =276kVA. | --> | 0.38 | 0 | 0.042978 | 0.4184 | 0 |  | --> | C17 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1417 | -6.0647
MV/LV Substation WH***005 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.428 | 3.5 |  | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2671 | -9.0676
MV/LV Substation WH***007X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 13.2 |  | --> | 0.38 | 0 | 0.026676 | 0.4171 | 0 |  | --> | C20 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3835 | -6.2219
MV/LV Substation WH***010 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =457kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2725 | -9.0508
MV/LV Substation WH***010 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 1.7 |  | --> | 0.19 | 0 | 0.020007 | 0.20949 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9984 | -6.985
MV/LV Substation WH***015X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C20 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1692 | -6.8948
MV/LV Substation WH***021 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.11 | -7.5969
MV/LV Substation WH***025Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =93kVA. | --> | 0.095 | 0 | 0 | 0.10106 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2998 | -6.5759
MV/LV Substation WH***026 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.485 | 4.1 |  | --> | 0.5985 | 0 | 0.025194 | 0.5 | 0 |  | --> | C20 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3899 | -6.2502
MV/LV Substation WH***027 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =126kVA. | --> | 0.19 | 0 | 0.003705 | 0.21094 | 0 |  | --> | C19 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7248 | -6.3626
MV/LV Substation WH***029 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =108kVA. | --> | 0.19 | 0 | 0.028158 | 0.21351 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2768 | -7.4821
MV/LV Substation WH***030X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2865 | -6.2089
MV/LV Substation WH***038 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.2 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2796 | -6.3747
MV/LV Substation WH***039 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.358 | 14.2 |  | --> | 0.38 | 0 | 0 | 0.40633 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2788 | -6.3754
MV/LV Substation WH***039X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.10152 | 0.5 | 0 |  | --> | C13 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3154 | -6.4728
MV/LV Substation WH***040Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =80kVA. | --> | 0.095 | 0 | 0 | 0.10299 | 0 |  | --> | C13 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1611 | -6.9176
MV/LV Substation WH***043X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =414.9kW. | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4734 | -8.2786
MV/LV Substation WH***047 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 14.2 |  | --> | 0.38 | 0 | 0 | 0.40393 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2779 | -6.377
MV/LV Substation WH***062 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.9 |  | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C26 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.268 | -9.1062
MV/LV Substation WH***066 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0 | 0.21079 | 0 |  | --> | C11 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6457 | -7.2647
MV/LV Substation WH***067 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0.003705 | 0.41681 | 0 |  | --> | C22 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3974 | -6.2928
MV/LV Substation WH***072 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.435 | 13.2 |  | --> | 0.5985 | 0 | 0.025935 | 0.5 | 0 |  | --> | C20 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3821 | -6.2183
MV/LV Substation WH***074 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =188kVA. | --> | 0.5985 | 0 | 0.033345 | 0.5 | 0 |  | --> | C13 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.375 | -6.2503
MV/LV Substation WH***075 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.14262 | 0.1 | Constrained,otherwise capacity available =312kVA. | --> | 0.5985 | 0 | 0.040755 | 0.5 | 0 |  | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3399 | -6.4632
MV/LV Substation WH***080 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.179 | 8.1 |  | --> | 0.38 | 0 | 0.070395 | 0.43222 | 0 |  | --> | C11 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3118 | -6.245
MV/LV Substation WH***085X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8993 | -6.3867
MV/LV Substation WH***086Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3319 | -6.3642
MV/LV Substation WH***088X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =416.5kW. | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.0697 | -7.2722
MV/LV Substation WH***090Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.1 |  | --> | 0.0475 | 0 | 0.003705 | 0.052518 | 0 |  | --> | C21 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0826 | -7.8936
MV/LV Substation WH***093 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.211 | 4.3 |  | --> | 0.38 | 0 | 0.016302 | 0.42772 | 0 |  | --> | C14 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2786 | -6.1862
MV/LV Substation WH***095 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.354 | 9.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8936 | -8.47
MV/LV Substation WH***101X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.4kW. | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.0553 | -7.3288
MV/LV Substation WH***102Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =32kVA. | --> | 0.0475 | 0 | 0.003705 | 0.052662 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9364 | -8.4537
MV/LV Substation WH***107Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C22 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0583 | -7.2291
MV/LV Substation WH***110X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 53.0074 | -6.6431
MV/LV Substation WH***118 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 3.5 |  | --> | 0.38 | 0 | 0.021489 | 0.41417 | 0 |  | --> | C12 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2651 | -9.0637
MV/LV Substation WH***118Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C13 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7685 | -7.1548
MV/LV Substation WH***118Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.392 | -6.255
MV/LV Substation WH***119X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =331kVA. | --> | 0.38 | 0 | 0.002964 | 0 | 0 | Constrained,otherwise capacity available =410.3kW. | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.0711 | -7.2674
MV/LV Substation WH***121 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 0.9 |  | --> | 0.38 | 0 | 0.014079 | 0.40856 | 0 |  | --> | C11 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0586 | -9.4774
MV/LV Substation WH***127 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.2 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2792 | -6.3782
MV/LV Substation WH***128 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 14.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2804 | -6.3764
MV/LV Substation WH***129X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.119 | 1.5 |  | --> | 0.19 | 0 | 0.003705 | 0.21194 | 0 |  | --> | C18 ex SHERCOCK | Shercock [T41,T42] | MEATH HILL |  | 54.0129 | -6.8873
MV/LV Substation WH***130Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =69kVA. | --> | 0.095 | 0 | 0 | 0.1046 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9387 | -8.4521
MV/LV Substation WH***140X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =295kVA. | --> | 0.38 | 0 | 0.026676 | 0.41564 | 0 |  | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3198 | -6.4796
MV/LV Substation WH***142 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 0.6 |  | --> | 0.095 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =106.2kW. | --> | C16 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3578 | -7.7315
MV/LV Substation WH***142Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 1.4 |  | --> | 0.095 | 0 | 0 | 0.10358 | 0 |  | --> | C26 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.6864 | -6.8531
MV/LV Substation WH***145 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6632 | -8.6357
MV/LV Substation WH***145X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 5.8 |  | --> | 0.19 | 0 | 0.005928 | 0.2045 | 0 |  | --> | C20 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2739 | -8.5122
MV/LV Substation WH***150Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.0475 | 0 | 0.006669 | 0.053235 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5205 | -6.1108
MV/LV Substation WH***152 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.38 | 0 | 0.020007 | 0.41666 | 0 |  | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3489 | -6.369
MV/LV Substation WH***152Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =21kVA. | --> | 0.0475 | 0 | 0.002964 | 0.05422 | 0 |  | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2502 | -6.5906
MV/LV Substation WH***164Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0.018525 | 0.053092 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 53.0047 | -6.6568
MV/LV Substation WH***172Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =259kVA. | --> | 0.38 | 0 | 0.064467 | 0.42086 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7104 | -6.3273
MV/LV Substation WH***178 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.244 | 3 |  | --> | 0.38 | 0 | 0.011856 | 0 | 0 | Constrained,otherwise capacity available =423kW. | --> | C11 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9589 | -7.7224
MV/LV Substation WH***179 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C19 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9463 | -8.2526
MV/LV Substation WH***181X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 9.1 |  | --> | 0.0475 | 0 | 0 | 0.05179 | 0 |  | --> | E11 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1072 | -9.0681
MV/LV Substation WH***182X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0.005187 | 0.050604 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3059 | -6.3755
MV/LV Substation WH***204Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =138kVA. | --> | 0.19 | 0 | 0 | 0.2092 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9122 | -8.474
MV/LV Substation WH***209Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0 | 0.20554 | 0 |  | --> | C18 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3946 | -6.3979
MV/LV Substation WH***214 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0.9 |  | --> | 0.5985 | 0 | 0.071877 | 0.5 | 0 |  | --> | C18 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3122 | -6.2822
MV/LV Substation WH***214X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.38 | 0 | 0.01482 | 0.44687 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3426 | -6.3914
MV/LV Substation WH***215 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.3 |  | --> | 0.0475 | 0 | 0.00741 | 0.05179 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8227 | -8.2356
MV/LV Substation WH***235 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =54kVA. | --> | 0.095 | 0 | 0 | 0.10675 | 0 |  | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.949 | -8.3751
MV/LV Substation WH***240Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | C14 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7938 | -6.4217
MV/LV Substation WH***241Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0.026676 | 0.20978 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.709 | -6.3232
MV/LV Substation WH***243 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9437 | -8.4046
MV/LV Substation WH***245 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C18 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0537 | -9.4704
MV/LV Substation WH***249Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 2.3 |  | --> | 0.095 | 0 | 0 | 0.10358 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8123 | -8.186
MV/LV Substation WH***253Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2784 | -6.3803
MV/LV Substation WH***255Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =194kVA. | --> | 0.19 | 0 | 0 | 0.20091 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9955 | -6.6481
MV/LV Substation WH***261 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.188 | 0.9 |  | --> | 0.38 | 0 | 0.020748 | 0.43096 | 0 |  | --> | C22 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3059 | -6.3205
MV/LV Substation WH***263Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7291 | -6.3424
MV/LV Substation WH***269X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =363kVA. | --> | 0.38 | 0 | 0 | 0.40558 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2803 | -6.3838
MV/LV Substation WH***271Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C30 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.6451 | -8.574
MV/LV Substation WH***274Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 1 |  | --> | 0.19 | 0 | 0.002223 | 0.20569 | 0 |  | --> | E20 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7406 | -7.7984
MV/LV Substation WH***284 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =307kVA. | --> | 0.38 | 0 | 0.01482 | 0.41388 | 0 |  | --> | C13 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3499 | -6.3746
MV/LV Substation WH***293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.314 | 1.8 |  | --> | 0.38 | 0 | 0.012597 | 0.41285 | 0 |  | --> | C18 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6765 | -8.6663
MV/LV Substation WH***317 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0.003705 | 0.41681 | 0 |  | --> | C18 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3898 | -6.4034
MV/LV Substation WH***320 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =98kVA. | --> | 0.095 | 0 | 0 | 0.1003 | 0 |  | --> | E16 ex BALLYDEHOB | Ballydehob [T421] | DUNMANWAY |  | 51.4644 | -9.7537
MV/LV Substation WH***320Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C18 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.5497 | -8.0693
MV/LV Substation WH***329Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.19 | 0 | 0.075582 | 0.21576 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.7011 | -6.2675
MV/LV Substation WH***330Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =67kVA. | --> | 0.19 | 0 | 0.010374 | 0.21923 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.7026 | -6.2656
MV/LV Substation WH***331 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 1.8 |  | --> | 0.095 | 0 | 0.00741 | 0.10504 | 0 |  | --> | C15 ex RANDALSTOWN | Randalstown [T41] | NAVAN |  | 53.6748 | -6.7588
MV/LV Substation WH***331Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.19 | 0 | 0.033345 | 0.21882 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.7035 | -6.2652
MV/LV Substation WH***364 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =476kVA. | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.3992 | -6.399
MV/LV Substation WH***366 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 2.9 |  | --> | 0.095 | 0 | 0.018525 | 0.10225 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6594 | -6.7133
MV/LV Substation WH***371 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0.011856 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1102 | -7.7682
MV/LV Substation WH***374 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =284kVA. | --> | 0.38 | 0 | 0.002964 | 0.41724 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.3974 | -6.3949
MV/LV Substation WH***374Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0.003705 | 0.050453 | 0 |  | --> | E16 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9782 | -8.5044
MV/LV Substation WH***378 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.004446 | 0.5 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.3969 | -6.3979
MV/LV Substation WH***399Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =281kVA. | --> | 0.38 | 0 | 0.004446 | 0.41768 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.368 | -6.3633
MV/LV Substation WH***4006 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =134kVA. | --> | 0.19 | 0 | 0.003705 | 0.20978 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.151 | -6.7792
MV/LV Substation WH***4008 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.8 |  | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8034 | -9.4793
MV/LV Substation WH***400Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =494kVA. | --> | 0.5985 | 0 | 0.010374 | 0.5 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3678 | -6.361
MV/LV Substation WH***402 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =140kVA. | --> | 0.19 | 0 | 0.003705 | 0.20891 | 0 |  | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.3957 | -6.3987
MV/LV Substation WH***4024 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C16 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.7985 | -6.4805
MV/LV Substation WH***4028 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =197kVA. | --> | 0.19 | 0 | 0 | 0.20045 | 0 |  | --> | E18 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.984 | -8.5335
MV/LV Substation WH***4054 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =337kVA. | --> | 0.38 | 0 | 0 | 0.40945 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5138 | -6.127
MV/LV Substation WH***4079 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.275 | -6.3152
MV/LV Substation WH***4094 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2724 | -6.3157
MV/LV Substation WH***4095 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2717 | -6.3117
MV/LV Substation WH***4127 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2731 | -6.3163
MV/LV Substation WH***4174 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.2 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.36 | -7.9863
MV/LV Substation WH***4197 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =302kVA. | --> | 0.38 | 0 | 0 | 0.41461 | 0 |  | --> | C15 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1892 | -6.8112
MV/LV Substation WH***4209 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =368kVA. | --> | 0.38 | 0 | 0.032604 | 0.40483 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.7011 | -6.2698
MV/LV Substation WH***4235 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3242 | -6.9789
MV/LV Substation WH***425 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.368 | 11.9 |  | --> | 0.38 | 0 | 0.004446 | 0.40483 | 0 |  | --> | C26 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2685 | -9.1046
MV/LV Substation WH***425Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0.002223 | 0.051348 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2988 | -6.6034
MV/LV Substation WH***4287 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.2164 | -7.1363
MV/LV Substation WH***4296 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =498kVA. | --> | 0.5985 | 0 | 0.011115 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2096 | -6.6753
MV/LV Substation WH***4297 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =468kVA. | --> | 0.5985 | 0 | 0.01482 | 0.5 | 0 |  | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2096 | -6.6735
MV/LV Substation WH***4309 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6 |  | --> | 0.95 | 0 | 0.005928 | 0.5 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3713 | -6.3822
MV/LV Substation WH***4310 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6 |  | --> | 0.95 | 0 | 0.009633 | 0.5 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3713 | -6.3822
MV/LV Substation WH***4316 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =310kVA. | --> | 0.38 | 0 | 0 | 0.41344 | 0 |  | --> | C33 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4044 | -6.2563
MV/LV Substation WH***433X |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =20kVA. | --> | 0.02375 | 0 | 0 | 0.025748 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5175 | -6.1167
MV/LV Substation WH***4371 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.4kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3469 | -9.0064
MV/LV Substation WH***440X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3465 | -6.2692
MV/LV Substation WH***463X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5186 | -6.1196
MV/LV Substation WH***471X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 2.9 |  | --> | 0.19 | 0 | 0 | 0.20316 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6602 | -6.7231
MV/LV Substation WH***472Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.129 | 0.9 |  | --> | 0.19 | 0 | 0.020748 | 0.2105 | 0 |  | --> | C15 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3265 | -6.4718
MV/LV Substation WH***490X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 1.4 |  | --> | 0.19 | 0 | 0.008151 | 0.2051 | 0 |  | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2772 | -6.3949
MV/LV Substation WH***506 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0.042237 | 0.41271 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2845 | -6.2885
MV/LV Substation WH***509Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0.01482 | 0.20346 | 0 |  | --> | C23 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6803 | -7.0283
MV/LV Substation WH***517 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =261kVA. | --> | 0.38 | 0 | 0.074841 | 0.42058 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2824 | -6.2884
MV/LV Substation WH***540Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =332kVA. | --> | 0.38 | 0 | 0.015561 | 0.4102 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3678 | -6.3578
MV/LV Substation WH***541Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =177kVA. | --> | 0.19 | 0 | 0.021489 | 0.20346 | 0 |  | --> | C15 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3664 | -6.3533
MV/LV Substation WH***564X |  | 10 kV | _ | LV | 25 kVA :Building Structure | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =25kVA. | --> | 0.02375 | 0 | 0 | 0.025 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2783 | -6.3803
MV/LV Substation WH***576X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =286kVA. | --> | 0.38 | 0 | 0.00741 | 0.41695 | 0 |  | --> | C17 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3447 | -6.3824
MV/LV Substation WH***577X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =108kVA. | --> | 0.19 | 0 | 0.002964 | 0.21351 | 0 |  | --> | C17 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.344 | -6.3813
MV/LV Substation WH***582Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =129kVA. | --> | 0.19 | 0 | 0.021489 | 0.2105 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7087 | -6.3193
MV/LV Substation WH***599Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 0.2 |  | --> | 0.095 | 0 | 0.002223 | 0 | 0 | Constrained,otherwise capacity available =102.1kW. | --> | E16 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2517 | -6.9632
MV/LV Substation WH***600 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =82kVA. | --> | 0.095 | 0 | 0 | 0.1027 | 0 |  | --> | C15 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.562 | -6.7948
MV/LV Substation WH***610Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0 | 0.41108 | 0 |  | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7094 | -6.3292
MV/LV Substation WH***612X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6641 | -6.2726
MV/LV Substation WH***633 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0.003705 | 0.052518 | 0 |  | --> | E18 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5097 | -8.1757
MV/LV Substation WH***654 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0 | 0.052949 | 0 |  | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9458 | -8.3725
MV/LV Substation WH***654X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.123 | 5.9 |  | --> | 0.19 | 0 | 0.003705 | 0.21137 | 0 |  | --> | C12 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5068 | -7.8921
MV/LV Substation WH***654X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =98kVA. | --> | 0.095 | 0 | 0 | 0.1003 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4702 | -6.4148
MV/LV Substation WH***660Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =112kVA. | --> | 0.19 | 0 | 0.018525 | 0.21294 | 0 |  | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2847 | -6.8615
MV/LV Substation WH***665 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0.050303 | 0 |  | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9507 | -8.3738
MV/LV Substation WH***665Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0.00741 | 0 | 0 | Constrained,otherwise capacity available =203.6kW. | --> | C17 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9464 | -7.7863
MV/LV Substation WH***676X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 13.5 |  | --> | 0.095 | 0 | 0 | 0.10255 | 0 |  | --> | C21 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8976 | -8.9385
MV/LV Substation WH***687 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.5713 | -6.7194
MV/LV Substation WH***691Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 0.9 |  | --> | 0.38 | 0 | 0.03705 | 0.4 | 0 |  | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3243 | -6.5007
MV/LV Substation WH***691Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =280kVA. | --> | 0.38 | 0 | 0.084474 | 0.41782 | 0 |  | --> | E21 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5074 | -6.3856
MV/LV Substation WH***692Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =450kVA. | --> | 0.5985 | 0 | 0.015561 | 0.5 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1509 | -7.1864
MV/LV Substation WH***698X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0.008151 | 0.051052 | 0 |  | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3183 | -6.479
MV/LV Substation WH***707 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 0.2 |  | --> | 0.0475 | 0 | 0.01482 | 0.05408 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.261 | -6.2943
MV/LV Substation WH***707Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =129kVA. | --> | 0.19 | 0 | 0 | 0.2105 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9338 | -6.6963
MV/LV Substation WH***708X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 1.7 |  | --> | 0.19 | 0 | 0.006669 | 0.20166 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8869 | -9.5501
MV/LV Substation WH***717 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3092 | -6.3123
MV/LV Substation WH***727X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =199kVA. | --> | 0.19 | 0 | 0 | 0.20015 | 0 |  | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3732 | -7.3805
MV/LV Substation WH***734X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.332 | 1.9 |  | --> | 0.38 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =410.2kW. | --> | C13 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8675 | -9.2832
MV/LV Substation WH***737 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =396kVA. | --> | 0.38 | 0 | 0 | 0.40061 | 0 |  | --> | C11 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3769 | -6.2511
MV/LV Substation WH***739 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0.002964 | 0.051052 | 0 |  | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5185 | -6.1282
MV/LV Substation WH***742Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =282kVA. | --> | 0.38 | 0 | 0.048165 | 0.41753 | 0 |  | --> | C22 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8033 | -8.4054
MV/LV Substation WH***750Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =145kVA. | --> | 0.19 | 0 | 0 | 0.20818 | 0 |  | --> | C14 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6045 | -6.9228
MV/LV Substation WH***763X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0 | 0.0538 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 53.0121 | -6.662
MV/LV Substation WH***765X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =290kVA. | --> | 0.38 | 0 | 0.008151 | 0.41637 | 0 |  | --> | C16 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8745 | -8.5066
MV/LV Substation WH***768Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0.005187 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1124 | -6.6196
MV/LV Substation WH***784 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1109 | -7.7531
MV/LV Substation WH***786 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1084 | -7.7459
MV/LV Substation WH***788 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.288 | 2.4 |  | --> | 0.38 | 0 | 0.027417 | 0.41666 | 0 |  | --> | C19 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1901 | -6.114
MV/LV Substation WH***791X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.9 |  | --> | 0.095 | 0 | 0 | 0.10181 | 0 |  | --> | C18 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6595 | -6.7205
MV/LV Substation WH***794Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =119kVA. | --> | 0.19 | 0 | 0.018525 | 0.21194 | 0 |  | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1526 | -7.1867
MV/LV Substation WH***805Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3372 | -9.0096
MV/LV Substation WH***812 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =258kVA. | --> | 0.38 | 0 | 0.035568 | 0.42101 | 0 |  | --> | C18 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3031 | -6.2348
MV/LV Substation WH***820Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1788 | -6.7981
MV/LV Substation WH***821Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1788 | -6.7982
MV/LV Substation WH***854X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3466 | -6.2692
MV/LV Substation WH***855Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =282kVA. | --> | 0.38 | 0 | 0.026676 | 0.41753 | 0 |  | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3215 | -6.4796
MV/LV Substation WH***864Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 4.2 |  | --> | 0.0475 | 0 | 0.00741 | 0.050453 | 0 |  | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0397 | -6.3946
MV/LV Substation WH***872 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0 | 0.10225 | 0 |  | --> | C18 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.2329 | -7.2158
MV/LV Substation WH***873 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.6 |  | --> | 0.5985 | 0 | 0.011115 | 0.5 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1102 | -6.0642
MV/LV Substation WH***875X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C23 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.6477 | -9.6727
MV/LV Substation WH***883 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0.015561 | 0.10373 | 0 |  | --> | C28 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3255 | -8.9674
MV/LV Substation WH***892 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.154 | 14.2 |  | --> | 0.19 | 0 | 0.005928 | 0.20687 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2847 | -6.3914
MV/LV Substation WH***901 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =199kVA. | --> | 0.19 | 0 | 0 | 0.20015 | 0 |  | --> | C16 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8108 | -6.461
MV/LV Substation WH***909Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 1.7 |  | --> | 0.19 | 0 | 0.002964 | 0.20613 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9459 | -7.0364
MV/LV Substation WH***931X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0 | 0.20628 | 0 |  | --> | C16 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3296 | -8.4728
MV/LV Substation WH***931X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =348kVA. | --> | 0.38 | 0 | 0 | 0.40782 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3082 | -6.3546
MV/LV Substation WH***932X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =159kVA. | --> | 0.19 | 0 | 0 | 0.20613 | 0 |  | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9932 | -8.1236
MV/LV Substation WH***955Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9947 | -6.6472
MV/LV Substation WH***957 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | C16 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8064 | -6.4627
MV/LV Substation WH***985 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0.004446 | 0 | 0 | Constrained,otherwise capacity available =101.2kW. | --> | C11 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7761 | -7.8399
MV/LV Substation WI***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.269 | 1.5 |  | --> | 0.38 | 0 | 0 | 0.41942 | 0 |  | --> | C11 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4475 | -9.4865
MV/LV Substation WI***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =396kVA. | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2719 | -8.478
MV/LV Substation WI***003Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.36 | 0.8 |  | --> | 0.38 | 0 | 0 | 0.40603 | 0 |  | --> | C16 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2591 | -7.1045
MV/LV Substation WI***004Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.2015 | -6.7537
MV/LV Substation WI***007 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 6 |  | --> | 0.38 | 0 | 0.018525 | 0 | 0 | Constrained,otherwise capacity available =418.7kW. | --> | C12 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3664 | -7.6979
MV/LV Substation WI***010 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.129 | 2.2 |  | --> | 0.19 | 0 | 0.003705 | 0.2105 | 0 |  | --> | C24 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9155 | -6.9737
MV/LV Substation WI***013 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.1 |  | --> | 0.5985 | 0 | 0.02223 | 0.5 | 0 |  | --> | C17 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3903 | -6.2695
MV/LV Substation WI***019Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =112kVA. | --> | 0.19 | 0 | 0.033345 | 0.21294 | 0 |  | --> | C17 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.242 | -7.0967
MV/LV Substation WI***030 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =407kVA. | --> | 0.5985 | 0 | 0.017784 | 0.5 | 0 |  | --> | C19 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3012 | -6.2451
MV/LV Substation WI***034 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 1.6 |  | --> | 0.095 | 0 | 0.008892 | 0 | 0 | Constrained,otherwise capacity available =105kW. | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4971 | -8.2088
MV/LV Substation WI***034 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 0.4 |  | --> | 0.19 | 0 | 0 | 0.20061 | 0 |  | --> | E19 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8007 | -6.6837
MV/LV Substation WI***035 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =396kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =400.6kW. | --> | C18 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3904 | -6.9432
MV/LV Substation WI***040X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.3kW. | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6504 | -8.1407
MV/LV Substation WI***041 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C18 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8527 | -6.5366
MV/LV Substation WI***041 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.027417 | 0.5 | 0 |  | --> | C12 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8557 | -8.2828
MV/LV Substation WI***044 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.008 | 5 |  | --> | 0.19 | 0 | 0.011856 | 0.22714 | 0 |  | --> | C13 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.655 | -7.2402
MV/LV Substation WI***058 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.5 |  | --> | 0.5985 | 0 | 0.032604 | 0.5 | 0 |  | --> | C19 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 53.9985 | -6.4259
MV/LV Substation WI***065X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 16.1 |  | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | E12 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3738 | -6.6533
MV/LV Substation WI***074 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =230kVA. | --> | 0.38 | 0 | 0.034086 | 0.42502 | 0 |  | --> | C22 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3922 | -6.2787
MV/LV Substation WI***077Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =193kVA. | --> | 0.19 | 0 | 0.002223 | 0.20106 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2354 | -7.0747
MV/LV Substation WI***081 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.244 | 12.2 |  | --> | 0.38 | 0 | 0.02964 | 0.42302 | 0 |  | --> | C20 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9751 | -6.0474
MV/LV Substation WI***085 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =56kVA. | --> | 0.095 | 0 | 0 | 0.10647 | 0 |  | --> | C11 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7188 | -6.3647
MV/LV Substation WI***086X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 2 |  | --> | 0.0475 | 0 | 0.002223 | 0.052228 | 0 |  | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 54.0521 | -7.7952
MV/LV Substation WI***088 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =129kVA. | --> | 0.19 | 0 | 0.006669 | 0 | 0 | Constrained,otherwise capacity available =210.5kW. | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6822 | -6.2968
MV/LV Substation WI***109Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.38 | 5.9 |  | --> | 0.38 | 0 | 0 | 0.40302 | 0 |  | --> | C18 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5117 | -7.8015
MV/LV Substation WI***122 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 12.2 |  | --> | 0.38 | 0 | 0.015561 | 0.40797 | 0 |  | --> | C20 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9745 | -6.0447
MV/LV Substation WI***126Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3253 | -6.3623
MV/LV Substation WI***134 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 6 |  | --> | 0.38 | 0 | 0 | 0.41373 | 0 |  | --> | C11 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8911 | -8.4682
MV/LV Substation WI***136X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =142kVA. | --> | 0.19 | 0 | 0.003705 | 0.20862 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8792 | -8.5049
MV/LV Substation WI***139Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 1.1 |  | --> | 0.38 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =406.2kW. | --> | C15 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4467 | -9.0447
MV/LV Substation WI***140Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0.016302 | 0.40916 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.346 | -6.5487
MV/LV Substation WI***149X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.298 | 4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SHERIFF STREET | Sheriff Street [T41,T42] | FRANCIS STREET |  | 53.3455 | -6.2445
MV/LV Substation WI***153Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =144kVA. | --> | 0.19 | 0 | 0.015561 | 0.20833 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9251 | -8.1834
MV/LV Substation WI***154 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.095 | 0 | 0 | 0.10941 | 0 |  | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.619 | -6.9253
MV/LV Substation WI***157X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SHERIFF STREET | Sheriff Street [T41,T42] | FRANCIS STREET |  | 53.3446 | -6.2431
MV/LV Substation WI***163X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.152 | 3.5 |  | --> | 0.19 | 0 | 0.025194 | 0.20716 | 0 |  | --> | C13 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 53.9978 | -6.4222
MV/LV Substation WI***166Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =271kVA. | --> | 0.38 | 0 | 0.04446 | 0.41913 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9287 | -8.5907
MV/LV Substation WI***168 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =148kVA. | --> | 0.38 | 0 | 0.016302 | 0.43653 | 0 |  | --> | C13 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8829 | -8.5066
MV/LV Substation WI***169 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =136kVA. | --> | 0.38 | 0 | 0 | 0.43819 | 0 |  | --> | C12 ex ROCHES STREET | Roches Street [T41,T42] | LIMERICK |  | 52.6617 | -8.6232
MV/LV Substation WI***169 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =310kVA. | --> | 0.38 | 0 | 0.015561 | 0.41344 | 0 |  | --> | C21 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8849 | -8.5098
MV/LV Substation WI***170 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =167kVA. | --> | 0.19 | 0 | 0 | 0.20495 | 0 |  | --> | C21 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8832 | -8.5139
MV/LV Substation WI***170Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 5.9 |  | --> | 0.19 | 0 | 0 | 0.20731 | 0 |  | --> | C12 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5058 | -7.8956
MV/LV Substation WI***171 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =138kVA. | --> | 0.19 | 0 | 0.026676 | 0.2092 | 0 |  | --> | C20 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2844 | -6.2396
MV/LV Substation WI***175Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =337kVA. | --> | 0.38 | 0 | 0 | 0.40945 | 0 |  | --> | C17 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4143 | -6.412
MV/LV Substation WI***186Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =332kVA. | --> | 0.38 | 0 | 0.003705 | 0.4102 | 0 |  | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3372 | -6.4765
MV/LV Substation WI***189 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =255kVA. | --> | 0.38 | 0 | 0.040014 | 0.42144 | 0 |  | --> | C20 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.3939 | -6.2825
MV/LV Substation WI***189 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.322 | 11.9 |  | --> | 0.38 | 0 | 0.019266 | 0.41167 | 0 |  | --> | C26 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2662 | -9.1092
MV/LV Substation WI***193 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 10.9 |  | --> | 0.095 | 0 | 0.004446 | 0.1003 | 0 |  | --> | C25 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5897 | -7.5306
MV/LV Substation WI***193Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =301kVA. | --> | 0.38 | 0 | 0.027417 | 0.41476 | 0 |  | --> | C22 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.883 | -8.6124
MV/LV Substation WI***194 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.315 | 0.9 |  | --> | 0.5985 | 0 | 0.01482 | 0.5 | 0 |  | --> | C16 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3249 | -6.3098
MV/LV Substation WI***197X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3013 | -6.2454
MV/LV Substation WI***200Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =136kVA. | --> | 0.19 | 0 | 0.02223 | 0.20949 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9266 | -8.1853
MV/LV Substation WI***201Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =67kVA. | --> | 0.095 | 0 | 0 | 0.10489 | 0 |  | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.4362 | -6.5331
MV/LV Substation WI***207X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 2 |  | --> | 0.38 | 0 | 0.017784 | 0.40618 | 0 |  | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 54.0504 | -7.7919
MV/LV Substation WI***209X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 2.8 |  | --> | 0.0475 | 0 | 0.003705 | 0.0538 | 0 |  | --> | E12 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.369 | -7.48
MV/LV Substation WI***209Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0.008892 | 0.41005 | 0 |  | --> | C20 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6455 | -8.5907
MV/LV Substation WI***211Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =263kVA. | --> | 0.38 | 0 | 0.01482 | 0.42029 | 0 |  | --> | C23 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8268 | -6.9067
MV/LV Substation WI***216X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =124kVA. | --> | 0.19 | 0 | 0.054093 | 0.21122 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2377 | -7.0957
MV/LV Substation WI***217Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 1.5 |  | --> | 0.38 | 0 | 0.00741 | 0.40438 | 0 |  | --> | C13 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4496 | -9.4802
MV/LV Substation WI***221X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 5.5 |  | --> | 0.38 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =412.6kW. | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9666 | -7.7582
MV/LV Substation WI***223 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.356 | 1.4 |  | --> | 0.5985 | 0 | 0.062244 | 0.5 | 0 |  | --> | C16 ex DODDER ROAD | Dodder Road [T42] | MILLTOWN (DR) |  | 53.2966 | -6.2608
MV/LV Substation WI***225Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =331kVA. | --> | 0.38 | 0 | 0 | 0.41034 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3336 | -6.5275
MV/LV Substation WI***226Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =295kVA. | --> | 0.38 | 0 | 0.035568 | 0.41564 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3354 | -6.5295
MV/LV Substation WI***228Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =277kVA. | --> | 0.38 | 0 | 0.010374 | 0.41826 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3352 | -6.5262
MV/LV Substation WI***230 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.257 | 4.2 |  | --> | 0.5985 | 0 | 0.01482 | 0.5 | 0 |  | --> | C14 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3199 | -6.3149
MV/LV Substation WI***233Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =280kVA. | --> | 0.38 | 0 | 0.003705 | 0.41782 | 0 |  | --> | C15 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9325 | -8.3796
MV/LV Substation WI***238X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =278kVA. | --> | 0.38 | 0 | 0.020748 | 0.41811 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3124 | -6.4012
MV/LV Substation WI***247Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 12.2 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9864 | -6.0531
MV/LV Substation WI***256Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0 | 0.40737 | 0 |  | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3363 | -6.5299
MV/LV Substation WI***261 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =122kVA. | --> | 0.19 | 0 | 0.009633 | 0.21151 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9084 | -6.8454
MV/LV Substation WI***261X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.265 | 4.6 |  | --> | 0.38 | 0 | 0.05187 | 0.42 | 0 |  | --> | C36 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9008 | -8.346
MV/LV Substation WI***267 |  | 10 kV | _ | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0 | 0 | Constrained,otherwise capacity available =143kVA. | --> | 0.1425 | 0 | 0.003705 | 0.15106 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3689 | -6.0669
MV/LV Substation WI***274Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2365 | -7.0837
MV/LV Substation WI***280 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.365 | 3.9 |  | --> | 0.38 | 0 | 0 | 0.40528 | 0 |  | --> | C26 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2903 | -9.011
MV/LV Substation WI***280Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.1 |  | --> | 0.0475 | 0 | 0.003705 | 0.052083 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7324 | -6.7105
MV/LV Substation WI***281Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 1.1 |  | --> | 0.095 | 0 | 0.008151 | 0.10475 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7338 | -6.712
MV/LV Substation WI***283 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =290kVA. | --> | 0.38 | 0 | 0.042978 | 0.41637 | 0 |  | --> | C19 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4598 | -6.2305
MV/LV Substation WI***287Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =181kVA. | --> | 0.19 | 0 | 0 | 0.20286 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2601 | -7.0257
MV/LV Substation WI***289X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 2.5 |  | --> | 0.19 | 0 | 0 | 0.20643 | 0 |  | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6584 | -7.5215
MV/LV Substation WI***292X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.004446 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4066 | -6.2222
MV/LV Substation WI***319 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0.01482 | 0.10402 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3691 | -6.068
MV/LV Substation WI***320Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.362 | 6.4 |  | --> | 0.38 | 0 | 0 | 0.40573 | 0 |  | --> | C12 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4119 | -7.8964
MV/LV Substation WI***322Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =388kVA. | --> | 0.38 | 0 | 0 | 0.37942 | 0 | Constrained,otherwise capacity available =401.8kW. | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2077 | -8.5103
MV/LV Substation WI***337Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.1 |  | --> | 0.0475 | 0 | 0.008151 | 0.060156 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.74 | -6.715
MV/LV Substation WI***339Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =305kVA. | --> | 0.38 | 0 | 0 | 0.41417 | 0 |  | --> | C20 ex BALLINACURRA | Ballinacurra [T41,T42] | LIMERICK |  | 52.6597 | -8.635
MV/LV Substation WI***342X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8755 | -6.407
MV/LV Substation WI***358 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.408 | 8.1 |  | --> | 0.5985 | 0 | 0.013338 | 0.5 | 0 |  | --> | C12 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3173 | -6.2551
MV/LV Substation WI***363Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =148kVA. | --> | 0.19 | 0 | 0.003705 | 0.20775 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.395 | -6.4429
MV/LV Substation WI***364Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =332kVA. | --> | 0.38 | 0 | 0.004446 | 0.4102 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3943 | -6.4428
MV/LV Substation WI***376 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =233kVA. | --> | 0.38 | 0 | 0.011115 | 0.42459 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3062 | -6.1976
MV/LV Substation WI***382Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =449kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E20 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5227 | -6.4131
MV/LV Substation WI***383 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.206 | 4.5 |  | --> | 0.38 | 0 | 0.060762 | 0.42843 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3017 | -6.3265
MV/LV Substation WI***389Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 10.9 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6124 | -7.42
MV/LV Substation WI***391X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0 | 0.41271 | 0 |  | --> | C17 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.3978 | -6.1949
MV/LV Substation WI***396Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =29kVA. | --> | 0.0475 | 0 | 0.014079 | 0.053092 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2302 | -7.0697
MV/LV Substation WI***400 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =468kVA. | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | C22 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3942 | -6.2794
MV/LV Substation WI***4021 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0.052373 | 0 |  | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5304 | -6.2362
MV/LV Substation WI***4032 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.5kW. | --> | C18 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8479 | -8.2059
MV/LV Substation WI***4047 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C21 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7287 | -8.4696
MV/LV Substation WI***4049 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.5 |  | --> | 0.5985 | 0 | 0.039273 | 0.5 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3068 | -6.3309
MV/LV Substation WI***4056 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 1 |  | --> | 0.095 | 0 | 0 | 0.10547 | 0 |  | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2498 | -7.1748
MV/LV Substation WI***4060 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6787 | -8.5461
MV/LV Substation WI***4063 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.017784 | 0.5 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2802 | -6.4777
MV/LV Substation WI***4064 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.7 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0174 | -6.9899
MV/LV Substation WI***4065 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.5985 | 0 | 0.064467 | 0.5 | 0 |  | --> | C13 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.3093 | -6.3308
MV/LV Substation WI***4074 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.163 | 5.6 |  | --> | 0.19 | 0 | 0 | 0.20554 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0714 | -6.1105
MV/LV Substation WI***4077 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.38033 | 0.4 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.052611 | 0.5 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2448 | -6.1881
MV/LV Substation WI***4094 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6504 | -8.2213
MV/LV Substation WI***4099 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.104 | 1.3 |  | --> | 0.19 | 0 | 0.11115 | 0.2 | 0 |  | --> | C22 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.8347 | -8.3207
MV/LV Substation WI***4101 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C11 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9492 | -6.2057
MV/LV Substation WI***410Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0.005187 | 0.20554 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3951 | -6.4408
MV/LV Substation WI***4121 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =154kVA. | --> | 0.19 | 0 | 0 | 0.20687 | 0 |  | --> | C15 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.8452 | -7.0838
MV/LV Substation WI***4132 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =294kVA. | --> | 0.38 | 0 | 0.041496 | 0.41578 | 0 |  | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2503 | -6.657
MV/LV Substation WI***4167 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =147kVA. | --> | 0.19 | 0 | 0.00741 | 0.20789 | 0 |  | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2978 | -6.5708
MV/LV Substation WI***417 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 8.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.2kW. | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0549 | -8.0185
MV/LV Substation WI***4174 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 3.3 |  | --> | 0.38 | 0 | 0.017784 | 0.41884 | 0 |  | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.735 | -6.8846
MV/LV Substation WI***417X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.8kW. | --> | C15 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8396 | -6.3124
MV/LV Substation WI***4189 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.38033 | 0.4 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2405 | -6.1984
MV/LV Substation WI***4191 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 12.2 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9336 | -6.0311
MV/LV Substation WI***4199 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.8 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.35 | -7.6236
MV/LV Substation WI***420Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E17 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6115 | -6.6923
MV/LV Substation WI***4217 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.01482 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4006 | -6.4457
MV/LV Substation WI***4223 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =187kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.5148 | -6.7111
MV/LV Substation WI***4250 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3796 | -6.4004
MV/LV Substation WI***4251 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.38 | -6.4012
MV/LV Substation WI***4291 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.10522 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4254 | -6.3757
MV/LV Substation WI***4311 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.31329 | 0.3 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3935 | -6.2396
MV/LV Substation WI***4337 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C21 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4011 | -6.2911
MV/LV Substation WI***4363 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3328 | -6.2515
MV/LV Substation WI***437X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =64kVA. | --> | 0.095 | 0 | 0.02223 | 0.10532 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9199 | -8.3134
MV/LV Substation WI***446Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =151kVA. | --> | 0.19 | 0 | 0 | 0.20731 | 0 |  | --> | C20 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1688 | -6.9089
MV/LV Substation WI***449Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.012597 | 0.5 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2397 | -7.0886
MV/LV Substation WI***451X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =137kVA. | --> | 0.19 | 0 | 0.006669 | 0 | 0 | Constrained,otherwise capacity available =209.3kW. | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4078 | -6.9363
MV/LV Substation WI***468Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0 | 0.40916 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3943 | -6.4404
MV/LV Substation WI***469Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2533 | -6.6676
MV/LV Substation WI***489 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.4 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C16 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1814 | -6.1429
MV/LV Substation WI***489Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =283kVA. | --> | 0.38 | 0 | 0 | 0.41739 | 0 |  | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3804 | -6.3993
MV/LV Substation WI***491X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9354 | -10.2402
MV/LV Substation WI***492 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8831 | -6.4094
MV/LV Substation WI***492Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.296 | 12.2 |  | --> | 0.38 | 0 | 0.015561 | 0.41549 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9872 | -6.0797
MV/LV Substation WI***496X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.5 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C13 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9668 | -7.7327
MV/LV Substation WI***504 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =311kVA. | --> | 0.38 | 0 | 0.028899 | 0.41329 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2868 | -6.2888
MV/LV Substation WI***508 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.293 | 3.3 |  | --> | 0.38 | 0 | 0.00741 | 0.41593 | 0 |  | --> | C19 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3265 | -6.2158
MV/LV Substation WI***520Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.474 | -6.2324
MV/LV Substation WI***521Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =351kVA. | --> | 0.38 | 0 | 0.017784 | 0.40737 | 0 |  | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4926 | -6.138
MV/LV Substation WI***542 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.9 |  | --> | 0.95 | 0 | 0.00741 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3254 | -6.2656
MV/LV Substation WI***546 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.166 | 4.5 |  | --> | 0.19 | 0 | 0 | 0.2051 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2975 | -6.3268
MV/LV Substation WI***548X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.7 |  | --> | 0.095 | 0 | 0 | 0.10076 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0219 | -6.994
MV/LV Substation WI***550X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =173kVA. | --> | 0.19 | 0 | 0.001482 | 0.20406 | 0 |  | --> | C15 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1299 | -8.6643
MV/LV Substation WI***553X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 1.6 |  | --> | 0.19 | 0 | 0.011115 | 0.20106 | 0 |  | --> | C18 ex TULLYNAMALRA | Tullynamalra [T41,T42] | MEATH HILL |  | 54.0816 | -6.8252
MV/LV Substation WI***561 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =243kVA. | --> | 0.38 | 0 | 0.018525 | 0.42316 | 0 |  | --> | C15 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3905 | -6.4197
MV/LV Substation WI***567Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0 | 0.20361 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8769 | -8.5078
MV/LV Substation WI***570 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0.004446 | 0.10225 | 0 |  | --> | E13 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3851 | -7.0017
MV/LV Substation WI***575Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =142kVA. | --> | 0.19 | 0 | 0.020748 | 0.20862 | 0 |  | --> | C17 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3469 | -6.547
MV/LV Substation WI***580X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =111kVA. | --> | 0.19 | 0 | 0.016302 | 0.21308 | 0 |  | --> | C13 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3555 | -6.4231
MV/LV Substation WI***586 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 3.3 |  | --> | 0.19 | 0 | 0.002223 | 0.2076 | 0 |  | --> | C19 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3266 | -6.217
MV/LV Substation WI***587X |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =16kVA. | --> | 0.02375 | 0 | 0 | 0.026331 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2728 | -6.5108
MV/LV Substation WI***588X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =275kVA. | --> | 0.38 | 0 | 0.039273 | 0.41855 | 0 |  | --> | C13 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3554 | -6.4267
MV/LV Substation WI***594 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =110kVA. | --> | 0.19 | 0 | 0 | 0.21322 | 0 |  | --> | C13 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2552 | -6.1361
MV/LV Substation WI***599X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0.042237 | 0.20628 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.836 | -9.0003
MV/LV Substation WI***612 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.041 | 2.4 |  | --> | 0.095 | 0 | 0.012597 | 0.10858 | 0 |  | --> | C16 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1777 | -6.1457
MV/LV Substation WI***612Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0.005928 | 0.20628 | 0 |  | --> | C11 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9737 | -7.348
MV/LV Substation WI***612Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 12.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9876 | -6.0767
MV/LV Substation WI***615 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.495 | 3.4 |  | --> | 0.5985 | 0 | 0.01482 | 0.5 | 0 |  | --> | C11 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3344 | -6.2471
MV/LV Substation WI***624 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.0475 | 0 | 0.00741 | 0.0538 | 0 |  | --> | C18 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.4608 | -7.3986
MV/LV Substation WI***625 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =82kVA. | --> | 0.095 | 0 | 0.016302 | 0.1027 | 0 |  | --> | C18 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.461 | -7.3947
MV/LV Substation WI***642Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =125kVA. | --> | 0.19 | 0 | 0.001482 | 0.21108 | 0 |  | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3363 | -6.476
MV/LV Substation WI***652Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.34 | -6.6029
MV/LV Substation WI***654 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =148kVA. | --> | 0.19 | 0 | 0.003705 | 0.20775 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6774 | -8.5811
MV/LV Substation WI***655 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =13kVA. | --> | 0.0475 | 0 | 0 | 0.05532 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6777 | -8.5777
MV/LV Substation WI***658 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 3.5 |  | --> | 0.0475 | 0 | 0 | 0.051348 | 0 |  | --> | E16 ex BUSH | Bush [T421,T422] | DUNDALK |  | 53.9915 | -6.1431
MV/LV Substation WI***665X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 6.4 |  | --> | 0.0475 | 0 | 0.004446 | 0.050903 | 0 |  | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4379 | -7.8999
MV/LV Substation WI***668Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8978 | -8.5335
MV/LV Substation WI***682 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8753 | -6.3985
MV/LV Substation WI***684 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =35kVA. | --> | 0.0475 | 0 | 0.005928 | 0.052228 | 0 |  | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6127 | -6.6754
MV/LV Substation WI***694Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6747 | -8.5842
MV/LV Substation WI***701X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.881 | -8.5076
MV/LV Substation WI***707 |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =20kVA. | --> | 0.02375 | 0 | 0 | 0.025748 | 0 |  | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8757 | -6.4093
MV/LV Substation WI***712Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0.0512 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6763 | -8.5911
MV/LV Substation WI***720Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.161 | 0.9 |  | --> | 0.19 | 0 | 0.017784 | 0.20584 | 0 |  | --> | C15 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0045 | -6.3566
MV/LV Substation WI***724X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =99kVA. | --> | 0.095 | 0 | 0 | 0.10015 | 0 |  | --> | C17 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8577 | -8.4503
MV/LV Substation WI***749 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0.034086 | 0.20554 | 0 |  | --> | C16 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9201 | -8.3191
MV/LV Substation WI***749 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2851 | -9.7079
MV/LV Substation WI***753X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.8 |  | --> | 0.0475 | 0 | 0.002964 | 0.051348 | 0 |  | --> | C17 ex RANDALSTOWN | Randalstown [T41] | NAVAN |  | 53.6703 | -6.7039
MV/LV Substation WI***770 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0.014079 | 0.052518 | 0 |  | --> | C15 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.3971 | -7.738
MV/LV Substation WI***773X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.5 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1371 | -8.643
MV/LV Substation WI***806X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 16.1 |  | --> | 0.095 | 0 | 0.014079 | 0.10225 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3887 | -6.3661
MV/LV Substation WI***828X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =41kVA. | --> | 0.0475 | 0 | 0.00741 | 0.051348 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8453 | -8.6104
MV/LV Substation WI***836 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =7kVA. | --> | 0.0475 | 0 | 0 | 0.056126 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1223 | -6.109
MV/LV Substation WI***838 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1239 | -6.1066
MV/LV Substation WI***840X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.263 | 12.2 |  | --> | 0.38 | 0 | 0.003705 | 0.42029 | 0 |  | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9821 | -6.0495
MV/LV Substation WI***862Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.341 | 6.4 |  | --> | 0.38 | 0 | 0 | 0.40886 | 0 |  | --> | C11 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4161 | -7.907
MV/LV Substation WI***876Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =150kVA. | --> | 0.19 | 0 | 0.001482 | 0 | 0 | Constrained,otherwise capacity available =207.5kW. | --> | C16 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1135 | -7.3158
MV/LV Substation WI***882 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C11 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.2714 | -8.7745
MV/LV Substation WI***882Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =74kVA. | --> | 0.095 | 0 | 0.003705 | 0.10387 | 0 |  | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6755 | -8.5793
MV/LV Substation WI***887Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.104 | 2.9 |  | --> | 0.19 | 0 | 0.002223 | 0.21407 | 0 |  | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6666 | -6.699
MV/LV Substation WI***888Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 2.9 |  | --> | 0.38 | 0 | 0 | 0.41034 | 0 |  | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6686 | -6.6956
MV/LV Substation WI***934 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.348 | 5.6 |  | --> | 0.38 | 0 | 0 | 0.40782 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1052 | -6.0638
MV/LV Substation WI***950Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =118kVA. | --> | 0.19 | 0 | 0.031122 | 0.21208 | 0 |  | --> | C16 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8924 | -8.4217
MV/LV Substation WI***974 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.1 |  | --> | 0.095 | 0 | 0 | 0.10015 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7387 | -6.7183
MV/LV Substation WI***989 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =135kVA. | --> | 0.19 | 0 | 0.025194 | 0.20964 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8531 | -8.9932
MV/LV Substation WI***989X |  | 20 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0.024 | 1.1 |  | --> | 0.02375 | 0 | 0 | 0.025151 | 0 |  | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7293 | -6.7233
MV/LV Substation WK***760Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 3.1 |  | --> | 0.19 | 0 | 0.05928 | 0.20465 | 0 |  | --> | C18 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6462 | -7.2133
MV/LV Substation WO***001 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 7.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.3kW. | --> | C17 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8585 | -7.659
MV/LV Substation WO***001 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.409 | 0.4 |  | --> | 0.5985 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9826 | -9.1134
MV/LV Substation WO***001Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0.018525 | 0.41005 | 0 |  | --> | C22 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8513 | -8.3154
MV/LV Substation WO***002Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4095 | -6.2361
MV/LV Substation WO***005 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =25kVA. | --> | 0.0475 | 0 | 0.004446 | 0.053659 | 0 |  | --> | C16 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.1929 | -8.5646
MV/LV Substation WO***007 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | E15 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5626 | -8.7662
MV/LV Substation WO***007X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.3 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1008 | -8.2846
MV/LV Substation WO***008 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =354kVA. | --> | 0.38 | 0 | 0 | 0.40692 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9014 | -8.1709
MV/LV Substation WO***008 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.8 |  | --> | 0.095 | 0 | 0 | 0.1003 | 0 |  | --> | E12 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8089 | -8.4818
MV/LV Substation WO***008Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 3.5 |  | --> | 0.38 | 0 | 0.028158 | 0.40782 | 0 |  | --> | C12 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.0139 | -6.4136
MV/LV Substation WO***012X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 1.5 |  | --> | 0.19 | 0 | 0 | 0.20331 | 0 |  | --> | C11 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.262 | -9.7032
MV/LV Substation WO***013 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0.011856 | 0.10402 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8523 | -9.0137
MV/LV Substation WO***013X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =301kVA. | --> | 0.38 | 0 | 0.021489 | 0 | 0 | Constrained,otherwise capacity available =414.8kW. | --> | E20 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9393 | -7.9924
MV/LV Substation WO***014 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8539 | -9.0095
MV/LV Substation WO***016 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =276kVA. | --> | 0.38 | 0 | 0.00741 | 0.4184 | 0 |  | --> | C17 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1625 | -6.903
MV/LV Substation WO***016Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.129 | 3.9 |  | --> | 0.19 | 0 | 0.013338 | 0.2105 | 0 |  | --> | C12 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9909 | -6.3914
MV/LV Substation WO***022Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 3.9 |  | --> | 0.095 | 0 | 0 | 0.10373 | 0 |  | --> | C18 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9816 | -6.3842
MV/LV Substation WO***024Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0.005928 | 0 | 0 | Constrained,otherwise capacity available =411.1kW. | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6849 | -6.2921
MV/LV Substation WO***025Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.684 | -6.291
MV/LV Substation WO***028 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =58kVA. | --> | 0.19 | 0 | 0 | 0.22046 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7079 | -6.4972
MV/LV Substation WO***030 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =267kVA. | --> | 0.38 | 0 | 0.018525 | 0.41971 | 0 |  | --> | C18 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2808 | -9.0253
MV/LV Substation WO***030 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =83kVA. | --> | 0.095 | 0 | 0 | 0.10255 | 0 |  | --> | C12 ex PORTLAW | Portlaw [T41,T42] | BUTLERSTOWN |  | 52.2943 | -7.3103
MV/LV Substation WO***030 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =453kVA. | --> | 0.5985 | 0 | 0.015561 | 0.5 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7101 | -6.5016
MV/LV Substation WO***030X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =291kVA. | --> | 0.38 | 0 | 0.01482 | 0.41622 | 0 |  | --> | C17 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5598 | -6.7745
MV/LV Substation WO***030Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 1.1 |  | --> | 0.095 | 0 | 0.011856 | 0.10387 | 0 |  | --> | C17 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0869 | -7.9002
MV/LV Substation WO***032 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =34kVA. | --> | 0.0475 | 0 | 0 | 0.052373 | 0 |  | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9381 | -8.5603
MV/LV Substation WO***033Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =349kVA. | --> | 0.38 | 0 | 0.002964 | 0.40767 | 0 |  | --> | C20 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8772 | -8.4901
MV/LV Substation WO***034 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =309kVA. | --> | 0.38 | 0 | 0 | 0.41359 | 0 |  | --> | C17 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2859 | -9.6914
MV/LV Substation WO***034Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C17 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4619 | -6.2115
MV/LV Substation WO***039 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.141 | 17.8 |  | --> | 0.19 | 0 | 0.014079 | 0.20877 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6447 | -6.2345
MV/LV Substation WO***040 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =21kVA. | --> | 0.0475 | 0 | 0.00741 | 0.05422 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2692 | -6.3139
MV/LV Substation WO***040 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0.009633 | 0.20569 | 0 |  | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3295 | -8.1933
MV/LV Substation WO***042 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.333 | 6.2 |  | --> | 0.38 | 0 | 0 | 0.41005 | 0 |  | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3813 | -7.9318
MV/LV Substation WO***042X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.299 | 4.5 |  | --> | 0.38 | 0 | 0.03705 | 0.41505 | 0 |  | --> | C19 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1798 | -6.1287
MV/LV Substation WO***043Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.244 | 0.3 |  | --> | 0.38 | 0 | 0.005187 | 0.42302 | 0 |  | --> | C16 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.399 | -6.2309
MV/LV Substation WO***044Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.248 | 0.3 |  | --> | 0.38 | 0 | 0.003705 | 0.42245 | 0 |  | --> | C16 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.4011 | -6.2308
MV/LV Substation WO***045 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 5.8 |  | --> | 0.38 | 0 | 0.011115 | 0.41138 | 0 |  | --> | C11 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2552 | -8.4668
MV/LV Substation WO***046 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =87kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102kW. | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.072 | -7.6787
MV/LV Substation WO***046 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 0.7 |  | --> | 0.19 | 0 | 0 | 0.21065 | 0 |  | --> | C15 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.64 | -9.4731
MV/LV Substation WO***048 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0.034827 | 0.5 | 0 |  | --> | C18 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.05 | -9.503
MV/LV Substation WO***050 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =51kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =107.2kW. | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0127 | -7.1478
MV/LV Substation WO***055 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 7.8 |  | --> | 0.19 | 0 | 0 | 0.20775 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7966 | -9.5413
MV/LV Substation WO***056X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =88kVA. | --> | 0.095 | 0 | 0.003705 | 0.10181 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9953 | -8.0658
MV/LV Substation WO***056Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0 | 0.21079 | 0 |  | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8757 | -8.3913
MV/LV Substation WO***059 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =261kVA. | --> | 0.38 | 0 | 0.090402 | 0.42058 | 0 |  | --> | C17 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3609 | -6.4453
MV/LV Substation WO***059Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 1.7 |  | --> | 0.19 | 0 | 0 | 0.20406 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9925 | -7.0013
MV/LV Substation WO***062 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 0.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102kW. | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8303 | -6.2346
MV/LV Substation WO***062Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =266kVA. | --> | 0.38 | 0 | 0.024453 | 0.41985 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3424 | -6.5529
MV/LV Substation WO***063Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =284kVA. | --> | 0.38 | 0 | 0.028158 | 0.41724 | 0 |  | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3425 | -6.5508
MV/LV Substation WO***067 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =283kVA. | --> | 0.38 | 0 | 0.022971 | 0 | 0 | Constrained,otherwise capacity available =417.4kW. | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9349 | -7.7353
MV/LV Substation WO***067X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =145kVA. | --> | 0.19 | 0 | 0.013338 | 0.20818 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3669 | -8.8892
MV/LV Substation WO***070Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =131kVA. | --> | 0.19 | 0 | 0.03705 | 0.21022 | 0 |  | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2371 | -7.0115
MV/LV Substation WO***071 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.32 | 13.1 |  | --> | 0.38 | 0 | 0.005928 | 0.41197 | 0 |  | --> | C12 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2258 | -6.6592
MV/LV Substation WO***074Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =488kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4085 | -6.2363
MV/LV Substation WO***078X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.0768 | -7.4506
MV/LV Substation WO***081 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 2.3 |  | --> | 0.38 | 0 | 0.028899 | 0.41608 | 0 |  | --> | C11 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2781 | -9.7022
MV/LV Substation WO***081Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =76kVA. | --> | 0.095 | 0 | 0 | 0.10358 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4464 | -6.4829
MV/LV Substation WO***082Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4442 | -6.4839
MV/LV Substation WO***085 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =288kVA. | --> | 0.5985 | 0 | 0.078546 | 0.5 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3089 | -6.209
MV/LV Substation WO***085 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2167 | -6.1135
MV/LV Substation WO***089X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.057 | 1.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =106.3kW. | --> | C11 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.61 | -9.1073
MV/LV Substation WO***090 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.169 | 0.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =204.7kW. | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8327 | -6.2322
MV/LV Substation WO***091 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.004 | 2.8 |  | --> | 0.095 | 0 | 0.005928 | 0.11357 | 0 |  | --> | E16 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.8434 | -7.3936
MV/LV Substation WO***094 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.428 | 13.4 |  | --> | 0.5985 | 0 | 0.008892 | 0.5 | 0 |  | --> | C17 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2761 | -6.143
MV/LV Substation WO***096 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =27kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =53.4kW. | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.934 | -6.2424
MV/LV Substation WO***096 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 18.7 |  | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C13 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8136 | -6.1579
MV/LV Substation WO***096 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =325kVA. | --> | 0.38 | 0 | 0 | 0.41123 | 0 |  | --> | E41 ex KINSALE | Kinsale [T423] | TRABEG |  | 51.6985 | -8.5194
MV/LV Substation WO***097 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | E11 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8237 | -8.7616
MV/LV Substation WO***098Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.288 | 6.4 |  | --> | 0.38 | 0 | 0.02223 | 0.41666 | 0 |  | --> | C17 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4332 | -7.8987
MV/LV Substation WO***100Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 4.9 |  | --> | 0.19 | 0 | 0.03705 | 0.20376 | 0 |  | --> | C11 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3956 | -6.1911
MV/LV Substation WO***102X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =103.1kW. | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.876 | -7.5785
MV/LV Substation WO***104X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.325 | 2.8 |  | --> | 0.38 | 0 | 0 | 0.41123 | 0 |  | --> | C18 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.3003 | -6.1884
MV/LV Substation WO***106Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 0.4 |  | --> | 0.38 | 0 | 0.003705 | 0.40871 | 0 |  | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1134 | -7.5839
MV/LV Substation WO***106Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.19 | 0 | 0.016302 | 0.21464 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5078 | -6.4719
MV/LV Substation WO***107Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =191kVA. | --> | 0.19 | 0 | 0.002964 | 0.20136 | 0 |  | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2131 | -8.5159
MV/LV Substation WO***112X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.1 |  | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | E24 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1081 | -7.8964
MV/LV Substation WO***112Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 1.1 |  | --> | 0.19 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =208.5kW. | --> | C15 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4441 | -9.0486
MV/LV Substation WO***116 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.0557 | -7.6929
MV/LV Substation WO***116 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =286kVA. | --> | 0.38 | 0 | 0.020007 | 0.41695 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2834 | -6.3378
MV/LV Substation WO***117 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =246kVA. | --> | 0.38 | 0 | 0.026676 | 0.42273 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2812 | -6.3345
MV/LV Substation WO***118X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3288 | -6.3543
MV/LV Substation WO***121 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =106kVA. | --> | 0.19 | 0 | 0.022971 | 0.21379 | 0 |  | --> | C28 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6473 | -6.6842
MV/LV Substation WO***122X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.365 | 4.6 |  | --> | 0.38 | 0 | 0 | 0.40528 | 0 |  | --> | C18 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.294 | -6.1412
MV/LV Substation WO***132 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 4.5 |  | --> | 0.38 | 0 | 0.013338 | 0.41271 | 0 |  | --> | C16 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1894 | -6.1119
MV/LV Substation WO***136 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15247 | 0.2 | Constrained,otherwise capacity available =312kVA. | --> | 0.38 | 0 | 0.011115 | 0.41315 | 0 |  | --> | C19 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2721 | -6.2493
MV/LV Substation WO***136 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =158kVA. | --> | 0.19 | 0 | 0.034827 | 0.20628 | 0 |  | --> | C12 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9058 | -8.4341
MV/LV Substation WO***136X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9301 | -7.7203
MV/LV Substation WO***138 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.478 | 6 |  | --> | 0.5985 | 0 | 0.020007 | 0.5 | 0 |  | --> | C11 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8851 | -8.4504
MV/LV Substation WO***143X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =43kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.1kW. | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2687 | -7.2686
MV/LV Substation WO***145X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.443 | 4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3494 | -6.2675
MV/LV Substation WO***145Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0.01482 | 0 | 0 | Constrained,otherwise capacity available =416.1kW. | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3868 | -6.9286
MV/LV Substation WO***147 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.412 | 13.9 |  | --> | 0.5985 | 0 | 0.01482 | 0.5 | 0 |  | --> | C21 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2922 | -6.202
MV/LV Substation WO***148X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0.008151 | 0.072493 | 0 | Constrained,otherwise capacity available =200kW. | --> | C15 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.889 | -8.0515
MV/LV Substation WO***151X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 0.4 |  | --> | 0.38 | 0 | 0.027417 | 0 | 0 | Constrained,otherwise capacity available =406.2kW. | --> | C13 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9387 | -8.9441
MV/LV Substation WO***151Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 12.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.994 | -6.0867
MV/LV Substation WO***152X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =136kVA. | --> | 0.19 | 0 | 0.013338 | 0.20949 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3541 | -6.4612
MV/LV Substation WO***155X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3753 | -6.3052
MV/LV Substation WO***157X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.089 | 2.3 |  | --> | 0.19 | 0 | 0.01482 | 0.21618 | 0 |  | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.2103 | -9.2221
MV/LV Substation WO***158Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =150kVA. | --> | 0.19 | 0 | 0.014079 | 0.20745 | 0 |  | --> | C21 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8861 | -8.5195
MV/LV Substation WO***161X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.107 | 1.3 |  | --> | 0.19 | 0 | 0.002223 | 0.21365 | 0 |  | --> | C22 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7694 | -8.5058
MV/LV Substation WO***162Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =489kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3881 | -6.3917
MV/LV Substation WO***166X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C18 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8213 | -6.4026
MV/LV Substation WO***166Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0.005928 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1453 | -8.2685
MV/LV Substation WO***169X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =169kVA. | --> | 0.19 | 0 | 0 | 0.20465 | 0 |  | --> | E25 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.7306 | -7.4055
MV/LV Substation WO***180Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 18.7 |  | --> | 0.38 | 0 | 0.008151 | 0.41491 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7947 | -6.1778
MV/LV Substation WO***182 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.379 | 4.5 |  | --> | 0.5985 | 0 | 0.08151 | 0.5 | 0 |  | --> | C18 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2904 | -6.3093
MV/LV Substation WO***184 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 12.2 |  | --> | 0.19 | 0 | 0.014079 | 0.22019 | 0 |  | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9947 | -6.0796
MV/LV Substation WO***189 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.097 | -7.7835
MV/LV Substation WO***189X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0.20301 | 0 |  | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9913 | -8.0672
MV/LV Substation WO***195Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =151kVA. | --> | 0.19 | 0 | 0.008892 | 0 | 0 | Constrained,otherwise capacity available =207.3kW. | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.0904 | -7.8523
MV/LV Substation WO***196X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =161kVA. | --> | 0.19 | 0 | 0 | 0.20584 | 0 |  | --> | C16 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8316 | -6.3896
MV/LV Substation WO***197Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 18.7 |  | --> | 0.38 | 0 | 0.004446 | 0.41329 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.797 | -6.1768
MV/LV Substation WO***197Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4413 | -6.4784
MV/LV Substation WO***201X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.38033 | 0.4 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.25 | -6.1873
MV/LV Substation WO***204X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.314 | 0.9 |  | --> | 0.38 | 0 | 0 | 0.41285 | 0 |  | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8201 | -9.8765
MV/LV Substation WO***206 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 0.9 |  | --> | 0.095 | 0 | 0 | 0.10121 | 0 |  | --> | C11 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0568 | -9.471
MV/LV Substation WO***208 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.312 | 1.4 |  | --> | 0.38 | 0 | 0.016302 | 0.41315 | 0 |  | --> | C13 ex DODDER ROAD | Dodder Road [T42] | MILLTOWN (DR) |  | 53.2998 | -6.274
MV/LV Substation WO***212Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C13 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7683 | -7.1361
MV/LV Substation WO***213 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.202 | 1.8 |  | --> | 0.38 | 0 | 0.008892 | 0.42899 | 0 |  | --> | C13 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6772 | -8.6532
MV/LV Substation WO***214Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | E18 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6852 | -8.9339
MV/LV Substation WO***215 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =467kVA. | --> | 0.5985 | 0 | 0.042237 | 0.5 | 0 |  | --> | C13 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6539 | -8.6016
MV/LV Substation WO***218 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.279 | 1.8 |  | --> | 0.38 | 0 | 0.016302 | 0.41797 | 0 |  | --> | C13 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6753 | -8.6628
MV/LV Substation WO***221X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =156kVA. | --> | 0.19 | 0 | 0.039273 | 0.20657 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3792 | -6.0601
MV/LV Substation WO***228X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0.00741 | 0.2048 | 0 |  | --> | E47 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3665 | -8.8907
MV/LV Substation WO***231X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.1 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C17 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6978 | -8.7701
MV/LV Substation WO***232 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 3 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.7kW. | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9831 | -7.6955
MV/LV Substation WO***232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.214 | 2.9 |  | --> | 0.38 | 0 | 0.040755 | 0.4273 | 0 |  | --> | C19 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2744 | -6.2003
MV/LV Substation WO***233 |  | 20 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.028 | 1.8 |  | --> | 0.03135 | 0 | 0.003705 | 0.033751 | 0 |  | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7068 | -8.4837
MV/LV Substation WO***234 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.022971 | 0.5 | 0 |  | --> | C11 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0616 | -9.4827
MV/LV Substation WO***234 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7077 | -8.4853
MV/LV Substation WO***238 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0.003705 | 0.10402 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2185 | -6.1221
MV/LV Substation WO***238Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.114 | 18.7 |  | --> | 0.19 | 0 | 0.008892 | 0.21265 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7982 | -6.1766
MV/LV Substation WO***240Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 0.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104.6kW. | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8319 | -6.2389
MV/LV Substation WO***240Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =165kVA. | --> | 0.19 | 0 | 0.006669 | 0.20525 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8545 | -8.5641
MV/LV Substation WO***243Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.10475 | 0 |  | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5754 | -9.3795
MV/LV Substation WO***246 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.293 | 1.8 |  | --> | 0.38 | 0 | 0.004446 | 0.41593 | 0 |  | --> | C14 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6791 | -8.6509
MV/LV Substation WO***249X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =140kVA. | --> | 0.19 | 0 | 0.002964 | 0.20891 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3212 | -6.3793
MV/LV Substation WO***250X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =229kVA. | --> | 0.38 | 0 | 0.020748 | 0.42516 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3213 | -6.3777
MV/LV Substation WO***250Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 6 |  | --> | 0.38 | 0 | 0 | 0.40827 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3849 | -6.3705
MV/LV Substation WO***253X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4117 | -6.2399
MV/LV Substation WO***257Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.7 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C17 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.784 | -7.1372
MV/LV Substation WO***258X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.444 | 4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3497 | -6.2679
MV/LV Substation WO***260Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =176kVA. | --> | 0.19 | 0 | 0.003705 | 0.20361 | 0 |  | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3561 | -7.1967
MV/LV Substation WO***264Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.045201 | 0.5 | 0 |  | --> | C19 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2221 | -6.6516
MV/LV Substation WO***267X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.8 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.25 | -8.469
MV/LV Substation WO***268 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.323 | 13.4 |  | --> | 0.38 | 0 | 0.016302 | 0.41153 | 0 |  | --> | C20 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2657 | -6.1452
MV/LV Substation WO***269X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =160kVA. | --> | 0.19 | 0 | 0.008151 | 0.20598 | 0 |  | --> | C18 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8258 | -6.3993
MV/LV Substation WO***269X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8221 | -8.5654
MV/LV Substation WO***270X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0.011856 | 0.20569 | 0 |  | --> | C18 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8265 | -6.3967
MV/LV Substation WO***272X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 1 |  | --> | 0.095 | 0 | 0 | 0.1027 | 0 |  | --> | E17 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7448 | -7.7178
MV/LV Substation WO***272X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.327 | 5.7 |  | --> | 0.38 | 0 | 0.004446 | 0.41094 | 0 |  | --> | C11 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.9934 | -6.393
MV/LV Substation WO***275 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 0.6 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.3kW. | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.5232 | -7.7552
MV/LV Substation WO***276Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.464 | 13.5 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8445 | -8.9842
MV/LV Substation WO***284X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.9 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3711 | -6.2093
MV/LV Substation WO***284Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0.004446 | 0.050453 | 0 |  | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5232 | -6.2115
MV/LV Substation WO***287Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 0.4 |  | --> | 0.19 | 0 | 0.032604 | 0.20569 | 0 |  | --> | E18 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8539 | -6.5631
MV/LV Substation WO***288Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =307kVA. | --> | 0.38 | 0 | 0.013338 | 0.41388 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.507 | -6.4683
MV/LV Substation WO***292X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 1.6 |  | --> | 0.095 | 0 | 0 | 0.1027 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.043 | -7.6789
MV/LV Substation WO***292Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =343kVA. | --> | 0.38 | 0 | 0 | 0.40856 | 0 |  | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3764 | -6.4034
MV/LV Substation WO***293Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =94kVA. | --> | 0.095 | 0 | 0 | 0.10091 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4732 | -6.3756
MV/LV Substation WO***297X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =328kVA. | --> | 0.38 | 0 | 0.002223 | 0.41079 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5111 | -8.8693
MV/LV Substation WO***298 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.284 | 6 |  | --> | 0.38 | 0 | 0 | 0.41724 | 0 |  | --> | C20 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3817 | -6.3195
MV/LV Substation WO***298 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 4.9 |  | --> | 0.38 | 0 | 0.010374 | 0.41373 | 0 |  | --> | C19 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3877 | -6.1761
MV/LV Substation WO***299 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.269 | 4.9 |  | --> | 0.38 | 0 | 0.010374 | 0.41942 | 0 |  | --> | C22 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3896 | -6.1742
MV/LV Substation WO***304 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8307 | -6.9272
MV/LV Substation WO***304Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =146kVA. | --> | 0.19 | 0 | 0.014079 | 0.20804 | 0 |  | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4295 | -6.1367
MV/LV Substation WO***307X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =289kVA. | --> | 0.38 | 0 | 0.018525 | 0.41651 | 0 |  | --> | C15 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.352 | -6.465
MV/LV Substation WO***310X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =28kVA. | --> | 0.19 | 0 | 0.017784 | 0.2245 | 0 |  | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.352 | -6.3707
MV/LV Substation WO***312X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.4 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C11 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.0891 | -9.314
MV/LV Substation WO***315X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =25kVA. | --> | 0.0475 | 0 | 0 | 0.053659 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9141 | -8.5731
MV/LV Substation WO***317Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.1 |  | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4412 | -9.05
MV/LV Substation WO***321Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2961 | -6.8232
MV/LV Substation WO***323X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =224kVA. | --> | 0.38 | 0 | 0.040755 | 0.42588 | 0 |  | --> | C20 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3538 | -6.3781
MV/LV Substation WO***324X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =109kVA. | --> | 0.19 | 0 | 0.015561 | 0.21336 | 0 |  | --> | C20 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3543 | -6.38
MV/LV Substation WO***325 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =135kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =209.6kW. | --> | C18 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.9958 | -7.4656
MV/LV Substation WO***326 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =52.1kW. | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1874 | -8.354
MV/LV Substation WO***334X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =186kVA. | --> | 0.19 | 0 | 0.003705 | 0.20211 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3775 | -6.0648
MV/LV Substation WO***334Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4089 | -6.236
MV/LV Substation WO***335X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.2 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8408 | -7.5824
MV/LV Substation WO***336 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.864 | -8.0336
MV/LV Substation WO***339Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =131kVA. | --> | 0.19 | 0 | 0.001482 | 0.21022 | 0 |  | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2908 | -6.8167
MV/LV Substation WO***340 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.1977 | -6.7455
MV/LV Substation WO***341 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C06 ex AHANE | Ahane [T102] | AHANE |  | 52.6672 | -8.5207
MV/LV Substation WO***341X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0.06669 | 0.2 | 0 |  | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.9016 | -6.4307
MV/LV Substation WO***347 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =40kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.5kW. | --> | E11 ex MACROOM | Macroom [T422] | MACROOM |  | 51.9469 | -8.8241
MV/LV Substation WO***347Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3768 | -6.4027
MV/LV Substation WO***357 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.268 | 11.9 |  | --> | 0.38 | 0 | 0.020007 | 0.41956 | 0 |  | --> | C27 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.3402 | -9.179
MV/LV Substation WO***369Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C18 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.5059 | -7.4521
MV/LV Substation WO***385Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 6.4 |  | --> | 0.38 | 0 | 0.023712 | 0.41049 | 0 |  | --> | C17 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4341 | -7.8977
MV/LV Substation WO***387Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =135kVA. | --> | 0.19 | 0 | 0.003705 | 0.20964 | 0 |  | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.8679 | -8.1631
MV/LV Substation WO***389Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.38 | 0 | 0.054834 | 0.4431 | 0 |  | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2844 | -6.8588
MV/LV Substation WO***391 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 2.3 |  | --> | 0.19 | 0 | 0.006669 | 0.21165 | 0 |  | --> | C11 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2796 | -9.7012
MV/LV Substation WO***393 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.278 | 11.9 |  | --> | 0.38 | 0 | 0.012597 | 0.41811 | 0 |  | --> | C33 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2612 | -9.1254
MV/LV Substation WO***395 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 3.9 |  | --> | 0.38 | 0 | 0.002964 | 0.40513 | 0 |  | --> | C24 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2776 | -9.0045
MV/LV Substation WO***398Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0 | 0.20301 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3536 | -6.4604
MV/LV Substation WO***4002 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =120kVA. | --> | 0.19 | 0 | 0.012597 | 0.2118 | 0 |  | --> | C21 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1403 | -8.6594
MV/LV Substation WO***4009 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4738 | -6.3652
MV/LV Substation WO***401 |  | 10 kV | _ | LV | 25 kVA :Kiosk Substation | 0.025 | --> | 0.025 | 0 | 5.8 |  | --> | 0.02375 | 0 | 0.018525 | 0.031272 | 0 |  | --> | C20 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2741 | -8.5161
MV/LV Substation WO***4020 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.9 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C13 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0441 | -9.4224
MV/LV Substation WO***403 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9341 | -8.7881
MV/LV Substation WO***4039 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 11.9 |  | --> | 0.0475 | 0 | 0 | 0.051052 | 0 |  | --> | C36 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.309 | -9.1333
MV/LV Substation WO***4047 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =100kVA. | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | E12 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4706 | -6.5691
MV/LV Substation WO***4047 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E12 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.084 | -9.8175
MV/LV Substation WO***4052 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.0528 | -7.6872
MV/LV Substation WO***4054 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 2.8 |  | --> | 0.095 | 0 | 0 | 0.1024 | 0 |  | --> | E13 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.4424 | -7.4843
MV/LV Substation WO***405Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.2 |  | --> | 0.0475 | 0 | 0.003705 | 0.052949 | 0 |  | --> | E16 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.6951 | -8.7324
MV/LV Substation WO***4064 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =346kVA. | --> | 0.38 | 0 | 0.011115 | 0.40812 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2363 | -6.1269
MV/LV Substation WO***4070 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.15247 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2616 | -6.2255
MV/LV Substation WO***4072 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =195kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200.8kW. | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.0822 | -7.7718
MV/LV Substation WO***407X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =98kVA. | --> | 0.095 | 0 | 0.017043 | 0.1003 | 0 |  | --> | C26 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9015 | -8.2399
MV/LV Substation WO***4086 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9394 | -7.7375
MV/LV Substation WO***4096 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.5114 | -8.4328
MV/LV Substation WO***4096 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.3 |  | --> | 0.0475 | 0 | 0 | 0.053518 | 0 |  | --> | E31 ex TRIM | Trim [T421] | NAVAN |  | 53.5505 | -6.8932
MV/LV Substation WO***4097 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 4.9 |  | --> | 0.38 | 0 | 0 | 0.40287 | 0 |  | --> | C22 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3909 | -6.1754
MV/LV Substation WO***409X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =249kVA. | --> | 0.38 | 0 | 0.017784 | 0.4223 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.325 | -6.3791
MV/LV Substation WO***4111 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.195 | 0.8 |  | --> | 0.19 | 0 | 0.003705 | 0.20076 | 0 |  | --> | C18 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8475 | -9.4293
MV/LV Substation WO***411Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0.002223 | 0 | 0 | Constrained,otherwise capacity available =104.2kW. | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3834 | -6.9419
MV/LV Substation WO***4120 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.15247 | 0.2 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2673 | -6.2069
MV/LV Substation WO***4156 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.134 | 12.2 |  | --> | 0.19 | 0 | 0 | 0.20978 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0195 | -6.1018
MV/LV Substation WO***4162 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0.002964 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 53.0091 | -6.3087
MV/LV Substation WO***4163 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 14.2 |  | --> | 0.5985 | 0 | 0.005928 | 0.5 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2895 | -6.385
MV/LV Substation WO***4163 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C16 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1026 | -7.8099
MV/LV Substation WO***4165 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =306kVA. | --> | 0.38 | 0 | 0.009633 | 0 | 0 | Constrained,otherwise capacity available =414kW. | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9365 | -6.2381
MV/LV Substation WO***4168 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C11 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3297 | -7.4067
MV/LV Substation WO***416Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =326kVA. | --> | 0.38 | 0 | 0.00741 | 0.41108 | 0 |  | --> | C22 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8089 | -8.3993
MV/LV Substation WO***4170 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.00741 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2172 | -6.1179
MV/LV Substation WO***4171 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2179 | -6.1179
MV/LV Substation WO***4172 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2178 | -6.1156
MV/LV Substation WO***4173 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2181 | -6.1136
MV/LV Substation WO***4174 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6411 | -7.0581
MV/LV Substation WO***418 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =92kVA. | --> | 0.095 | 0 | 0 | 0.10121 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9425 | -8.1131
MV/LV Substation WO***4206 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.36 | 1.1 |  | --> | 0.38 | 0 | 0 | 0.40603 | 0 |  | --> | C19 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1036 | -7.9121
MV/LV Substation WO***421 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 0.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =100.3kW. | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8325 | -6.2349
MV/LV Substation WO***4211 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1555 | -8.3452
MV/LV Substation WO***4211 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.9kW. | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1232 | -6.5563
MV/LV Substation WO***4222 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2485 | -6.1581
MV/LV Substation WO***4245 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex WATLING STREET | Watling Street [T41,T42] | FRANCIS STREET |  | 53.3478 | -6.2829
MV/LV Substation WO***424Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =339kVA. | --> | 0.38 | 0 | 0.011856 | 0.37942 | 0 | Constrained,otherwise capacity available =409.2kW. | --> | E14 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1672 | -8.6085
MV/LV Substation WO***4259 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 6.4 |  | --> | 0.38 | 0 | 0.19266 | 0.4 | 0 |  | --> | C20 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4257 | -7.8942
MV/LV Substation WO***4269 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.4 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | C14 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7613 | -6.8393
MV/LV Substation WO***431X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =97kVA. | --> | 0.19 | 0 | 0.004446 | 0.21506 | 0 |  | --> | C14 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3374 | -6.404
MV/LV Substation WO***4404 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.349 | 1.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =407.7kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4419 | -9.0527
MV/LV Substation WO***4404 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | E14 ex CRANE | Crane [T122] | CRANE |  | 52.5325 | -6.6319
MV/LV Substation WO***443 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.6kW. | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6524 | -8.2674
MV/LV Substation WO***4446 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0.002223 | 0.5 | 0 |  | --> | C30 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6499 | -6.6531
MV/LV Substation WO***4457 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0.050303 | 0 |  | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9126 | -6.8586
MV/LV Substation WO***448 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =255kVA. | --> | 0.38 | 0 | 0.017784 | 0.42144 | 0 |  | --> | C16 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8893 | -8.4235
MV/LV Substation WO***449 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0.011115 | 0.052949 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8419 | -9.0277
MV/LV Substation WO***452 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 0.2 |  | --> | 0.0475 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =52.4kW. | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.893 | -7.5436
MV/LV Substation WO***452X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =226kVA. | --> | 0.38 | 0 | 0.012597 | 0.42559 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3235 | -6.3829
MV/LV Substation WO***452Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.4 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8312 | -6.2316
MV/LV Substation WO***459Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.268 | 18.7 |  | --> | 0.38 | 0 | 0.003705 | 0.41956 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7975 | -6.1787
MV/LV Substation WO***460 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 5.6 |  | --> | 0.095 | 0 | 0.004446 | 0.10575 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0952 | -6.0689
MV/LV Substation WO***461X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =305kVA. | --> | 0.38 | 0 | 0 | 0.41417 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3235 | -6.3799
MV/LV Substation WO***462 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 6.2 |  | --> | 0.0475 | 0 | 0 | 0.050152 | 0 |  | --> | C24 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3789 | -7.8204
MV/LV Substation WO***481Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 0.4 |  | --> | 0.19 | 0 | 0 | 0.20151 | 0 |  | --> | E12 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7892 | -6.729
MV/LV Substation WO***492Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =149kVA. | --> | 0.19 | 0 | 0.018525 | 0 | 0 | Constrained,otherwise capacity available =207.6kW. | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3875 | -6.9298
MV/LV Substation WO***496Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.8623 | -8.2181
MV/LV Substation WO***498X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =72kVA. | --> | 0.095 | 0 | 0.009633 | 0.10417 | 0 |  | --> | E18 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3372 | -7.0538
MV/LV Substation WO***499Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.9037 | -8.1479
MV/LV Substation WO***504Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0.003705 | 0.41608 | 0 |  | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9415 | -8.5622
MV/LV Substation WO***508X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =248kVA. | --> | 0.38 | 0 | 0.03705 | 0.42245 | 0 |  | --> | C18 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3577 | -6.428
MV/LV Substation WO***510Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =309kVA. | --> | 0.38 | 0 | 0.027417 | 0.41359 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9024 | -8.1604
MV/LV Substation WO***513 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0.003705 | 0.2 | 0 |  | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5755 | -9.0043
MV/LV Substation WO***517Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =228kVA. | --> | 0.38 | 0 | 0.026676 | 0.42531 | 0 |  | --> | C21 ex CASTLETROY | Castletroy [T41,T42] | ARDNACRUSHA |  | 52.6645 | -8.5473
MV/LV Substation WO***520Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 16.1 |  | --> | 0.38 | 0 | 0.016302 | 0.40871 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3896 | -6.4441
MV/LV Substation WO***522Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6342 | -7.2434
MV/LV Substation WO***523 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 13.9 |  | --> | 0.38 | 0 | 0.026676 | 0.41884 | 0 |  | --> | C21 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2864 | -6.1964
MV/LV Substation WO***524Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 12.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9937 | -6.087
MV/LV Substation WO***533X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9579 | -8.1689
MV/LV Substation WO***538X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =143kVA. | --> | 0.19 | 0 | 0.011856 | 0.20848 | 0 |  | --> | C16 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8355 | -8.9953
MV/LV Substation WO***539Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0.011115 | 0 | 0 | Constrained,otherwise capacity available =412.7kW. | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0437 | -7.3193
MV/LV Substation WO***540Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1932 | -6.9872
MV/LV Substation WO***541 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.3kW. | --> | C23 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7592 | -8.4041
MV/LV Substation WO***541X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =42kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.2kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.1255 | -7.4801
MV/LV Substation WO***541Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =46kVA. | --> | 0.0475 | 0 | 0 | 0.050604 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1918 | -6.9879
MV/LV Substation WO***542 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2597 | -7.3159
MV/LV Substation WO***542X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =51.8kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.126 | -7.474
MV/LV Substation WO***547Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =307kVA. | --> | 0.38 | 0 | 0.002223 | 0 | 0 | Constrained,otherwise capacity available =413.9kW. | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1779 | -6.5302
MV/LV Substation WO***550 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.25 | 2.1 |  | --> | 0.38 | 0 | 0.005187 | 0 | 0 | Constrained,otherwise capacity available =422.2kW. | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9967 | -7.5059
MV/LV Substation WO***550Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | E14 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3397 | -6.9304
MV/LV Substation WO***552Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 4.6 |  | --> | 0.38 | 0 | 0.01482 | 0.41049 | 0 |  | --> | C18 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.912 | -8.3922
MV/LV Substation WO***554Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =249kVA. | --> | 0.38 | 0 | 0.019266 | 0.4223 | 0 |  | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.294 | -6.6857
MV/LV Substation WO***557X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0 | 0.41271 | 0 |  | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.946 | -8.0812
MV/LV Substation WO***561Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =163kVA. | --> | 0.19 | 0 | 0.016302 | 0.20554 | 0 |  | --> | C20 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3758 | -6.6013
MV/LV Substation WO***562 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0.008151 | 0.10373 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9155 | -8.5777
MV/LV Substation WO***565Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 1.1 |  | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E12 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6595 | -6.6614
MV/LV Substation WO***565Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =366kVA. | --> | 0.38 | 0 | 0 | 0.40513 | 0 |  | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5055 | -6.4688
MV/LV Substation WO***568Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 9.5 |  | --> | 0.38 | 0 | 0 | 0.40453 | 0 |  | --> | C14 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7435 | -8.7336
MV/LV Substation WO***573Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1974 | -7.0089
MV/LV Substation WO***576Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =139kVA. | --> | 0.19 | 0 | 0.009633 | 0.20906 | 0 |  | --> | C12 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3732 | -6.4997
MV/LV Substation WO***579X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =185kVA. | --> | 0.19 | 0 | 0 | 0.20226 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.912 | -8.5743
MV/LV Substation WO***580Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =199kVA. | --> | 0.19 | 0 | 0 | 0.20015 | 0 |  | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2945 | -6.8203
MV/LV Substation WO***581X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.2 |  | --> | 0.095 | 0 | 0.008892 | 0.10076 | 0 |  | --> | E16 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.703 | -8.7014
MV/LV Substation WO***583X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | C16 ex CURRA | Curra [T41] | SOMERSET |  | 53.0525 | -8.4053
MV/LV Substation WO***586Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =352kVA. | --> | 0.38 | 0 | 0.01482 | 0.40722 | 0 |  | --> | C21 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9708 | -6.7261
MV/LV Substation WO***589 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.021 | 3 |  | --> | 0.03135 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =34.8kW. | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9825 | -7.6987
MV/LV Substation WO***591 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.4 |  | --> | 0.095 | 0 | 0 | 0.10076 | 0 |  | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.223 | -6.5425
MV/LV Substation WO***595 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200.3kW. | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1905 | -7.0444
MV/LV Substation WO***609 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 2 |  | --> | 0.0475 | 0 | 0.002223 | 0 | 0 | Constrained,otherwise capacity available =51.9kW. | --> | E18 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5286 | -8.9473
MV/LV Substation WO***615 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =269kVA. | --> | 0.38 | 0 | 0.040014 | 0.41942 | 0 |  | --> | C15 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2884 | -6.2205
MV/LV Substation WO***617X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 17.8 |  | --> | 0.38 | 0 | 0.009633 | 0.40393 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6455 | -6.2389
MV/LV Substation WO***619Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.5 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | E12 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4137 | -6.8101
MV/LV Substation WO***624 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =261kVA. | --> | 0.38 | 0 | 0.023712 | 0.42058 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2778 | -6.3127
MV/LV Substation WO***626 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.6 |  | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | C12 ex CLOONBANNIN | Cloonbannin [T42] | GLENLARA |  | 52.1435 | -9.123
MV/LV Substation WO***626X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0 | 0.10373 | 0 |  | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9432 | -8.1153
MV/LV Substation WO***628 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0.050303 | 0 |  | --> | E22 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.183 | -8.4682
MV/LV Substation WO***628 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 6.2 |  | --> | 0.0475 | 0 | 0.001482 | 0 | 0 | Constrained,otherwise capacity available =52.2kW. | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.3422 | -8.8656
MV/LV Substation WO***636 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.056 | 1.3 |  | --> | 0.095 | 0 | 0.008151 | 0.10647 | 0 |  | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5338 | -6.9701
MV/LV Substation WO***637Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.357 | 2.5 |  | --> | 0.38 | 0 | 0.009633 | 0.40648 | 0 |  | --> | E18 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7159 | -6.8485
MV/LV Substation WO***639X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =330kVA. | --> | 0.38 | 0 | 0.017043 | 0.41049 | 0 |  | --> | C17 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3748 | -6.3781
MV/LV Substation WO***644 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =311kVA. | --> | 0.38 | 0 | 0.014079 | 0.41329 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2777 | -6.3098
MV/LV Substation WO***645 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =342kVA. | --> | 0.38 | 0 | 0.018525 | 0.40871 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2763 | -6.309
MV/LV Substation WO***649X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0 | 0.41197 | 0 |  | --> | C18 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3587 | -6.4251
MV/LV Substation WO***654X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =292kVA. | --> | 0.38 | 0 | 0.025194 | 0.41608 | 0 |  | --> | C20 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8322 | -8.9983
MV/LV Substation WO***654Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.095 | 0 | 0 | 0.11091 | 0 |  | --> | C14 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6041 | -6.9338
MV/LV Substation WO***655X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | C15 ex CRANNY | Cranny [T41] | ENNIS |  | 52.7159 | -9.3322
MV/LV Substation WO***661 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =22kVA. | --> | 0.0475 | 0 | 0.006669 | 0 | 0 | Constrained,otherwise capacity available =54.1kW. | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1059 | -7.5304
MV/LV Substation WO***661 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 1.4 |  | --> | 0.38 | 0 | 0.037791 | 0.41403 | 0 |  | --> | C13 ex DODDER ROAD | Dodder Road [T42] | MILLTOWN (DR) |  | 53.3014 | -6.275
MV/LV Substation WO***687 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.065 | 1.6 |  | --> | 0.095 | 0 | 0.003705 | 0.10518 | 0 |  | --> | C16 ex CURRA | Curra [T41] | SOMERSET |  | 53.0533 | -8.4016
MV/LV Substation WO***687Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.268 | 5 |  | --> | 0.38 | 0 | 0 | 0.41956 | 0 |  | --> | C11 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6555 | -7.2423
MV/LV Substation WO***690 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.159 | 1.6 |  | --> | 0.19 | 0 | 0.008151 | 0.20613 | 0 |  | --> | C16 ex CURRA | Curra [T41] | SOMERSET |  | 53.0478 | -8.3988
MV/LV Substation WO***691X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3348 | -6.9715
MV/LV Substation WO***697 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 0.2 |  | --> | 0.095 | 0 | 0.008892 | 0.10299 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2659 | -6.3131
MV/LV Substation WO***697X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =154kVA. | --> | 0.19 | 0 | 0.001482 | 0.20687 | 0 |  | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2126 | -8.5145
MV/LV Substation WO***701X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =155kVA. | --> | 0.19 | 0 | 0.009633 | 0.20672 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8414 | -9.0322
MV/LV Substation WO***703X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8407 | -9.0282
MV/LV Substation WO***711Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.496 | 6 |  | --> | 0.5985 | 0 | 0.03705 | 0.5 | 0 |  | --> | C13 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8799 | -8.4664
MV/LV Substation WO***713 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.042 | 0.1 |  | --> | 0.095 | 0 | 0 | 0.10844 | 0 |  | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.1284 | -8.7371
MV/LV Substation WO***718X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.128 | 1.6 |  | --> | 0.19 | 0 | 0.003705 | 0.21065 | 0 |  | --> | C16 ex CURRA | Curra [T41] | SOMERSET |  | 53.051 | -8.4009
MV/LV Substation WO***722X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 2.6 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C17 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0547 | -7.6162
MV/LV Substation WO***722X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =33kVA. | --> | 0.0475 | 0 | 0 | 0.052518 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4782 | -6.3698
MV/LV Substation WO***723X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =223kVA. | --> | 0.38 | 0 | 0.022971 | 0.42602 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2755 | -6.3341
MV/LV Substation WO***732Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 1.1 |  | --> | 0.38 | 0 | 0.00741 | 0 | 0 | Constrained,otherwise capacity available =414kW. | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4418 | -9.0465
MV/LV Substation WO***735X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.184 | 1.4 |  | --> | 0.19 | 0 | 0 | 0.20241 | 0 |  | --> | E18 ex CONG | Cong [T421,T422] | CLOON |  | 53.5441 | -9.3624
MV/LV Substation WO***736 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.021 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0.05422 | 0 |  | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7198 | -7.5108
MV/LV Substation WO***747 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =384kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =402.4kW. | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.125 | -7.4757
MV/LV Substation WO***749Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 2.5 |  | --> | 0.19 | 0 | 0 | 0.20211 | 0 |  | --> | E18 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7172 | -6.8496
MV/LV Substation WO***752 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.4 |  | --> | 0.095 | 0 | 0.00741 | 0.10076 | 0 |  | --> | C20 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8327 | -6.9711
MV/LV Substation WO***753X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.213 | 12.2 |  | --> | 0.38 | 0 | 0.15709 | 0.42744 | 0 |  | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0039 | -6.1079
MV/LV Substation WO***754Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =31kVA. | --> | 0.0475 | 0 | 0 | 0.052806 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4763 | -6.3651
MV/LV Substation WO***755X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 1.9 |  | --> | 0.38 | 0 | 0.016302 | 0 | 0 | Constrained,otherwise capacity available =416.1kW. | --> | C16 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8573 | -9.3157
MV/LV Substation WO***765Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 0.4 |  | --> | 0.095 | 0 | 0.002964 | 0.10661 | 0 |  | --> | E12 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7971 | -6.7308
MV/LV Substation WO***767X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =157kVA. | --> | 0.19 | 0 | 0.020007 | 0.20643 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2748 | -6.338
MV/LV Substation WO***769X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4739 | -6.3769
MV/LV Substation WO***772Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.731 | -6.4738
MV/LV Substation WO***773X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 2.1 |  | --> | 0.19 | 0 | 0.033345 | 0.20935 | 0 |  | --> | C14 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2738 | -8.7334
MV/LV Substation WO***773Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =48kVA. | --> | 0.0475 | 0 | 0 | 0.050303 | 0 |  | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.926 | -6.6594
MV/LV Substation WO***774 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.401 | 4.5 |  | --> | 0.5985 | 0 | 0.022971 | 0.5 | 0 |  | --> | C16 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.189 | -6.1097
MV/LV Substation WO***780 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0.014079 | 0.41197 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4146 | -6.4711
MV/LV Substation WO***784 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =285kVA. | --> | 0.38 | 0 | 0.02223 | 0.4171 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1363 | -6.058
MV/LV Substation WO***785X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7306 | -6.8423
MV/LV Substation WO***786X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.184 | 1.4 |  | --> | 0.19 | 0 | 0 | 0.20241 | 0 |  | --> | C14 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7329 | -6.8441
MV/LV Substation WO***790 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 8.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =102.1kW. | --> | E16 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7673 | -9.5555
MV/LV Substation WO***790X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =350kVA. | --> | 0.38 | 0 | 0.003705 | 0.40752 | 0 |  | --> | C32 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.646 | -6.6831
MV/LV Substation WO***795 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =73kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =104kW. | --> | E22 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9743 | -7.8892
MV/LV Substation WO***797 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.1 |  | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C14 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3265 | -8.4682
MV/LV Substation WO***800X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =245kVA. | --> | 0.38 | 0 | 0.021489 | 0.42288 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2741 | -6.3264
MV/LV Substation WO***804 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 2.9 |  | --> | 0.19 | 0 | 0 | 0.20421 | 0 |  | --> | C18 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2865 | -6.2063
MV/LV Substation WO***808 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =44kVA. | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2755 | -6.3181
MV/LV Substation WO***812Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4747 | -6.3647
MV/LV Substation WO***819 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C26 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.8035 | -8.2797
MV/LV Substation WO***820X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 3 |  | --> | 0.19 | 0 | 0.006669 | 0.20818 | 0 |  | --> | C24 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6764 | -6.3077
MV/LV Substation WO***821 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.5985 | 0 | 0.002964 | 0.5 | 0 |  | --> | C11 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.057 | -9.4715
MV/LV Substation WO***824X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =257kVA. | --> | 0.38 | 0 | 0.01482 | 0.42115 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2739 | -6.3232
MV/LV Substation WO***825X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =208kVA. | --> | 0.38 | 0 | 0.008151 | 0.42815 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2759 | -6.3298
MV/LV Substation WO***827X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =129kVA. | --> | 0.19 | 0 | 0.024453 | 0.2105 | 0 |  | --> | C28 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6485 | -6.6813
MV/LV Substation WO***827Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 9.5 |  | --> | 0.19 | 0 | 0.015561 | 0.20376 | 0 |  | --> | C13 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7326 | -8.7583
MV/LV Substation WO***834 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =191kVA. | --> | 0.19 | 0 | 0 | 0.20136 | 0 |  | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1999 | -6.9864
MV/LV Substation WO***848 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =399kVA. | --> | 0.38 | 0 | 0.02964 | 0.40015 | 0 |  | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5021 | -7.2298
MV/LV Substation WO***853X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =141kVA. | --> | 0.19 | 0 | 0.00741 | 0.20877 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2739 | -6.3217
MV/LV Substation WO***854 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 13.4 |  | --> | 0.38 | 0 | 0.003705 | 0.40618 | 0 |  | --> | C18 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2779 | -6.1153
MV/LV Substation WO***857 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 18.8 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3439 | -6.2703
MV/LV Substation WO***865 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C15 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.8763 | -8.3103
MV/LV Substation WO***865 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.8kW. | --> | E18 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.1228 | -7.8801
MV/LV Substation WO***865 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =38kVA. | --> | 0.0475 | 0 | 0.003705 | 0 | 0 | Constrained,otherwise capacity available =51.8kW. | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6538 | -8.4267
MV/LV Substation WO***867X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2394 | -7.0641
MV/LV Substation WO***868X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.319 | 6.2 |  | --> | 0.38 | 0 | 0.008892 | 0.41212 | 0 |  | --> | C17 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3829 | -7.9131
MV/LV Substation WO***876X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =287kVA. | --> | 0.38 | 0 | 0.030381 | 0.41681 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2756 | -6.3254
MV/LV Substation WO***898Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =49kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | C12 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.722 | -8.7902
MV/LV Substation WO***901 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.8813 | -7.8994
MV/LV Substation WO***908X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 7.2 |  | --> | 0.0475 | 0 | 0.014079 | 0.052518 | 0 |  | --> | C06 ex AHANE | Ahane [T102] | AHANE |  | 52.6703 | -8.5184
MV/LV Substation WO***909X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =168kVA. | --> | 0.19 | 0 | 0.01482 | 0.2048 | 0 |  | --> | E18 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9142 | -8.5754
MV/LV Substation WO***910 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.6 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.2kW. | --> | E17 ex BELMULLET | Belmullet [T421] | BELLACORICK |  | 54.229 | -10.0083
MV/LV Substation WO***914X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =157kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =206.4kW. | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6838 | -6.293
MV/LV Substation WO***930 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0.00741 | 0.10061 | 0 |  | --> | E16 ex CLONROCHE | Clonroche [T421,T422] | WEXFORD |  | 52.548 | -6.736
MV/LV Substation WO***932Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.379 | 1.7 |  | --> | 0.38 | 0 | 0.004446 | 0.40318 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9929 | -6.999
MV/LV Substation WO***933X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =70kVA. | --> | 0.19 | 0 | 0.033345 | 0.21882 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2737 | -6.3297
MV/LV Substation WO***936 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.8 |  | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3669 | -7.6273
MV/LV Substation WO***937Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4 |  | --> | 0.5985 | 0 | 0.002964 | 0.5 | 0 |  | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8634 | -7.1953
MV/LV Substation WO***944Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =358kVA. | --> | 0.38 | 0 | 0.006669 | 0.40633 | 0 |  | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5115 | -8.8729
MV/LV Substation WO***956 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 5.8 |  | --> | 0.0475 | 0 | 0.003705 | 0.052373 | 0 |  | --> | C20 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2716 | -8.5173
MV/LV Substation WO***957 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.053 | 1.3 |  | --> | 0.19 | 0 | 0.020007 | 0.22114 | 0 |  | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5333 | -6.9606
MV/LV Substation WO***963X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =360kVA. | --> | 0.38 | 0 | 0.002223 | 0.40603 | 0 |  | --> | C16 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8755 | -8.5179
MV/LV Substation WO***970Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =321kVA. | --> | 0.38 | 0 | 0.002223 | 0.41182 | 0 |  | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6964 | -6.2602
MV/LV Substation WO***971 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.364 | 4.5 |  | --> | 0.38 | 0 | 0 | 0.40543 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1865 | -6.1004
MV/LV Substation WO***978Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 0.4 |  | --> | 0.38 | 0 | 0.011856 | 0.40408 | 0 |  | --> | E12 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7953 | -6.7294
MV/LV Substation WO***981 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =47kVA. | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2754 | -8.2002
MV/LV Substation WO***982 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =45kVA. | --> | 0.0475 | 0 | 0 | 0.050753 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2832 | -7.9771
MV/LV Substation WO***989Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =300kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =414.9kW. | --> | E11 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3978 | -6.9264
MV/LV Substation WO***992 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.3 |  | --> | 0.095 | 0 | 0 | 0.10166 | 0 |  | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1055 | -8.2368
MV/LV Substation WO***992Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.162 | 0.4 |  | --> | 0.19 | 0 | 0.016302 | 0.20569 | 0 |  | --> | E12 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7927 | -6.7264
MV/LV Substation WO***993X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | E16 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8495 | -9.2766
MV/LV Substation WO***997X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =21kVA. | --> | 0.0475 | 0 | 0.012597 | 0.05422 | 0 |  | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8436 | -9.0256
MV/LV Substation WO***999X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0 | 0.20569 | 0 |  | --> | C22 ex COBH | Cobh [T41,T42] | COW CROSS |  | 51.8513 | -8.3147
MV/LV Substation WP***4009 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.9 |  | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50.5kW. | --> | C12 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2528 | -6.9567
MV/LV Substation WP***4281 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.8 |  | --> | 0.095 | 0 | 0 | 0.1 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8091 | -9.5454
MV/LV Substation WR***018 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 0.4 |  | --> | 0.38 | 0 | 0.019266 | 0.41461 | 0 |  | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7981 | -6.7446
MV/LV Substation WR***052 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.092 | 5.7 |  | --> | 0.38 | 0 | 0.00741 | 0.44418 | 0 |  | --> | C23 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0071 | -6.4011
MV/LV Substation WR***064 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 5.8 |  | --> | 0.38 | 0 | 0.02223 | 0.4171 | 0 |  | --> | C13 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2672 | -8.5014
MV/LV Substation WR***086Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =496kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3896 | -6.0746
MV/LV Substation WR***188Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =127kVA. | --> | 0.19 | 0 | 0.018525 | 0.21079 | 0 |  | --> | C22 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8056 | -8.4069
MV/LV Substation WR***578 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =194kVA. | --> | 0.19 | 0 | 0 | 0.20091 | 0 |  | --> | C17 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5422 | -6.7141
MV/LV Substation WR***896X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =375kVA. | --> | 0.38 | 0 | 0 | 0.40378 | 0 |  | --> | C18 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2458 | -7.1436
MV/LV Substation WR***968 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =333kVA. | --> | 0.38 | 0 | 0 | 0.41005 | 0 |  | --> | C13 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3548 | -6.2644
MV/LV Substation WU***4293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =376kVA. | --> | 0.38 | 0 | 0.013338 | 0.40363 | 0 |  | --> | C15 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9696 | -6.4145
MV/LV Substation WU***4294 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =393kVA. | --> | 0.38 | 0 | 0 | 0.40106 | 0 |  | --> | C15 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9659 | -6.4144
MV/LV Substation WV***4066 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =85kVA. | --> | 0.095 | 0 | 0 | 0.10225 | 0 |  | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8282 | -10.1661
MV/LV Substation WW***4085 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 0.2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.3kW. | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.9317 | -7.4589
MV/LV Substation WW***4166 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.476 | 11.9 |  | --> | 0.5985 | 0 | 0.056316 | 0.5 | 0 |  | --> | C32 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2896 | -9.0752
MV/LV Substation WW***4174 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 9.5 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C14 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7518 | -8.7184
MV/LV Substation WW***929X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =190kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =201.5kW. | --> | C17 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0835 | -7.7025
MV/LV Substation WY***048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =230kVA. | --> | 0.38 | 0 | 0.052611 | 0.42502 | 0 |  | --> | C25 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2839 | -6.251
MV/LV Substation WY***060 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.14262 | 0.1 | Constrained,otherwise capacity available =484kVA. | --> | 0.5985 | 0 | 0.003705 | 0.5 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3393 | -6.4737
MV/LV Substation WY***072Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =84kVA. | --> | 0.095 | 0 | 0.002964 | 0.1024 | 0 |  | --> | C12 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8885 | -8.5311
MV/LV Substation WY***093 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =180kVA. | --> | 0.19 | 0 | 0.036309 | 0.20301 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5431 | -6.3491
MV/LV Substation WY***120Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =11kVA. | --> | 0.0475 | 0 | 0 | 0.05559 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5284 | -6.3127
MV/LV Substation WY***131X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.15247 | 0.2 | Constrained,otherwise capacity available =392kVA. | --> | 0.38 | 0 | 0 | 0.40121 | 0 |  | --> | C14 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2803 | -6.2448
MV/LV Substation WY***159 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.224 | 4.3 |  | --> | 0.38 | 0 | 0.033345 | 0.42588 | 0 |  | --> | C19 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2894 | -6.1637
MV/LV Substation WY***161X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.14262 | 0.1 | Constrained,otherwise capacity available =382kVA. | --> | 0.38 | 0 | 0.004446 | 0.40272 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3398 | -6.472
MV/LV Substation WY***173X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.8 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2814 | -6.2421
MV/LV Substation WY***217 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =166kVA. | --> | 0.19 | 0 | 0 | 0.2051 | 0 |  | --> | C21 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2205 | -7.4746
MV/LV Substation WY***320X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.8 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2857 | -6.2392
MV/LV Substation WY***323 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =236kVA. | --> | 0.38 | 0 | 0.02964 | 0.42417 | 0 |  | --> | C12 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2505 | -6.1361
MV/LV Substation WY***335X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.019092 | 0 | Constrained,otherwise capacity available =315kVA. | --> | 0.38 | 0 | 0.009633 | 0 | 0 | Constrained,otherwise capacity available =412.7kW. | --> | C18 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1318 | -6.8959
MV/LV Substation WY***363X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.8 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2857 | -6.2391
MV/LV Substation WY***4169 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.9 |  | --> | 0.95 | 0 | 0.02964 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.322 | -6.267
MV/LV Substation WY***4193 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.14262 | 0.1 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C15 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3397 | -6.4706
MV/LV Substation WY***499 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 5.3 |  | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C12 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3062 | -8.4611
MV/LV Substation WY***524X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =75kVA. | --> | 0.095 | 0 | 0.008151 | 0 | 0 | Constrained,otherwise capacity available =103.7kW. | --> | C13 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.6763 | -8.6833
MV/LV Substation WY***531 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.411 | 0.9 |  | --> | 0.5985 | 0 | 0.020007 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3222 | -6.2671
MV/LV Substation WY***548 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5396 | -6.3433
MV/LV Substation WY***571 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.305 | 4 |  | --> | 0.38 | 0 | 0.018525 | 0.41417 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2685 | -6.1153
MV/LV Substation WY***819Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5395 | -6.3553
MV/LV Substation WY***830Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =37kVA. | --> | 0.0475 | 0 | 0 | 0.051937 | 0 |  | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1906 | -6.7747
MV/LV Substation WY***844X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =324kVA. | --> | 0.38 | 0 | 0.018525 | 0.41138 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8861 | -8.62
MV/LV Substation WY***908Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 1.7 |  | --> | 0.19 | 0 | 0 | 0.20271 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9988 | -6.9885
MV/LV Substation WY***969X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.183 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.6kW. | --> | E11 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5947 | -8.9765
MV/LV Substation YA***056X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =320kVA. | --> | 0.38 | 0 | 0.011115 | 0.41197 | 0 |  | --> | C19 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3008 | -6.2285
MV/LV Substation YA***311X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =400kVA. | --> | 0.38 | 0 | 0.008151 | 0.4 | 0 |  | --> | C11 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3885 | -6.0677
MV/LV Substation YA***816 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 18.7 |  | --> | 0.0475 | 0 | 0 | 0.051496 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7998 | -6.1712
MV/LV Substation YE***019 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.065 | 5.3 |  | --> | 0.095 | 0 | 0 | 0.10518 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2814 | -8.4499
MV/LV Substation YE***021Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0.2 | 0 |  | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5693 | -6.4556
MV/LV Substation YE***065 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =335kVA. | --> | 0.5985 | 0 | 0.005928 | 0.5 | 0 |  | --> | C20 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7218 | -6.3445
MV/LV Substation YE***068 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.26 | 3 |  | --> | 0.38 | 0 | 0.010374 | 0.42072 | 0 |  | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8618 | -8.205
MV/LV Substation YE***068Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =268kVA. | --> | 0.38 | 0 | 0.032604 | 0.41956 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4207 | -6.4765
MV/LV Substation YE***097 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =51kVA. | --> | 0.19 | 0 | 0.027417 | 0.22141 | 0 |  | --> | C21 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4491 | -6.1638
MV/LV Substation YE***108 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =109kVA. | --> | 0.19 | 0 | 0 | 0.21336 | 0 |  | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2447 | -7.1299
MV/LV Substation YE***148X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 5.3 |  | --> | 0.38 | 0 | 0 | 0.40856 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2801 | -8.4524
MV/LV Substation YE***149X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 5.3 |  | --> | 0.38 | 0 | 0 | 0.40841 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2788 | -8.4531
MV/LV Substation YE***189X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =284kVA. | --> | 0.38 | 0 | 0.00741 | 0.41724 | 0 |  | --> | C34 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3264 | -6.3813
MV/LV Substation YE***206 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.8 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | E14 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.809 | -8.3273
MV/LV Substation YE***233X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.3 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.281 | -8.4527
MV/LV Substation YE***251X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.095 | 0 | 0 | 0.10061 | 0 |  | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7292 | -6.5584
MV/LV Substation YE***253 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =296kVA. | --> | 0.38 | 0 | 0.043719 | 0.41549 | 0 |  | --> | C17 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4511 | -6.1698
MV/LV Substation YE***258Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =133kVA. | --> | 0.19 | 0 | 0.011856 | 0.20993 | 0 |  | --> | C17 ex VIRGINIA | Virginia [T41,T42] | MEATH HILL |  | 53.8331 | -7.0694
MV/LV Substation YE***278 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 4.1 |  | --> | 0.095 | 0 | 0.018525 | 0.10195 | 0 |  | --> | C14 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3292 | -8.5024
MV/LV Substation YE***4193 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.6193 | -6.9209
MV/LV Substation YE***4278 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =381kVA. | --> | 0.38 | 0 | 0 | 0.40287 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3303 | -6.3859
MV/LV Substation YE***459 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 13.1 |  | --> | 0.0475 | 0 | 0.00741 | 0.050753 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2254 | -6.7359
MV/LV Substation YE***580X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0.018525 | 0.051643 | 0 |  | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9412 | -8.6693
MV/LV Substation YE***678X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =153kVA. | --> | 0.19 | 0 | 0 | 0.20701 | 0 |  | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2254 | -7.0039
MV/LV Substation YE***881X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 13.1 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2352 | -6.733
MV/LV Substation YE***911 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.261 | 5.3 |  | --> | 0.38 | 0 | 0.011115 | 0.42058 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3064 | -8.5643
MV/LV Substation YE***930Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =162kVA. | --> | 0.19 | 0 | 0.018525 | 0.20569 | 0 |  | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2253 | -6.9993
MV/LV Substation YE***931Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =131kVA. | --> | 0.19 | 0 | 0 | 0.21022 | 0 |  | --> | C32 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6456 | -6.699
MV/LV Substation YE***999 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =39kVA. | --> | 0.0475 | 0 | 0 | 0.051643 | 0 |  | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7353 | -6.3473
MV/LV Substation YO***007Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =50kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =50kW. | --> | C15 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2461 | -8.3645
MV/LV Substation YO***052X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =390kVA. | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =401.5kW. | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.953 | -7.8698
MV/LV Substation YO***073Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E19 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.6935 | -7.8199
MV/LV Substation YO***109X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =385kVA. | --> | 0.38 | 0 | 0.01482 | 0 | 0 | Constrained,otherwise capacity available =402.3kW. | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9511 | -7.8734
MV/LV Substation YO***124X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained,otherwise capacity available =500kVA. | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CAMDEN ROW | Camden Row [T41] | FRANCIS STREET |  | 53.3393 | -6.2641
MV/LV Substation YO***224X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =348kVA. | --> | 0.38 | 0 | 0.00741 | 0 | 0 | Constrained,otherwise capacity available =407.8kW. | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.936 | -7.859
MV/LV Substation YO***240 |  | 20 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.02375 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =25.2kW. | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9666 | -7.8631
MV/LV Substation YO***286X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =183kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =202.6kW. | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.97 | -7.8622
MV/LV Substation YO***353 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =36kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.1kW. | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9711 | -7.8593
MV/LV Substation YO***354 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3 |  | --> | 0.0475 | 0 | 0 | 0.050903 | 0 |  | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8934 | -8.2961
MV/LV Substation YO***4063 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =90kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =101.5kW. | --> | C20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9494 | -7.8088
MV/LV Substation YO***4262 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.5 |  | --> | 0.0475 | 0 | 0 | 0.05 | 0 |  | --> | E13 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.693 | -6.936
MV/LV Substation YO***430 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =96kVA. | --> | 0.19 | 0 | 0.021489 | 0 | 0 | Constrained,otherwise capacity available =215.2kW. | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0847 | -7.6304
MV/LV Substation YO***545Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.1 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.9018 | -8.4667
MV/LV Substation YO***571 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained,otherwise capacity available =30kVA. | --> | 0.0475 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =52.9kW. | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9507 | -7.7281
MV/LV Substation YO***648 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =110.9kW. | --> | E19 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 52.0063 | -7.9069
MV/LV Substation YO***670 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 1.4 |  | --> | 0.095 | 0 | 0 | 0.10195 | 0 |  | --> | E13 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2046 | -6.4077
MV/LV Substation YO***877X |  | 10 kV | _ | LV | 25 kVA :Pole Substation | 0.025 | --> | 0.025 | 0 | 0 | Constrained,otherwise capacity available =24kVA. | --> | 0.02375 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =25.2kW. | --> | C20 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.8571 | -7.8153
MV/LV Substation YO***887 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.276 | 16.1 |  | --> | 0.38 | 0 | 0.003705 | 0.4184 | 0 |  | --> | C22 ex RINGSEND | Ringsend [T101,T102] | POOLBEG |  | 53.3446 | -6.2269
MV/LV Substation YO***911 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 4.4 |  | --> | 0.0475 | 0 | 0 | 0.050453 | 0 |  | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9083 | -6.8037
MV/LV Substation ZA***060 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0.4 | 0 |  | --> | C25 ex SRAH | Srah [T43] | THORNSBERRY |  | 53.2835 | -7.5069
MV/LV Substation ZA***876 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained,otherwise capacity available =386kVA. | --> | 0.38 | 0 | 0 | 0.40212 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.128 | -6.0622
MV/LV Substation ZE***462 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.8 |  | --> | 0.095 | 0 | 0 | 0.10045 | 0 |  | --> | C19 ex RECESS | Recess [T41] | SCREEB |  | 53.416 | -9.7948
MV/LV Substation ZE***539X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.5 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =500kW. | --> | C18 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9604 | -7.7137
MV/LV Substation ZE***662Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained,otherwise capacity available =200kVA. | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained,otherwise capacity available =200kW. | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.365 | -6.9665
MV/LV Substation ZI***330 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.194 | 1.4 |  | --> | 0.19 | 0 | 0 | 0.20091 | 0 |  | --> | C11 ex DODDER ROAD | Dodder Road [T42] | MILLTOWN (DR) |  | 53.3054 | -6.2727
MV/LV Substation ZI***4230 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.2 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8958 | -8.4868
MV/LV Substation ZO***130 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.1 |  | --> | 0.5985 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3536 | -6.3024
MV/LV Substation ZU***019 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 17.8 |  | --> | 0.095 | 0 | 0.002223 | 0.10255 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6726 | -6.2176
NAAS (015000) 38 kV STATION | Naas [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 2.2702 | 13.635 | 4.954 |  | --> |  | Kilteel [T141,T142] | KILTEEL |  | 53.1987 | -6.6602
NAVAN (694000) 110 kV STATION | Navan [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 15.2361 | N/A, consult Eirgrid |  | --> | 77.9 | 0 | 43.0606 | 48.0292 | 0 |  | --> |  | Transmission Source | NAVAN |  | 53.705 | -6.7109
NENAGH (946000) 110 kV STATION | Nenagh [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 3.5912 | N/A, consult Eirgrid |  | --> | 30.1 | 0 | 20.5425 | 16.4264 | 0 |  | --> |  | Transmission Source | NENAGH |  | 52.8664 | -8.1737
NENAGH (946000) 110 kV STATION | Nenagh [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.9993 | 3.6 |  | --> | 12.4 | 4.75 | 4.0979 | 10.3804 | 4.8273 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8664 | -8.1737
NENAGH (946000) 110 kV STATION | Nenagh [T422] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 3.5912 | 3.6 | Constrained,otherwise capacity available =8.7 MVA | --> | 9.8 | 0 | 9.59 | 0.21 | 0 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8664 | -8.1737
NEWBRIDGE (695000) 110 kV STATION | Newbridge [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 18.5124 | 31.2347 | 0 |  | --> |  | Transmission Source | NEWBRIDGE |  | 53.1981 | -6.8437
NEWBROOK (465000) 38 kV STATION | Newbrook [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.6 |  | --> | 4.8 | 0 | 0.58787 | 5.386 | 0 |  | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.5214 | -7.3821
NEWCASTLEWEST (185000) 38 kV STATION | Newcastlewest [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.0534 | 12.7 |  | --> | 6.2 | 2.375 | 1.4154 | 0 | 0 | Constrained,otherwise capacity available =6.2 MW Firm & 2.4 MW Non-firm | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4479 | -9.0462
NEWMARKET (DR) (217000) 38 kV STATION | Newmarket (dr) [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 1.041 | 31.2 |  | --> | 9.5 | 0 | 0.23728 | 11.1657 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3347 | -6.2819
NEWMARKET (SR) (481000) 38 kV STATION | Newmarket (sr) [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.1601 | 38.7 |  | --> | 6.2 | 2.375 | 0.51726 | 6.9778 | 2.4232 |  | --> |  | Glenlara [T142] | GLENLARA |  | 52.21 | -8.9982
NEWPORT (260000) 38 kV STATION | Newport [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.6738 | 8.4 |  | --> | 4.8 | 0 | 1.0065 | 4.2886 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8858 | -9.5017
NEWTOWNCUNNINGHAM (503000) 38 kV STATION | Newtowncunningham [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.0886 | 13.8 |  | --> | 6.2 | 2.375 | 0.59608 | 0 | 0 | Constrained,otherwise capacity available =6.9 MW Firm & 2.4 MW Non-firm | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 55.008 | -7.4657
NORTH QUAYS (981000) 110 kV STATION | North Quays [T101,T102,T103] | 110 kV | _ | MV | 3x20 MVA @ 10 kV | 60 | --> | 45 | 6.9871 | 54.9 |  | --> | 24.7 | 9.4991 | 0.31775 | 29.787 | 9.9507 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3532 | -6.2311
OAKFIELD (240000) 38 kV STATION | Oakfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.7778 | 27.9 |  | --> | 12.4 | 4.75 | 1.6487 | 12.2854 | 4.7814 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2573 | -8.505
OLDBAWN (365000) 38 kV STATION | Oldbawn [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =0.2 MVA | --> | 12.4 | 4.75 | 2.3613 | 12.1375 | 4.8246 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2762 | -6.3517
OLDCASTLE (538000) 38 kV STATION | Oldcastle [T41,T422] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.6754 | 3.6 |  | --> | 6.2 | 2.375 | 3.7309 | 3.2732 | 2.3918 |  | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.7816 | -7.1696
ORANMORE (487000) 38 kV STATION | Oranmore [T41,T44] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 2.1126 | 13.5557 | 5.1258 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2884 | -8.9245
OUGHTERARD (444000) 38 kV STATION | Oughterard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 6.5266 | 6.9 |  | --> | 6.2 | 2.375 | 0.88345 | 5.2915 | 2.375 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4249 | -9.3117
OUGHTRAGH (696000) 110 kV STATION | Oughtragh [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 30.1 | 0 | 18.7599 | 18.1243 | 0 |  | --> |  | Transmission Source | OUGHTRAGH |  | 52.1418 | -9.7044
PALLAS (559000) 38 kV STATION | Pallas [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 0.91794 | 0 | 0 | Constrained,otherwise capacity available =7 MW Firm & 2.5 MW Non-firm | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.0378 | -7.3205
PALMERSTOWN (302000) 38 kV STATION | Palmerstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =2.8 MVA | --> | 12.4 | 4.75 | 1.1626 | 13.5676 | 4.8276 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.3595 | -6.3721
PARKMORE (551000) 38 kV STATION | Parkmore [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 0.29394 | 8.5484 | 2.8544 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.3021 | -8.9846
PATRICKSWELL (077000) 38 kV STATION | Patrickswell [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 1.959 | 6.0695 | 2.4894 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.5919 | -8.7527
PELLETSTOWN (092000) 110 kV STATION | Pelletstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 5.9558 | 88 |  | --> | 24.7 | 9.5 | 2.1356 | 26.139 | 9.5798 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3788 | -6.3228
PEMBROKE (094000) 38 kV STATION | Pembroke [T41,T42,T43,T44] | 38 kV | _ | MV | 4x10 MVA @ 10 kV | 40 | --> | 30 | 3.3174 | 20.6 |  | --> | 12.4 | 4.75 | 0.70611 | 16.0584 | 5.2211 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | RINGSEND |  | 53.3428 | -6.2348
PHIBSBORO (307000) 38 kV STATION | Phibsboro [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 1.6888 | 14.2752 | 5.0949 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3564 | -6.2768
POLLERTON (242000) 38 kV STATION | Pollerton [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 20.5 |  | --> | 12.4 | 4.75 | 2.0411 | 8.9772 | 0 | Constrained,otherwise capacity available =13.7 MW Firm & 5 MW Non-firm | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8431 | -6.9178
POOLBEG (799000) 220 kV STATION | Poolbeg [TF3,TF4] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 54.886 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 82.3887 | 291.84 | 0 |  | --> |  | Transmission Source | POOLBEG |  | 53.3438 | -6.1967
POPPINTREE (983000) 110 kV STATION | Poppintree [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 |  | --> | 24.7 | 9.5 | 5.2234 | 25.2766 | 9.7577 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.4081 | -6.2756
PORTARLINGTON (160000) 38 kV STATION | Portarlington [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 3.8951 | 0 | 0 | Constrained,otherwise capacity available =3.5 MW Firm & 2.4 MW Non-firm | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.1553 | -7.1994
PORTARLINGTON (160000) 38 kV STATION | Portarlington [T43] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 0.70036 | 4.9116 | 0 |  | --> |  | Blake [T142] | BLAKE |  | 53.1553 | -7.1994
PORTLAOISE (201000) 110 kV STATION | Portlaoise [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 39.3 | 0 | 71.7759 | 0 | 0 |  | --> |  | Transmission Source | PORTLAOISE |  | 53.022 | -7.3041
PORTLAOISE (201000) 110 kV STATION | Portlaoise [T423,T424] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =7 MVA | --> | 12.4 | 4.75 | 0.65356 | 0 | 0 | Constrained,otherwise capacity available =12.9 MW Firm & 4.8 MW Non-firm | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.022 | -7.3041
PORTLAOISE (201000) 110 kV STATION | Portlaoise [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 1.2398 | 0 | 0 | Constrained,otherwise capacity available =15.1 MW Firm & 5.1 MW Non-firm | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.022 | -7.3041
PORTLAW (471000) 38 kV STATION | Portlaw [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0 | 0 | Constrained,otherwise capacity available =1.8 MVA | --> | 2.8 | 0.95 | 2.8297 | 0.25474 | 0.87832 |  | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.3033 | -7.3259
POTTERY ROAD (317000) 110 kV STATION | Pottery Road [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.4177 | 199 |  | --> | 24.7 | 9.5 | 1.2349 | 28.2236 | 9.7627 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2765 | -6.1586
PURCELLS INCH (485000) 38 kV STATION | Purcells Inch [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 7.5 | 3.0575 | 7.3 |  | --> | 3.1 | 2.375 | 0.79149 | 3.1135 | 2.4385 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.647 | -7.214
RAHANS (461000) 38 kV STATION | Rahans [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.73552 | 13 |  | --> | 4.8 | 0 | 0.19459 | 5.73 | 0 |  | --> |  | Moy [T141,T142] | MOY |  | 54.1078 | -9.1659
RAHEEN (401000) 38 kV STATION | Raheen [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 1.7587 | 14.4346 | 5.0039 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.6303 | -8.663
RAMPARTS (175000) 38 kV STATION | Ramparts [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.6871 | 20.5 |  | --> | 12.4 | 4.75 | 0.52383 | 13.6789 | 4.7929 |  | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0064 | -6.4047
RAMSTOWN (287000) 38 kV STATION | Ramstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.0311 | 3.1 |  | --> | 6.2 | 2.375 | 0.66505 | 6.5754 | 2.4043 |  | --> |  | Crane [T141] | CRANE |  | 52.6637 | -6.3193
RANDALSTOWN (463000) 38 kV STATION | Randalstown [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.0883 | 15.2 |  | --> | 4.8 | 0 | 0.34977 | 4.8351 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6705 | -6.7238
RANDALSTOWN (463000) 38 kV STATION | Randalstown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.8184 | 15.2 |  | --> | 4.8 | 0 | 0.12726 | 4.9986 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6705 | -6.7238
RATHDOWNEY (391000) 38 kV STATION | Rathdowney [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained,otherwise capacity available =0 MVA | --> | 4.8 | 0 | 0.43434 | 0 | 0 | Constrained,otherwise capacity available =5.2 MW Firm & 0 MW Non-firm | --> |  | Ikerrin [T141] | IKERRIN |  | 52.8498 | -7.5926
RATHDRUM (602000) 38 kV STATION | Rathdrum [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 55 |  | --> | 4.8 | 0 | 5.515 | 0 | 0 | Constrained,otherwise capacity available =0.2 MW Firm & 0 MW Non-firm | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.9421 | -6.2583
RATHKEALE (712000) 110 kV STATION | Rathkeale [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 1.982 | 12.7 |  | --> | 12.4 | 4.75 | 1.4592 | 0 | 0 | Constrained,otherwise capacity available =13.4 MW Firm & 4.8 MW Non-firm | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.5406 | -8.9745
RATHKEALE (712000) 110 kV STATION | Rathkeale [T141,T142] | 110 kV | _ | 38 kV | 2x30 MVA @ 38 kV | 60 | --> | 42 | 12.6638 | N/A, consult Eirgrid |  | --> | 37.5 | 0 | 62.8036 | 0 | 0 |  | --> |  | Transmission Source | RATHKEALE |  | 52.5406 | -8.9745
RATHMORE (221000) 38 kV STATION | Rathmore [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.89424 | 0.9 | Constrained,otherwise capacity available =2.6 MVA | --> | 6.2 | 2.375 | 0.70611 | 6.1499 | 2.401 |  | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0803 | -9.1908
RATHMULLAN (422000) 38 kV STATION | Rathmullan [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =0.8 MVA | --> | 12.4 | 4.75 | 1.2119 | 13.9477 | 4.8852 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7125 | -6.3661
REAMORE (197000) 110 kV STATION | Reamore [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.4824 | N/A, consult Eirgrid |  | --> | 60.2 | 0 | 44.35 | 15.8 | 0 |  | --> |  | Transmission Source | REAMORE |  | 52.2973 | -9.5504
REAMORE (197000) 110 kV STATION | Reamore [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.0198 | N/A, consult Eirgrid |  | --> | 60.2 | 0 | 45.1 | 15.5633 | 0 |  | --> |  | Transmission Source | REAMORE |  | 52.2973 | -9.5504
RECESS (581000) 38 kV STATION | Recess [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.7641 | 6.9 |  | --> | 4.8 | 0 | 0.33335 | 4.7739 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4543 | -9.7555
RICHMOND (713000) 110 kV STATION | Richmond [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 3.9354 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 29.272 | 19.8898 | 0 |  | --> |  | Transmission Source | RICHMOND |  | 53.7492 | -7.8419
RINEANNA (109000) 38 kV STATION | Rineanna [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.3932 | 3.8 |  | --> | 12.4 | 4.75 | 0.61825 | 14.6628 | 4.8911 |  | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.7096 | -8.8866
RINGASKIDDY 110KV (603000) 110 kV STATION | Ringaskiddy 110kv [T42] | 110 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4.5683 | 20.8 |  | --> | 9.5 | 0 | 0.55996 | 9.6527 | 0 |  | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8315 | -8.3406
RINGSEND (998000) 110 kV STATION | Ringsend [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 16.0833 | 54.9 |  | --> | 24.7 | 9.5 | 0.025453 | 29.1502 | 9.7485 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3447 | -6.2005
RIVERSTOWN (129000) 38 kV STATION | Riverstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 1.2119 | 6.5866 | 2.4553 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.9341 | -8.3652
ROCHES STREET (356000) 38 kV STATION | Roches Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =4.4 MVA | --> | 12.4 | 4.75 | 0.18638 | 14.6715 | 4.8355 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.659 | -8.6305
ROOSKY (434000) 38 kV STATION | Roosky [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.3106 | 3.9 |  | --> | 4.8 | 0 | 0.4836 | 4.8998 | 0 |  | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.8405 | -7.9198
ROSBERCON (179000) 38 kV STATION | Rosbercon [T424] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.2063 | 27 |  | --> | 14.6 | 0 | 14.28 | 0.27 | 0 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.3977 | -6.9486
ROSBERCON (179000) 38 kV STATION | Rosbercon [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0.23865 | 27 |  | --> | 1.5 | 1.1875 | 5.0218 | 0 | 0 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.3977 | -6.9486
ROSCOMMON (136000) 38 kV STATION | Roscommon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 8.5 |  | --> | 12.6 | 4.75 | 9.4787 | 5.7685 | 4.8431 |  | --> |  | Lanesboro [T141] | LANESBORO |  | 53.6305 | -8.1528
ROSCREA (055000) 38 kV STATION | Roscrea [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 1.179 | 0 | 0 | Constrained,otherwise capacity available =14.3 MW Firm & 4.9 MW Non-firm | --> |  | Ikerrin [T141] | IKERRIN |  | 52.9596 | -7.8072
ROSEHILL (193000) 38 kV STATION | Rosehill [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 7.3 |  | --> | 12.4 | 4.75 | 1.5592 | 13.8216 | 4.8918 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6399 | -7.2705
ROSS CARBERY (352000) 38 kV STATION | Ross Carbery [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.8833 | 44.2 |  | --> | 6.5 | 2.375 | 5.2028 | 2.1072 | 1.3358 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.6071 | -9.0157
ROSSGEIR (489000) 38 kV STATION | Rossgeir [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.24583 | 13.8 |  | --> | 6.2 | 2.375 | 1.0689 | 0 | 0 | Constrained,otherwise capacity available =6.5 MW Firm & 2.4 MW Non-firm | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.8614 | -7.5172
SAGGART (172000) 38 kV STATION | Saggart [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 0.94914 | 6.7479 | 2.4432 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.2731 | -6.4548
SALLINS (268000) 38 kV STATION | Sallins [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =0.7 MVA | --> | 12.4 | 4.75 | 2.5822 | 12.4619 | 4.8557 |  | --> |  | Griffinrath [T141,T142] | GRIFFINRATH |  | 53.2518 | -6.6629
SALLYNOGGIN ROAD (133000) 38 kV STATION | Sallynoggin Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2343 | 70.4 |  | --> | 12.4 | 4.75 | 2.7292 | 11.8402 | 4.8147 |  | --> |  | Cherrywood [T141,T142] | CHERRYWOOD |  | 53.281 | -6.1416
SALTHILL (161000) 110 kV STATION | Salthill [T101,T102] | 110 kV | _ | MV | 2x31.5 MVA @ 10 kV | 63 | --> | 47.25 | 11.8866 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 4.1085 | 42.1674 | 15.192 |  | --> |  | Transmission Source | SALTHILL |  | 53.2718 | -9.073
SALTHILL (161000) 110 kV STATION | Salthill [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 44.8867 | N/A, consult Eirgrid |  | --> | 60.1 | 0 | 47.8171 | 17.3804 | 0 |  | --> |  | Transmission Source | SALTHILL |  | 53.2718 | -9.073
SANDYFORD (288000) 38 kV STATION | Sandyford [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.15247 | 4.3 |  | --> | 12.4 | 4.75 | 2.0477 | 12.8644 | 4.8456 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2665 | -6.2258
SANTRY (315000) 38 kV STATION | Santry [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.31329 | 23.7 |  | --> | 12.4 | 4.75 | 0.72745 | 14.0532 | 4.8656 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3928 | -6.2492
SCARIFF (229000) 38 kV STATION | Scariff [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained,otherwise capacity available =0.5 MVA | --> | 4.8 | 0 | 0.72171 | 4.7066 | 0 |  | --> |  | Ennis [T141,T142] | ENNIS |  | 52.9016 | -8.5292
SCARTEEN (211000) 38 kV STATION | Scarteen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 18.5 |  | --> | 6.2 | 2.375 | 4.6098 | 3.3511 | 2.2233 |  | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1463 | -8.6725
SCREEB (366000) 110 kV STATION | Screeb [T41] | 110 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.4737 | 6.9 |  | --> | 4.8 | 0 | 0.39903 | 5.0959 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.3894 | -9.5708
SCREEB (366000) 110 kV STATION | Screeb [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.9205 | N/A, consult Eirgrid |  | --> | 30.1 | 0 | 10.2095 | 24.5218 | 0 |  | --> |  | Transmission Source | SCREEB |  | 53.3894 | -9.5708
SEMPERIT (360000) 38 kV STATION | Semperit [T41,T42,T43] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 22.5 | 0 | 0 |  | --> | 12.3 | 4.7481 | 0.98198 | 15.757 | 5.2649 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.3359 | -6.3539
SHANKILL (714000) 110 kV STATION | Shankill [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 14.7454 | N/A, consult Eirgrid |  | --> | 78.2 | 0 | 72.6734 | 20.4313 | 0 |  | --> |  | Transmission Source | SHANKILL |  | 54.0044 | -7.3094
SHANNON (325000) 38 kV STATION | Shannon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.042007 | 3.8 |  | --> | 12.4 | 4.75 | 0.21429 | 14.9304 | 4.9237 |  | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.698 | -8.8964
SHERCOCK (539000) 38 kV STATION | Shercock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.5204 | 27.8 |  | --> | 6.2 | 2.375 | 0.32349 | 7.8093 | 2.5088 |  | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9961 | -6.9203
SHERIFF STREET (588000) 38 kV STATION | Sheriff Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.978 | 33.2 |  | --> | 12.4 | 4.75 | 0.032021 | 13.5325 | 4.778 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3488 | -6.2392
SHILLELAGH (708000) 38 kV STATION | Shillelagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 20.5 |  | --> | 6.5 | 2.375 | 5.5799 | 2.7537 | 1.6319 |  | --> |  | Carlow [T141,T142] | CARLOW |  | 52.7481 | -6.5265
SINGLAND (521000) 110 kV STATION | Singland [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.797 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 1.7234 | 26.4545 | 9.5754 |  | --> |  | Transmission Source | SINGLAND |  | 52.6677 | -8.5792
SKIBBEREEN (164000) 38 kV STATION | Skibbereen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 44.2 |  | --> | 6.4 | 2.375 | 5.5949 | 2.8517 | 1.9463 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.567 | -9.255
SLANE (208000) 38 kV STATION | Slane [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained,otherwise capacity available =1.5 MVA | --> | 9.8 | 0 | 7.8665 | 3.1233 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7558 | -6.5442
SLANE (208000) 38 kV STATION | Slane [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained,otherwise capacity available =4.5 MVA | --> | 4.8 | 0 | 3.8922 | 0.8578 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7558 | -6.5442
SLIGO (715000) 110 kV STATION | Sligo [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 27.9238 | N/A, consult Eirgrid |  | --> | 78.2 | 0 | 26.8784 | 68.155 | 0 |  | --> |  | Transmission Source | SLIGO |  | 54.2379 | -8.4592
SMEARLA (018000) 38 kV STATION | Smearla [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.4597 | 14.4 |  | --> | 12.5 | 4.75 | 5.649 | 8.9241 | 4.8043 |  | --> |  | Trien [T141,T142] | TRIEN |  | 52.4372 | -9.446
SOMERSET (716000) 110 kV STATION | Somerset [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 2.2002 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 7.5051 | 29.049 | 0 |  | --> |  | Transmission Source | SOMERSET |  | 53.2595 | -8.2412
SORNE HILL (743000) 110 kV STATION | Sorne Hill [T122] | 110 kV | _ | MV | 1x31.5 MVA @ 20 kV | 31.5 | --> | 28.35 | 27.6894 | N/A, consult Eirgrid |  | --> | 30.2 | 0 | 25.25 | 4.975 | 0 |  | --> |  | Transmission Source | SORNE HILL |  | 55.1231 | -7.361
SOUTH KING STREET (241000) 38 kV STATION | South King Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.7074 | 33.2 |  | --> | 12.4 | 4.75 | 0.017242 | 15.1232 | 4.8603 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3423 | -6.269
SPA ROAD (205000) 38 kV STATION | Spa Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9469 | 11.8 |  | --> | 6.2 | 2.375 | 1.402 | 0 | 0 | Constrained,otherwise capacity available =6.1 MW Firm & 2.4 MW Non-firm | --> |  | Doon [T141,T142] | DOON |  | 52.3529 | -7.6775
SPIDDAL (443000) 38 kV STATION | Spiddal [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 6.9 |  | --> | 5 | 0 | 4.2102 | 1.9905 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.2582 | -9.3209
SPRINGS (585000) 38 kV STATION | Springs [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =8.1 MVA | --> | 12.6 | 4.75 | 9.9955 | 0 | 0 | Constrained,otherwise capacity available =4.9 MW Firm & 4.8 MW Non-firm | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.0866 | -7.6482
SRAH (484000) 38 kV STATION | Srah [T43] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 1.4436 | 64.1 |  | --> | 9.5 | 0 | 0.45322 | 10.2495 | 0 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2828 | -7.5199
SRAH (484000) 38 kV STATION | Srah [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 64.1 |  | --> | 6.2 | 2.375 | 5.4107 | 2.039 | 1.1769 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2828 | -7.5199
STEPHENSTOWN (730000) 110 kV STATION | Stephenstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 | Constrained,otherwise capacity available =13.4 MVA | --> | 24.7 | 9.5 | 11.3827 | 16.5199 | 9.5624 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.6057 | -6.1974
STICKILLEN (063000) 38 kV STATION | Stickillen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained,otherwise capacity available =1 MVA | --> | 6.2 | 2.375 | 1.3876 | 5.9307 | 2.4095 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.8627 | -6.533
STRANORLAR (150000) 38 kV STATION | Stranorlar [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 4.3662 | 13.8 |  | --> | 12.6 | 4.75 | 9.8319 | 0 | 0 | Constrained,otherwise capacity available =4.9 MW Firm & 3.3 MW Non-firm | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.808 | -7.7617
STRATFORD (913000) 110 kV STATION | Stratford [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0.14764 | N/A, consult Eirgrid |  | --> | 30.2 | 0 | 18.7343 | 18.0604 | 0 |  | --> |  | Transmission Source | STRATFORD |  | 52.9896 | -6.6669
SUTTON (333000) 38 kV STATION | Sutton [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =1 MVA | --> | 12.4 | 4.75 | 1.7094 | 12.7847 | 4.8095 |  | --> |  | Grange (dr) [T141,T142] | GRANGE (DR) |  | 53.3875 | -6.1215
SWINFORD (043000) 38 kV STATION | Swinford [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.42911 | 25.1 |  | --> | 6.2 | 2.375 | 0.66834 | 0 | 0 | Constrained,otherwise capacity available =6.9 MW Firm & 2.4 MW Non-firm | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.9394 | -8.9569
SWORDS (066000) 38 kV STATION | Swords [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =1.3 MVA | --> | 12.4 | 4.75 | 1.4015 | 14.8504 | 5.1413 |  | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.4613 | -6.2256
TALBOTS INCH (508000) 38 kV STATION | Talbots Inch [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 7.3 |  | --> | 6.2 | 2.375 | 6.2499 | 1.8167 | 1.0645 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6758 | -7.2636
TANEY (953000) 110 kV STATION | Taney [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 19.8462 | 199 |  | --> | 24.7 | 9.5 | 0.30954 | 26.2846 | 9.5215 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2846 | -6.2385
TAWNAGHMORE (952000) 110 kV STATION | Tawnaghmore [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 26.837 | N/A, consult Eirgrid |  | --> | 30.1 | 0 | 30 | 0.117 | 0 |  | --> |  | Transmission Source | TAWNAGHMORE |  | 54.1991 | -9.229
TELAYDON (415000) 38 kV STATION | Telaydon [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.9259 | 5.7 |  | --> | 12.4 | 4.75 | 1.335 | 0 | 0 | Constrained,otherwise capacity available =13.4 MW Firm & 4.8 MW Non-firm | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2688 | -6.9899
TEMPLEMORE (057000) 38 kV STATION | Templemore [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =7.1 MVA | --> | 12.4 | 4.75 | 0.94996 | 0 | 0 | Constrained,otherwise capacity available =12.8 MW Firm & 4.8 MW Non-firm | --> |  | Ikerrin [T141] | IKERRIN |  | 52.7898 | -7.8383
TEMPLEOGUE (146000) 38 kV STATION | Templeogue [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.4683 | 26.9 |  | --> | 12.4 | 4.75 | 2.0879 | 12.1117 | 4.7987 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3005 | -6.308
TERMONFECKIN ROAD (263000) 38 kV STATION | Termonfeckin Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 4.4357 | 3.6511 | 2.4999 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7295 | -6.3184
THORNSBERRY (717000) 110 kV STATION | Thornsberry [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 64.0948 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 32.9223 | 48.8174 | 0 |  | --> |  | Transmission Source | THORNSBERRY |  | 53.2917 | -7.4657
THURLES (718000) 110 kV STATION | Thurles [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 13.6887 | N/A, consult Eirgrid |  | --> | 39.4 | 0 | 45.1001 | 3.0072 | 0 |  | --> |  | Transmission Source | THURLES |  | 52.6972 | -7.7687
TIMOLEAGUE (163000) 38 kV STATION | Timoleague [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.3 |  | --> | 4.8 | 0 | 5.8494 | 0 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.6825 | -8.7671
TINAHASK (362000) 38 kV STATION | Tinahask [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 55 |  | --> | 6.2 | 2.375 | 1.5957 | 0 | 0 | Constrained,otherwise capacity available =6.2 MW Firm & 2.5 MW Non-firm | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.7921 | -6.1724
TIPPERARY (806000) 110 kV STATION | Tipperary [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 2.7632 | N/A, consult Eirgrid |  | --> | 30.1 | 0 | 18.1142 | 19.1707 | 0 |  | --> |  | Transmission Source | TIPPERARY |  | 52.4802 | -8.0759
TOGHER (336000) 38 kV STATION | Togher [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =3.2 MVA | --> | 12.4 | 4.75 | 1.4933 | 13.4825 | 4.8593 |  | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.8827 | -8.5056
TONROE (904000) 110 kV STATION | Tonroe [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.9577 | N/A, consult Eirgrid |  | --> | 30.2 | 0 | 22.1527 | 13.6886 | 0 |  | --> |  | Transmission Source | TONROE |  | 53.9135 | -8.5866
TOOMEVARA (385000) 38 kV STATION | Toomevara [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.6 |  | --> | 5 | 0 | 5.8701 | 0.072493 | 0 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8734 | -8.0397
TRABEG (701000) 110 kV STATION | Trabeg [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 6.0171 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 1.8227 | 27.0609 | 9.6126 |  | --> |  | Transmission Source | TRABEG |  | 51.8856 | -8.4621
TRABEG (701000) 110 kV STATION | Trabeg [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 10.5948 | 41.0923 | 0 |  | --> |  | Transmission Source | TRABEG |  | 51.8856 | -8.4621
TRALEE (719000) 110 kV STATION | Tralee [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 30.3872 | N/A, consult Eirgrid |  | --> | 78.2 | 0 | 75.1502 | 14.7169 | 0 |  | --> |  | Transmission Source | TRALEE |  | 52.2874 | -9.6776
TRAMORE (032000) 38 kV STATION | Tramore [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =0.8 MVA | --> | 12.4 | 4.75 | 9.6925 | 5.0397 | 1.4412 | Constrained,otherwise capacity available =5 MW Firm & 3.7 MW Non-firm | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.1603 | -7.1467
TRIEN (720000) 110 kV STATION | Trien [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.82 | N/A, consult Eirgrid |  | --> | 60.2 | 0 | 46.3 | 13.85 | 0 |  | --> |  | Transmission Source | TRIEN |  | 52.4203 | -9.4318
TRIEN (720000) 110 kV STATION | Trien [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 14.4185 | N/A, consult Eirgrid |  | --> | 39.4 | 0 | 37.5918 | 14.8632 | 0 |  | --> |  | Transmission Source | TRIEN |  | 52.4203 | -9.4318
TRILLICK (721000) 110 kV STATION | Trillick [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 4.9238 | N/A, consult Eirgrid |  | --> | 30.2 | 0 | 54.9579 | 0 | 0 |  | --> |  | Transmission Source | TRILLICK |  | 55.1182 | -7.4248
TRILLICK (721000) 110 kV STATION | Trillick [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 27.9524 | N/A, consult Eirgrid |  | --> | 30.2 | 0 | 30.89 | 0 | 0 |  | --> |  | Transmission Source | TRILLICK |  | 55.1182 | -7.4248
TRIM (196000) 38 kV STATION | Trim [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.33039 | 15.2 |  | --> | 4.8 | 0 | 0.76112 | 4.5389 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.5544 | -6.7864
TRIM (196000) 38 kV STATION | Trim [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 15.2 |  | --> | 6.2 | 2.375 | 6.1801 | 1.5574 | 0.84751 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.5544 | -6.7864
TRIMMS LANE (427000) 38 kV STATION | Trimms Lane [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.4537 | 44.9 |  | --> | 12.4 | 4.75 | 0.58705 | 14.0616 | 3.3188 | Constrained,otherwise capacity available =14.1 MW Firm & 4.8 MW Non-firm | --> |  | Salthill [T141] | SALTHILL |  | 53.2643 | -9.0739
TRINITY (494000) 110 kV STATION | Trinity [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.9486 | 54.9 |  | --> | 24.7 | 9.5 | 0.070611 | 29.7677 | 9.696 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3456 | -6.2435
TUAM NORTH (253000) 38 kV STATION | Tuam North [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 12.8 |  | --> | 6.2 | 2.375 | 1.3662 | 6.5593 | 2.4729 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.5329 | -8.8772
TUAM SOUTH (040000) 38 kV STATION | Tuam South [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 12.8 |  | --> | 4.8 | 0 | 0.18145 | 6.0071 | 0 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.516 | -8.8665
TUBBERCURRY (355000) 38 kV STATION | Tubbercurry [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0.060409 | 7 |  | --> | 1.2 | 1.1875 | 0.56653 | 1.2098 | 1.407 |  | --> |  | Tonroe [T142] | TONROE |  | 54.0575 | -8.7418
TULLA (182000) 38 kV STATION | Tulla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 0 |  | --> | 3.1 | 1.1875 | 0.72253 | 3.0628 | 1.1999 |  | --> |  | Ennis [T141,T142] | ENNIS |  | 52.8543 | -8.7626
TULLABRACK (722000) 110 kV STATION | Tullabrack [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 14.4476 | N/A, consult Eirgrid |  | --> | 30.2 | 0 | 33.2612 | 1.7563 | 0 |  | --> |  | Transmission Source | TULLABRACK |  | 52.6666 | -9.462
TULLOW (293000) 38 kV STATION | Tullow [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0.43064 | 20.5 |  | --> | 12.6 | 4.75 | 11.5328 | 3.6904 | 1.8925 |  | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8003 | -6.7211
TULLYNAMALRA (466000) 38 kV STATION | Tullynamalra [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.5847 | 27.8 |  | --> | 6.5 | 2.375 | 2.8465 | 5.0345 | 2.4272 |  | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 54.0666 | -6.8262
TURLOUGH ROAD (042000) 38 kV STATION | Turlough Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.9336 | 25.1 |  | --> | 6.2 | 2.375 | 0.57966 | 0 | 0 | Constrained,otherwise capacity available =6.5 MW Firm & 2.4 MW Non-firm | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8678 | -9.2871
TURLOUGH ROAD (042000) 38 kV STATION | Turlough Road [T43] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.5134 | 25.1 |  | --> | 4.8 | 0 | 0.12891 | 0 | 0 | Constrained,otherwise capacity available =5.3 MW Firm & 0 MW Non-firm | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8678 | -9.2871
TYCOR (286000) 38 kV STATION | Tycor [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.95428 | 27 |  | --> | 6.2 | 2.375 | 0.46636 | 6.9582 | 2.4173 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2539 | -7.1345
TYMON (424000) 38 kV STATION | Tymon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =1.4 MVA | --> | 12.4 | 4.75 | 1.2669 | 13.5842 | 4.8375 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2972 | -6.3369
UNIDARE (245000) 38 kV STATION | Unidare [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 0.40888 | 14.0492 | 4.8098 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3995 | -6.3031
URLINGFORD (910000) 38 kV STATION | Urlingford [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 13.7 |  | --> | 9.5 | 0 | 0 | 3.0072 | 0 | Constrained,otherwise capacity available =9.5 MW Firm & 0 MW Non-firm | --> |  | Thurles [T141,T142] | THURLES |  | 52.705 | -7.5965
VIRGINIA (452000) 38 kV STATION | Virginia [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 27.8 |  | --> | 6.2 | 2.375 | 0.42038 | 7.8546 | 2.5404 |  | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8085 | -7.0378
WATERFORD (808000) 110 kV STATION | Waterford [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 27.0276 | N/A, consult Eirgrid |  | --> | 78.1 | 0 | 31.8636 | 69.5192 | 0 |  | --> |  | Transmission Source | WATERFORD |  | 52.2685 | -7.1278
WATERFORD (808000) 110 kV STATION | Waterford [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.8208 | 27 |  | --> | 6.2 | 2.375 | 0.12726 | 6.828 | 2.3932 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2685 | -7.1278
WATERFORD IND EST (348000) 38 kV STATION | Waterford Ind Est [T41,T42,T44] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 22.5 | 0 | 0 | Constrained,otherwise capacity available =9.1 MVA | --> | 12.3 | 4.7481 | 0.34895 | 6.4809 | 0 | Constrained,otherwise capacity available =16 MW Firm & 5.1 MW Non-firm | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.2426 | -7.1558
WATLING STREET (361000) 38 kV STATION | Watling Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.5587 | 31.2 |  | --> | 12.4 | 4.75 | 8.1867 | 5.9467 | 4.2694 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3469 | -6.2808
WESTPORT (116000) 38 kV STATION | Westport [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 8.1047 | 25.1 |  | --> | 12.4 | 4.75 | 1.3252 | 0 | 0 | Constrained,otherwise capacity available =12.8 MW Firm & 4.8 MW Non-firm | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.7963 | -9.4872
WEXFORD (742000) 110 kV STATION | Wexford [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 16.1248 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 2.6602 | 24.8272 | 9.5462 |  | --> |  | Transmission Source | WEXFORD |  | 52.3425 | -6.5476
WEXFORD (742000) 110 kV STATION | Wexford [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 35.0177 | N/A, consult Eirgrid |  | --> | 78 | 0 | 55.5875 | 35.3609 | 0 |  | --> |  | Transmission Source | WEXFORD |  | 52.3425 | -6.5476
WHITECHURCH (167000) 38 kV STATION | Whitechurch [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =0.1 MVA | --> | 12.4 | 4.75 | 6.5666 | 8.4669 | 4.8643 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.9901 | -8.4998
WHITEHALL (183000) 38 kV STATION | Whitehall [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained,otherwise capacity available =1.7 MVA | --> | 9.5 | 0 | 0.86457 | 9.9556 | 0 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3782 | -6.2569
WHITESTOWN (423000) 38 kV STATION | Whitestown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained,otherwise capacity available =6.9 MVA | --> | 12.4 | 4.75 | 0.52712 | 13.1007 | 4.77 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2802 | -6.3801
WINDSOR (608000) 38 kV STATION | Windsor [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 25.1 |  | --> | 6.5 | 2.375 | 5.2346 | 0 | 0 | Constrained,otherwise capacity available =3.4 MW Firm & 2.1 MW Non-firm | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8745 | -9.2555
WOLFE TONE STREET (769000) 110 kV STATION | Wolfe Tone Street [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 3.9893 | 88 |  | --> | 24.7 | 9.5 | 0.14368 | 30.4398 | 9.7525 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3519 | -6.2732
WOODFORD (276000) 38 kV STATION | Woodford [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.89424 | 0.9 | Constrained,otherwise capacity available =3 MVA | --> | 12.4 | 4.75 | 1.3465 | 13.6129 | 4.7167 | Constrained,otherwise capacity available =13.6 MW Firm & 4.8 MW Non-firm | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0537 | -9.4547

## Disclaimer
Disclaimer
This capacity heatmap provides an indication of the available transformer capacity at substations. The map indicates transformer capacity only. It does not guarantee the same capacity is available in the upstream networks. The heatmap is a snapshot, representing a moment in time, of a continually changing network system. It cannot be relied upon in isolation to assess the viability of a connection to a premises. Whilst we use reasonable endeavours to ensure that the capacity map and related information is accurate, we do not warrant, and do not accept any responsibility or liability for, the accuracy or completeness of the content or for any consequence or loss which may arise from reliance on the capacity heatmap or related information. The data provided must be considered in conjunction with explanations in ‘Important details about the Heatmap’ section. The available capacity figures will be periodically updated, and you should check the webpage routinely for the latest version. The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.
The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.

## Notes & FAQs
What is the Available Capacity Heatmap?
At ESB Networks we are committed to improving the experience of our customers. As part of this commitment, we have developed our interactive Capacity Heatmap. It contains capacity information on all our 3-phase LV, MV and HV DSO substations. It provides an interface that enables the easy identification of potential transformer capacity in the vicinity of your site. An excel file is available to download from the download section on this page.
We envisage that the map will be used to inform initial discussion between ourselves and our customers. Although we have taken steps to ensure the accuracy of the map, it cannot replicate the level of accuracy provided by the detailed assessment carried out as part of the formal application process. Please read the accompanying notes and important details section to understand what the map does and does not provide.
If the Available Capacity Heatmap indicates that there is insufficient capacity to accommodate your development, please contact us to discuss the next steps. We will always work with customers to find solutions.
Generation customer queries should be directed to DSOgenerators@esb.ie.
Demand customer queries should be directed to innovationfeedback@esbnetworks.ie.
Map Preparation Date: 23 May 2025
What can I learn from the map?
The Capacity Heatmap provides an indication of available transformer capacity, at substation level and at all voltage levels, for new demand and generation customers. It is a user-friendly and interactive map that shows how much demand or generation could be added into a substation without reinforcement. It empowers potential customers and helps them have a better understanding as to where connection is possible.
In the map HV substations are classified into three categories corresponding to the connection voltage i.e., 110kV, 38kV or Medium Voltage (MV).
The map also gives the location and available demand capacity for all 3 phase Medium Voltage to Low Voltage (MV/LV) substations.The LV data capacity is in the range of customers looking to connect demand less than 500kVA. This scale would be of most interest to small businesses, farming, and small community projects. If the indicated capacity meets your needs, then you can be reasonably assured no new substation development is required. However, site specific detail such as proximity and physical access could still be an overarching limiting factor.
Available capacity for LV generation is not specified because of additional considerations that are mainly site specific, see point No 5 below.
The pins on the map are colour coded by ranges of available capacity which can be separately filtered. Filtering can also be independently applied by voltage level.
How do I know which substation to review for my site?
We recommend using the Location Finder tool by clicking on the icon to the right of the map. Look for this symbol
Here you can type your place name, or Eircode and it will show the stations closest to the location. Please ensure you have selected the relevant connection voltages and available ranges in the filters section on the left or it may not return results.
For LV substations, use the map to locate your own site and then find the nearest LV substation to it. Typically, a substation must be within 300m or less to be suitable for connecting at LV otherwise a new substation must be provided nearer to you. The pop-up box also shows the parent HV substation that supplies the LV substation. Also check this for available capacity.
For MV connection (greater than or equal to 500kVA) locate the nearest LV station as in the previous paragraph and the parent capacity will also be shown.
Does the Capacity Available value mean I can connect the amount shown?
Not necessarily. There are many site-specific issues and detailed technical checks that must be completed to give that assurance and they can only be completed as part of an application. Below are some of the factors that influence the answer:
Am I the first to apply? All connection offers are provided on a first come first served basis so other customers may have applied ahead and used a proportion of the available capacity.
Proximity to the substation: typically for LV, you must be a maximum of 300m from the substation and much closer for the higher level of LV capacity. For 38kV and MV circuits, capacity is not assured, and new lines may need to be constructed or existing one upgraded.
HV substations are sometimes a parent supply to other downstream substations. In cases where the parent substation has limited capacity then all child substations will be curtailed by that limit. Furthermore, if just one child substation absorbs all the available capacity then that will result in no spare capacity for the other child stations. This form of interaction requires continual re-assessment to ensure no system overload occur.
A similar interaction can occur on circuits where apparently available capacity cannot be contracted because of customer increases on other circuits which share a common source with a capacity limit.
Generation, at all voltages, is particularly onerous due to the limited latitude to accommodate the associated voltage rise. This has an acute effect on the necessary proximity to a substation.
For ECP generation connections, the capacity available may differ depending on customers accepting or withdrawing their connection study offers during each batch of studies.
Capacity available is also influenced by disturbing load such as flicker and harmonic emissions.
The stated available capacity may exceed the maximum rating for an individual network component for example standard circuit connection capacity. In such cases, aconnection will be constrained by the network component and therefore will not be able to avail of the full value indicated.
How has the data been produced?
The data has been produced by an analysis of the available transformer capacity, existing loads, and contractual commitments to new customers. Detailed assessment aspects, necessary for connection offers, such as upstream circuit capacity and service contingency requirement are not included.
What are the available capacity figures based on?
Station capacity, as of April 2025.
Base load information comes from Special Load Readings, 2024/2025 which include 2024 Summer Valley load used in the Generation capacity preparation.
Demand calculation incorporates demand contracts and offers up to 02 May 2025
Generation calculations incorporates generation contracts and offers up to 15 May 2025 November 2024.
How often is the Network Capacity Map updated?
As part of ESB Networks strategy, the objective is to update the map quarterly.
Are the substation locations accurate?
HV substation locations are only indicative. The exact locations of MV/LV substations are provided.
How long does a connection take?
In general, where HV substation capacity is adequate, MV connections up to a maximum of 10MVA will entail construction of overhead line or new underground cable network, associated civil works and minor station works only and typically do not require planning permission. These would not be expected to take longer than 6-9 months. However, any instances requiring significant station work such as the installation of a new transformer or MV switchgear will require increased time, and possibly planning permission or necessary permits and would typically be expected to take approximately 2-3 years.
LV connections alone are usually completed within 6 months of application.
Generation connection information: Enduring Connection Policy (ECP) (esbnetworks.ie)
What other important points should be kept in mind about the data in the map?
The map does not replace a full formal application in determining network capacity.
The map does not provide capacity figures for the final connection from HV substation to customer premises. Such connections will need to tap into the existing MV (10kV or 20kV) network. Capacity availability is subject to many variables and an assessment is necessary.
In some cases, the available capacity shown in the Demand Map may already be contracted to individual customers but is not currently being fully utilised.
The information provided in the Generation and Demand Maps does not guarantee the same capacity is available in the upstream DSO networks.
Any increased load on the Distribution System will impact on the upstream Transmission System and reinforcements may be required on the Transmission System in order to cater for these loads. This will be separately assessed by the TSO.
An individual connection cannot be greater than the capacity of an individual transformer. In the case of 38kV and MV, the available capacity shown is the total of all transformers in the substation at the respective voltage. Therefore, full capacity utilisation may, sometimes, only be possible with more than one connection. (Note, a single premises cannot have more than one connection).