0104098 | MV/LV Substation CO***4098 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.5371 | -6.9123
068609X | MV/LV Substation CA***609X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 20.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex HEUSTON SQUARE | Heuston Square [T101,T102] | INCHICORE 220KV |  | 53.3415 | -6.3043
3654260 | MV/LV Substation MA***4260 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2806 | -6.4162
350016 | MV/LV Substation FI***016 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.308 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4931 | -8.2383
204572 | MV/LV Substation TE***572 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 2.02 |  | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =33 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.1186 | -7.4453
037330Y | MV/LV Substation PM***330Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8173 | -8.9587
0954098 | MV/LV Substation LI***4098 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.1 |  | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C26 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.6956 | -9.6223
053040Z | MV/LV Substation DO***040Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.363 | 2.39 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C12 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2788 | -7.4992
014525Z | MV/LV Substation GR***525Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.63 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.083 | -6.7137
037322 | MV/LV Substation LO***322 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C16 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.857 | -9.0138
009478X | MV/LV Substation KI***478X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C15 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.305 | -7.1712
030004X | MV/LV Substation RE***004X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =214 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E20 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9256 | -7.8723
1544217 | MV/LV Substation WI***4217 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4006 | -6.4457
005819 | MV/LV Substation FR***819 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E22 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6369 | -6.3676
244517X | MV/LV Substation CO***517X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E18 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1698 | -9.5967
002861 | MV/LV Substation DE***861 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.34 | 4.51 |  | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1879 | -6.1061
006796 | MV/LV Substation ED***796 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.29 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex MONFIN | Monfin [T41,T42] | WEXFORD |  | 52.4536 | -6.5542
068833 | MV/LV Substation HA***833 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.38 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3411 | -6.2408
0274164 | MV/LV Substation AN***4164 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.382 | 7.79 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C13 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7276 | -9.104
062071Z | MV/LV Substation 01***071Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 2.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C18 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.033 | -6.3902
324574X | MV/LV Substation KE***574X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.5638 | -8.2466
081212Z | MV/LV Substation B ***212Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =515 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3477 | -6.3886
042942 | MV/LV Substation BA***942 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =4 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C21 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.7949 | -9.3156
276074 | MV/LV Substation GL***074 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 0.76 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C12 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0156 | -9.3619
256925 | MV/LV Substation BA***925 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.082 | 1.28 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C17 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7662 | -8.4844
365064Y | MV/LV Substation CO***064Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3085 | -6.5123
009663X | MV/LV Substation WA***663X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 0.53 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C19 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2541 | -7.105
018078 | MV/LV Substation TA***078 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5869 | -9.365
109570 | MV/LV Substation WE***570 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.381 | 0.38 | Constrained, otherwise capacity available =598 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.71 | -8.8932
0504354 | MV/LV Substation ES***4354 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C23 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4319 | -7.9408
237186X | MV/LV Substation MI***186X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8442 | -6.2601
052747Z | MV/LV Substation BU***747Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 10.9 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6087 | -7.4359
293867 | MV/LV Substation RA***867 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9193 | -6.5465
089102X | MV/LV Substation PO***102X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | E18 ex MOY | Moy [T421,T422] | MOY |  | 54.1162 | -9.1576
154432Z | MV/LV Substation PH***432Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =586 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3996 | -6.4361
036037 | MV/LV Substation EM***037 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.293 | 2.76 |  | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =347 kW | --> | C16 ex KILROSS ROAD | Kilross Road [T42] | TIPPERARY |  | 52.4724 | -8.1688
209456X | MV/LV Substation PR***456X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0628 | -7.7846
055992 | MV/LV Substation SH***992 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E22 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9868 | -7.9244
127016Y | MV/LV Substation TH***016Y |  | 10 kV | _ | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.142 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =134 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6592 | -7.8301
154343Z | MV/LV Substation AL***343Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0.032 | 0.338 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3935 | -6.429
070675 | MV/LV Substation KI***675 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.009 | 2.63 |  | --> | 0.048 | 0 | 0.01 | 0.034 | 0 |  | --> | C12 ex CLOONBANNIN | Cloonbannin [T42] | GLENLARA |  | 52.1763 | -9.1581
245001 | MV/LV Substation BU***001 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C22 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3977 | -6.2923
054051Z | MV/LV Substation TH***051Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0505 | -7.3214
377360 | MV/LV Substation DE***360 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7791 | -10.0017
029396Y | MV/LV Substation DU***396Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =23 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9137 | -8.1335
093121Z | MV/LV Substation MA***121Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0.005 | 0.363 | 0 |  | --> | C20 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3977 | -6.2759
281440X | MV/LV Substation HA***440X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C22 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8589 | -8.4956
002159 | MV/LV Substation HE***159 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.276 | 2.36 |  | --> | 0.38 | 0 | 0.054 | 0.323 | 0 |  | --> | C16 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1923 | -6.1269
0394247 | MV/LV Substation LI***4247 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2704 | -9.0997
001197 | MV/LV Substation GR***197 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 1.55 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C21 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2797 | -6.1938
196826 | MV/LV Substation BR***826 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.34 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5124 | -6.8766
0704289 | MV/LV Substation BA***4289 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.76 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E17 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0618 | -9.0791
377570X | MV/LV Substation GA***570X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9449 | -10.2325
109542 | MV/LV Substation MI***542 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 0.38 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C22 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7012 | -8.9306
111889X | MV/LV Substation AR***889X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.051 | 0.94 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E11 ex CASTLETOWNBERE | Castletownbere [T421] | BALLYLICKY |  | 51.7346 | -9.8972
0824520 | MV/LV Substation BL***4520 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.01 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6609 | -6.698
081364X | MV/LV Substation LA***364X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 7.91 |  | --> | 0.38 | 0 | 0.036 | 0.338 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3791 | -6.3803
182583 | MV/LV Substation SC***583 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =129 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | C11 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.905 | -8.5366
0494608 | MV/LV Substation BA***4608 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7762 | -7.6474
039364X | MV/LV Substation BA***364X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C28 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.3135 | -9.0223
013894Y | MV/LV Substation SU***894Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C13 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9908 | -6.9864
0664108 | MV/LV Substation KI***4108 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4645 | -6.3469
109044 | MV/LV Substation PU***044 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.287 | 0.38 |  | --> | 0.38 | 0 | 0.028 | 0.344 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7043 | -8.8823
110208X | MV/LV Substation PA***208X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 0.76 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8183 | -9.8722
0814356 | MV/LV Substation KI***4356 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.393 | 7.91 |  | --> | 0.38 | 0 | 0.014 | 0.369 | 0 |  | --> | C26 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3738 | -6.3625
288651 | MV/LV Substation GL***651 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.005 | 0.042 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2239 | -6.2203
003208 | MV/LV Substation TH***208 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 11.58 |  | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9831 | -6.0598
069598 | MV/LV Substation HE***598 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =254 kVA | --> | 0.38 | 0 | 0.066 | 0.311 | 0 |  | --> | C13 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2854 | -6.2725
093198 | MV/LV Substation HI***198 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.351 | 2.86 |  | --> | 0.38 | 0 | 0.022 | 0.357 | 0 |  | --> | C18 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3878 | -6.2759
024805X | MV/LV Substation BA***805X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.1831 | -8.6725
082556Y | MV/LV Substation GO***556Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5903 | -6.5169
1564448 | MV/LV Substation MC***4448 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3559 | -7.041
180786X | MV/LV Substation WO***786X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C14 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7329 | -6.8441
020734X | MV/LV Substation RE***734X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =770 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =918 kW | --> | C15 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0685 | -9.5168
029278 | MV/LV Substation AV***278 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0.004 | 0.365 | 0 |  | --> | C13 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9237 | -8.1792
099661X | MV/LV Substation RO***661X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.96 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C15 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9499 | -7.7366
081160Y | MV/LV Substation SA***160Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3588 | -6.5515
366935 | MV/LV Substation B ***935 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.18 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C16 ex SCREEB | Screeb [T41] | SCREEB |  | 53.2476 | -9.7384
164003 | MV/LV Substation NO***003 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.043 | 0 | 0 | Constrained, otherwise capacity available =337 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.553 | -9.2618
081461Z | MV/LV Substation TA***461Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3486 | -6.5997
417418 | MV/LV Substation GR***418 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0855 | -8.1292
012101 | MV/LV Substation OA***101 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =67 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8476 | -6.9155
015607Z | MV/LV Substation AL***607Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =654 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =902 kW | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2133 | -6.6951
065522X | MV/LV Substation BA***522X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0.03 | 0.058 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5877 | -6.1898
0674237 | MV/LV Substation CO***4237 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =391 kVA | --> | 0.38 | 0 | 0.067 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C12 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.662 | -8.6665
2814359 | MV/LV Substation CO***4359 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =594 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C21 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8798 | -8.5928
0444056 | MV/LV Substation MO***4056 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E21 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.0307 | -9.1167
001366 | MV/LV Substation TO***366 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.256 | 13.42 |  | --> | 0.38 | 0 | 0.056 | 0.318 | 0 |  | --> | C19 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.273 | -6.155
067054Y | MV/LV Substation KN***054Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C18 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6726 | -8.6704
158833 | MV/LV Substation CR***833 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 53.0059 | -9.3659
127408 | MV/LV Substation KY***408 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6731 | -7.7678
176911X | MV/LV Substation CO***911X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 18.78 |  | --> | 0.095 | 0 | 0.01 | 0.087 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9202 | -9.1628
1544303 | MV/LV Substation LI***4303 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =484 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =575 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3881 | -6.5818
075408X | MV/LV Substation OL***408X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 17.8 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.5564 | -6.2152
184869 | MV/LV Substation KN***869 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1265 | -6.8749
093109Z | MV/LV Substation AW***109Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =180 kVA | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C20 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3879 | -6.3035
055840X | MV/LV Substation PA***840X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | C20 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.8002 | -7.8327
015950X | MV/LV Substation DE***950X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 12.6 |  | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C22 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2136 | -6.6738
127262Y | MV/LV Substation BR***262Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 5.89 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C18 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5153 | -7.8158
009042 | MV/LV Substation AB***042 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =625 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C30 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2566 | -7.1335
110180 | MV/LV Substation DR***180 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.351 | 0.76 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8896 | -9.5846
281880Z | MV/LV Substation SI***880Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C11 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8933 | -8.5208
069027 | MV/LV Substation CL***027 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.337 | 0.91 |  | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C16 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3223 | -6.3025
461090X | MV/LV Substation WA***090X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 2.33 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1023 | -9.1626
007745Z | MV/LV Substation BU***745Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C14 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3396 | -6.4613
022110 | MV/LV Substation FI***110 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C18 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1335 | -8.6957
001999 | MV/LV Substation MO***999 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 1.16 |  | --> | 0.19 | 0 | 0.005 | 0.182 | 0 |  | --> | C16 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.3057 | -6.2076
016254Z | MV/LV Substation MA***254Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.598 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =532 kW | --> | C28 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3654 | -6.5828
009689X | MV/LV Substation CA***689X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.25 | 0.53 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C20 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2564 | -7.1128
060107Y | MV/LV Substation DR***107Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.945 | -7.0609
0814314 | MV/LV Substation TH***4314 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =413 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3366 | -6.4678
117577X | MV/LV Substation HU***577X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1361 | -8.6439
5034030 | MV/LV Substation PO***4030 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.69 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0528 | -7.4039
031277Y | MV/LV Substation BI***277Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0783 | -7.6449
149298X | MV/LV Substation WA***298X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6674 | -8.1285
127126X | MV/LV Substation BA***126X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7412 | -7.6126
039235 | MV/LV Substation PO***235 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 11.03 |  | --> | 0.38 | 0 | 0.052 | 0.329 | 0 |  | --> | C24 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2638 | -9.102
160002 | MV/LV Substation PE***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | C15 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1166 | -7.3268
0594042 | MV/LV Substation AN***4042 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.066 | 0.07 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1012 | -7.4567
065182Z | MV/LV Substation KN***182Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C22 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.626 | -6.2134
0074584 | MV/LV Substation KE***4584 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 0.14 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3603 | -6.4517
160683Y | MV/LV Substation LE***683Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C23 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1513 | -7.1586
014097 | MV/LV Substation NI***097 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.097 | 0.63 |  | --> | 0.19 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =152 kW | --> | C17 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1276 | -6.7489
082239Y | MV/LV Substation BO***239Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.6971 | -6.6153
110482 | MV/LV Substation SH***482 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.187 | 0.76 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | E11 ex KILGARVAN | Kilgarvan [T421] | KNOCKEARAGH |  | 51.8735 | -9.5645
069073 | MV/LV Substation KE***073 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.382 | 0.87 |  | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C13 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3195 | -6.2809
365506X | MV/LV Substation MO***506X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =466 kVA | --> | 0.598 | 0 | 0.065 | 0.5 | 0 |  | --> | C22 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3153 | -6.3635
008568 | MV/LV Substation BA***568 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.2 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2784 | -6.8392
426069 | MV/LV Substation EI***069 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1551 | -10.2931
151342 | MV/LV Substation TU***342 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3123 | -8.4059
081568X | MV/LV Substation VI***568X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.38 | 0 | 0 | 0.341 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3562 | -6.4495
156509X | MV/LV Substation GL***509X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.012 | 2.47 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3177 | -6.8963
067752Y | MV/LV Substation PA***752Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.319 | 13.8 |  | --> | 0.38 | 0 | 0 | 0.369 | 0 |  | --> | C13 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6643 | -8.6007
066489Z | MV/LV Substation BO***489Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5182 | -6.531
001304 | MV/LV Substation RU***304 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.42 |  | --> | 0.598 | 0 | 0.031 | 0.5 | 0 |  | --> | C19 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2781 | -6.1551
041359 | MV/LV Substation BA***359 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.793 | -8.9114
3634044 | MV/LV Substation TR***4044 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5473 | -9.4727
001051 | MV/LV Substation CA***051 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =63 kVA | --> | 0.095 | 0 | 0 | 0.09 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2597 | -6.1623
001169X | MV/LV Substation AR***169X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.356 | 1.16 |  | --> | 0.38 | 0 | 0.01 | 0.366 | 0 |  | --> | C17 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2815 | -6.1522
052640Y | MV/LV Substation DE***640Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.6075 | -7.0838
165793X | MV/LV Substation RO***793X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.6719 | -8.9887
013710 | MV/LV Substation LO***710 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.12 |  | --> | 0.048 | 0 | 0.012 | 0.038 | 0 |  | --> | C12 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9524 | -6.904
062310X | MV/LV Substation AR***310X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 4.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0845 | -6.2825
138099X | MV/LV Substation CO***099X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.169 | 1.52 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C18 ex SHERCOCK | Shercock [T41,T42] | MEATH HILL |  | 53.9975 | -6.8925
069323 | MV/LV Substation GR***323 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.356 | 0.98 |  | --> | 0.598 | 0 | 0.069 | 0.5 | 0 |  | --> | C15 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3294 | -6.2685
007365Z | MV/LV Substation DU***365Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.143 | 0.14 | Constrained, otherwise capacity available =488 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =579 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3428 | -6.4655
0184130 | MV/LV Substation AP***4130 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.236 | 3.75 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | C13 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4484 | -9.4664
067080Z | MV/LV Substation BL***080Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =214 kVA | --> | 0.38 | 0 | 0.123 | 0 | 0 | Constrained, otherwise capacity available =263 kW | --> | C21 ex CASTLETROY | Castletroy [T41,T42] | ARDNACRUSHA |  | 52.6613 | -8.5419
035225X | MV/LV Substation BE***225X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 6.17 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3704 | -7.9329
002104 | MV/LV Substation LO***104 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.259 | 4.51 |  | --> | 0.38 | 0 | 0.087 | 0.296 | 0 |  | --> | C21 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1955 | -6.1046
365021 | MV/LV Substation BE***021 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =543 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C19 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2764 | -6.413
136865Y | MV/LV Substation OA***865Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C17 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6242 | -8.1664
0124247 | MV/LV Substation JO***4247 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.83 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6941 | -6.9768
069439 | MV/LV Substation LI***439 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.368 | 4.47 |  | --> | 0.38 | 0 | 0.005 | 0.372 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3063 | -6.3387
365336X | MV/LV Substation RO***336X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0 | 0.365 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2882 | -6.4003
149735 | MV/LV Substation TU***735 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =69 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6458 | -8.1134
3654196 | MV/LV Substation BB***4196 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2938 | -6.4314
065420Z | MV/LV Substation GO***420Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5275 | -6.0942
207444 | MV/LV Substation GO***444 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 3.38 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.6683 | -7.6122
095068Y | MV/LV Substation LI***068Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.7 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.7259 | -9.4155
001110X | MV/LV Substation SY***110X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2865 | -6.237
093379Z | MV/LV Substation ST***379Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =159 kVA | --> | 0.38 | 0 | 0.004 | 0.343 | 0 |  | --> | C12 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3986 | -6.1451
064969Y | MV/LV Substation TH***969Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =288 kVA | --> | 0.38 | 0 | 0.075 | 0 | 0 | Constrained, otherwise capacity available =309 kW | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7636 | -6.2662
074461 | MV/LV Substation CH***461 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.49 | 8.5 |  | --> | 0.598 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0477 | -8.0414
238037Y | MV/LV Substation HA***037Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E11 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6228 | -9.2077
288258X | MV/LV Substation MI***258X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =748 kVA | --> | 0.95 | 0 | 0.017 | 0.5 | 0 |  | --> | C19 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2628 | -6.1969
029476X | MV/LV Substation ME***476X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.018 | 2.31 |  | --> | 0.048 | 0 | 0.015 | 0.032 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8278 | -8.2256
003551 | MV/LV Substation CA***551 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex KILMARTIN | Kilmartin [T41] | ARKLOW |  | 53.0368 | -6.0656
253064 | MV/LV Substation E ***064 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5183 | -8.8574
029176 | MV/LV Substation OI***176 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.31 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8333 | -8.2315
433104 | MV/LV Substation DE***104 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.322 | 1.04 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8711 | -8.4042
0114091 | MV/LV Substation CL***4091 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6326 | -7.0526
023035Y | MV/LV Substation KI***035Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.1564 | -8.1767
001195 | MV/LV Substation GL***195 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.274 | 1.16 |  | --> | 0.38 | 0 | 0.015 | 0.351 | 0 |  | --> | C14 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.3018 | -6.2113
060483X | MV/LV Substation CO***483X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C18 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1558 | -7.2371
054997X | MV/LV Substation KN***997X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C12 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0273 | -7.3152
050899X | MV/LV Substation WA***899X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =393 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4482 | -8.06
142480X | MV/LV Substation AT***480X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =69 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C11 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.2832 | -8.845
033145Y | MV/LV Substation BE***145Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.059 | 0 | Constrained, otherwise capacity available =94 kW | --> | C23 ex CREGG ROAD | Cregg Road [T41,T42] | BALLYDINE |  | 52.3704 | -7.3354
2074061 | MV/LV Substation TR***4061 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 3.38 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7485 | -7.5734
005419 | MV/LV Substation SE***419 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.341 | 17.8 |  | --> | 0.38 | 0 | 0.01 | 0.364 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6773 | -6.2195
046209X | MV/LV Substation CA***209X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.38 | 5.48 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C14 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2779 | -8.474
039448 | MV/LV Substation LY***448 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C20 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.3233 | -8.9402
1584111 | MV/LV Substation WO***4111 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 0.83 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C18 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8475 | -9.4293
207256 | MV/LV Substation BR***256 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.38 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C17 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.6142 | -7.7016
010241 | MV/LV Substation BA***241 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.4882 | -6.9234
015321 | MV/LV Substation VI***321 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =522 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C14 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2103 | -6.6641
0934308 | MV/LV Substation FI***4308 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.4007 | -6.2988
1174084 | MV/LV Substation HS***4084 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 0.32 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C18 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0947 | -8.5167
029816Y | MV/LV Substation EA***816Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C13 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9306 | -8.1822
127609 | MV/LV Substation CA***609 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 5.89 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.6134 | -7.9791
182010 | MV/LV Substation T ***010 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C22 ex TULLA | Tulla [T41,T42] | ENNIS |  | 52.9683 | -8.7182
068558X | MV/LV Substation AC***558X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3448 | -6.2493
029260 | MV/LV Substation GA***260 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.31 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8052 | -8.1794
071881 | MV/LV Substation CH***881 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1272 | -6.0634
068170X | MV/LV Substation CA***170X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.488 | 2.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3501 | -6.2702
014182 | MV/LV Substation PA***182 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | C17 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1806 | -6.8033
365004 | MV/LV Substation ES***004 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2965 | -6.3581
2374055 | MV/LV Substation MU***4055 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8613 | -6.4014
138721 | MV/LV Substation CO***721 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 2.18 |  | --> | 0.19 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C24 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9123 | -6.974
064021Z | MV/LV Substation GR***021Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =156 kW | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7063 | -6.3129
034082 | MV/LV Substation HI***082 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.14 | 0.57 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C16 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3631 | -7.7145
081275X | MV/LV Substation TH***275X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.096 | 7.91 |  | --> | 0.19 | 0 | 0.032 | 0.152 | 0 |  | --> | C22 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3764 | -6.372
139855X | MV/LV Substation KI***855X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.8858 | -7.0506
1544345 | MV/LV Substation KI***4345 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =576 kVA | --> | 0.598 | 0 | 0.099 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4269 | -6.3841
001323 | MV/LV Substation WY***323 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =239 kVA | --> | 0.38 | 0 | 0.04 | 0.328 | 0 |  | --> | C12 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2505 | -6.1361
2884153 | MV/LV Substation MU***4153 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =629 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2658 | -6.2843
082336Y | MV/LV Substation MO***336Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6227 | -6.5708
029548X | MV/LV Substation CO***548X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =7 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C32 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8578 | -8.1194
136234Y | MV/LV Substation GA***234Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6172 | -8.4592
156096Z | MV/LV Substation LO***096Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.098 | 2.47 |  | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =138 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2907 | -6.8767
0034280 | MV/LV Substation HA***4280 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.58 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =593 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9853 | -6.0726
020066 | MV/LV Substation CO***066 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.598 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =523 kW | --> | C12 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0591 | -9.5064
001005 | MV/LV Substation PE***005 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.304 | 1.23 |  | --> | 0.598 | 0 | 0.032 | 0.5 | 0 |  | --> | C22 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2899 | -6.1292
142009 | MV/LV Substation CH***009 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C16 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.3001 | -8.7506
156414Z | MV/LV Substation LI***414Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2178 | -6.8467
035680 | MV/LV Substation NE***680 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 0.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3082 | -7.8483
127806Y | MV/LV Substation WE***806Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 5.89 |  | --> | 0.095 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =74 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5676 | -7.8889
054436Y | MV/LV Substation AN***436Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =443 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | C26 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0261 | -7.3055
082692Y | MV/LV Substation BA***692Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6284 | -6.6864
070741X | MV/LV Substation IR***741X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0948 | -9.2979
078273 | MV/LV Substation TH***273 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C11 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9573 | -8.8084
366391X | MV/LV Substation NA***391X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.182 | 0.45 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2654 | -9.6019
180103X | MV/LV Substation CA***103X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C17 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.7063 | -7.0106
0144146 | MV/LV Substation SU***4146 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1064 | -6.8595
164321X | MV/LV Substation RO***321X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.551 | -9.3091
026317 | MV/LV Substation RO***317 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 8.66 |  | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | C13 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.733 | -8.7539
0294173 | MV/LV Substation OB***4173 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.876 | -8.0832
029752Y | MV/LV Substation WA***752Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C19 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9191 | -8.1985
069551 | MV/LV Substation SW***551 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.148 | 0.87 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3229 | -6.2641
082289Z | MV/LV Substation RE***289Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.01 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6516 | -6.7097
068603X | MV/LV Substation AN***603X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =539 kVA | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C21 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3589 | -6.2874
021155 | MV/LV Substation KN***155 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =394 kVA | --> | 0.598 | 0 | 0.012 | 0.5 | 0 |  | --> | C24 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9096 | -8.4856
093066Z | MV/LV Substation MA***066Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =374 kVA | --> | 0.38 | 0 | 0.01 | 0.369 | 0 |  | --> | C14 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3791 | -6.2906
0034199 | MV/LV Substation SE***4199 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 11.58 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C20 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9713 | -6.0514
011337X | MV/LV Substation MO***337X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 5.05 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C20 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.7082 | -7.1777
069013 | MV/LV Substation HA***013 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.187 | 9.99 |  | --> | 0.598 | 0 | 0.043 | 0.5 | 0 |  | --> | C16 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3215 | -6.2757
011032 | MV/LV Substation GR***032 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =313 kVA | --> | 0.38 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C16 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6575 | -7.2523
015440X | MV/LV Substation ST***440X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =344 kW | --> | E20 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1724 | -6.5319
243107 | MV/LV Substation FA***107 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | E17 ex INCH | Inch [T421,T422] | OUGHTRAGH |  | 52.3036 | -10.0394
074313 | MV/LV Substation PA***313 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0358 | -7.9491
288262X | MV/LV Substation GA***262X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =218 kVA | --> | 0.38 | 0 | 0.006 | 0.35 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2466 | -6.1818
266968 | MV/LV Substation MC***968 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2776 | -7.2361
204871 | MV/LV Substation SA***871 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1335 | -7.4336
001020 | MV/LV Substation WE***020 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.087 | 1.16 |  | --> | 0.38 | 0 | 0.055 | 0.294 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2701 | -6.1741
001242 | MV/LV Substation HI***242 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.263 | 1.23 |  | --> | 0.38 | 0 | 0.102 | 0.285 | 0 |  | --> | C17 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2734 | -6.1318
062045Z | MV/LV Substation MO***045Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.366 | 4.25 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.037 | -6.3708
025234X | MV/LV Substation RA***234X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4662 | -8.4635
015896Y | MV/LV Substation BA***896Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2571 | -6.7069
020541X | MV/LV Substation CH***541X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =548 kVA | --> | 0.598 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =561 kW | --> | C16 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0602 | -9.5126
176629X | MV/LV Substation DR***629X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 18.78 |  | --> | 0.048 | 0 | 0.025 | 0.028 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.8892 | -9.0361
068871X | MV/LV Substation FL***871X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 28.43 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C06 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3458 | -6.2617
068077 | MV/LV Substation ST***077 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.91 |  | --> | 0.95 | 0 | 0.085 | 0.5 | 0 |  | --> | C29 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3691 | -6.3238
051930 | MV/LV Substation NE***930 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 2.22 |  | --> | 0.095 | 0 | 0.006 | 0.09 | 0 |  | --> | E12 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3744 | -7.4232
365310 | MV/LV Substation TA***310 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =219 kVA | --> | 0.38 | 0 | 0.043 | 0.323 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3027 | -6.3617
034506 | MV/LV Substation CL***506 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 0.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E23 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.4129 | -7.7552
066213 | MV/LV Substation KI***213 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3853 | -6.0512
047053X | MV/LV Substation EL***053X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8444 | -8.1976
251031 | MV/LV Substation PA***031 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =388 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C16 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.3032 | -8.9901
053575Y | MV/LV Substation CL***575Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =492 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2679 | -7.467
253205X | MV/LV Substation EL***205X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E17 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4676 | -9.1093
3654066 | MV/LV Substation M5***4066 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.38 | 0 | 0 | 0.348 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3086 | -6.3533
067687X | MV/LV Substation BU***687X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E18 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.7044 | -8.8146
004452Y | MV/LV Substation WO***452Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.45 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8312 | -6.2316
011717X | MV/LV Substation AR***717X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 5.05 |  | --> | 0.095 | 0 | 0.08 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.659 | -7.2099
093201Z | MV/LV Substation GE***201Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =337 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C20 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.4009 | -6.2598
365460X | MV/LV Substation KE***460X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.216 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.354 | 0 |  | --> | C22 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2971 | -6.3787
150325 | MV/LV Substation SH***325 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.382 | 3.96 |  | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =556 kW | --> | E21 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7989 | -7.7787
165096 | MV/LV Substation KN***096 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.6509 | -8.9992
068818 | MV/LV Substation IL***818 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =912 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3509 | -6.2635
167928Y | MV/LV Substation KI***928Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9431 | -8.5973
039414X | MV/LV Substation DU***414X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =508 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C13 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2841 | -9.0517
3684045 | MV/LV Substation BE***4045 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7668 | -8.8459
365129 | MV/LV Substation SA***129 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2703 | -6.3898
059554Y | MV/LV Substation TH***554Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0842 | -7.4165
256818 | MV/LV Substation DE***818 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8585 | -8.3978
0344247 | MV/LV Substation BA***4247 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.95 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3673 | -7.5603
003039 | MV/LV Substation ST***039 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 11.58 |  | --> | 0.38 | 0 | 0.052 | 0 | 0 | Constrained, otherwise capacity available =324 kW | --> | C22 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9779 | -6.0474
065495Z | MV/LV Substation BA***495Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5888 | -6.1993
281961Z | MV/LV Substation GA***961Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.49 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8759 | -8.4437
075084Y | MV/LV Substation TO***084Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.035 | 1.13 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6067 | -6.603
039593X | MV/LV Substation CU***593X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =125 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C19 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.2916 | -8.9912
014292Z | MV/LV Substation SI***292Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 0.63 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C17 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1494 | -6.7184
043001 | MV/LV Substation TH***001 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.166 | 0.43 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C19 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9433 | -8.9498
064765 | MV/LV Substation TR***765 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =19 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7623 | -6.2721
067276X | MV/LV Substation AS***276X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 13.8 |  | --> | 0.38 | 0 | 0.03 | 0.345 | 0 |  | --> | C20 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6619 | -8.6018
082841Y | MV/LV Substation CH***841Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.628 | -6.5297
041962X | MV/LV Substation BR***962X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7206 | -8.8729
2064048 | MV/LV Substation ER***4048 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.6 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex BELMULLET | Belmullet [T421] | BELLACORICK |  | 54.2306 | -10.0309
093057Y | MV/LV Substation IS***057Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0 | 0.369 | 0 |  | --> | C11 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3877 | -6.0677
293469Y | MV/LV Substation TU***469Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.102 | 0.43 |  | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =139 kW | --> | E19 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8102 | -6.7212
162601 | MV/LV Substation CA***601 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.092 | 0.25 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8034 | -7.5936
059393Y | MV/LV Substation ES***393Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =103 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C18 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0014 | -7.3589
082952 | MV/LV Substation HA***952 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.6712 | -6.5968
3684007 | MV/LV Substation CA***4007 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7967 | -8.79
075231 | MV/LV Substation CO***231 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 0.58 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E17 ex FERNS | Ferns [T421] | CRANE |  | 52.6427 | -6.4561
008815 | MV/LV Substation CL***815 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex CLONROCHE | Clonroche [T421,T422] | WEXFORD |  | 52.4333 | -6.8182
130761 | MV/LV Substation PA***761 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =919 kVA | --> | 0.95 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =935 kW | --> | E11 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7777 | -7.4987
015864Z | MV/LV Substation MA***864Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1985 | -6.4649
099145X | MV/LV Substation CA***145X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9832 | -7.6902
069244 | MV/LV Substation BR***244 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.33 | 0.87 |  | --> | 0.598 | 0 | 0.042 | 0.5 | 0 |  | --> | C20 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3124 | -6.2771
233584 | MV/LV Substation RA***584 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C21 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.1666 | -9.4584
048222X | MV/LV Substation DR***222X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 1.31 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C14 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.8568 | -7.9155
281563Y | MV/LV Substation WE***563Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.042 | 0.154 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8867 | -8.6146
014980Z | MV/LV Substation KC***980Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1544 | -7.0367
119539 | MV/LV Substation KI***539 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.079 | -8.9815
033044 | MV/LV Substation E ***044 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0.059 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex CREGG ROAD | Cregg Road [T41,T42] | BALLYDINE |  | 52.3473 | -7.4002
160100Z | MV/LV Substation BR***100Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0447 | -7.2612
033629Y | MV/LV Substation KY***629Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C12 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.3327 | -7.3145
068080X | MV/LV Substation MO***080X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3562 | -6.2559
007904Z | MV/LV Substation PA***904Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =870 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =932 kW | --> | C14 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3364 | -6.4591
053678Y | MV/LV Substation AR***678Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 3.28 |  | --> | 0.19 | 0 | 0.028 | 0.16 | 0 |  | --> | C23 ex SRAH | Srah [T43] | THORNSBERRY |  | 53.2846 | -7.4887
075120 | MV/LV Substation BA***120 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5414 | -6.3568
008460Z | MV/LV Substation FA***460Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 0.2 |  | --> | 0.19 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2795 | -6.8411
109564 | MV/LV Substation CN***564 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7584 | -8.8736
065471 | MV/LV Substation AR***471 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.6081 | -6.3941
041573X | MV/LV Substation CA***573X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.8087 | -9.0979
049046Z | MV/LV Substation MC***046Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 0.21 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E19 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7145 | -7.8182
1274237 | MV/LV Substation BA***4237 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6395 | -7.7212
154568Z | MV/LV Substation PR***568Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =562 kVA | --> | 0.598 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =574 kW | --> | E14 ex CORDUFF |  |  |  | 53.4152 | -6.3492
006687Y | MV/LV Substation BE***687Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 3.12 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5039 | -6.5806
149937 | MV/LV Substation EN***937 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C14 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6592 | -8.1118
238396 | MV/LV Substation CA***396 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6416 | -9.379
017446Z | MV/LV Substation AS***446Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.6084 | -9.055
052627Z | MV/LV Substation LA***627Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C17 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5308 | -7.3188
025827 | MV/LV Substation KN***827 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.3393 | -8.9574
288326 | MV/LV Substation AI***326 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2549 | -6.2836
238004 | MV/LV Substation TH***004 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =65 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E11 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6217 | -9.2135
008521X | MV/LV Substation CE***521X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =15 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E17 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3648 | -6.7742
158901X | MV/LV Substation LI***901X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C16 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9368 | -9.3995
167014 | MV/LV Substation OW***014 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 52.0399 | -8.4273
060325X | MV/LV Substation DU***325X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9387 | -7.0219
074392X | MV/LV Substation AN***392X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 8.5 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0198 | -7.9435
281159 | MV/LV Substation RO***159 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.19 | 0 | 0.041 | 0.142 | 0 |  | --> | C20 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.882 | -8.5314
039206X | MV/LV Substation CA***206X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C12 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.3322 | -9.0185
0464157 | MV/LV Substation LI***4157 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C13 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2666 | -8.4605
0254356 | MV/LV Substation MO***4356 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4195 | -8.5755
0644290 | MV/LV Substation OL***4290 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.38 | 0 | 0.063 | 0 | 0 | Constrained, otherwise capacity available =299 kW | --> | C18 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7132 | -6.3876
288023X | MV/LV Substation BR***023X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0.017 | 0.352 | 0 |  | --> | C19 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2716 | -6.2545
365701X | MV/LV Substation MI***701X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =445 kVA | --> | 0.598 | 0 | 0.043 | 0.5 | 0 |  | --> | C15 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2821 | -6.3518
0084372 | MV/LV Substation AR***4372 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4045 | -6.9305
154283 | MV/LV Substation AS***283 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.3948 | -6.3775
004014 | MV/LV Substation CO***014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =137 kVA | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =323 kW | --> | C25 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7949 | -6.1582
154546 | MV/LV Substation CL***546 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =923 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =944 kW | --> | C21 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4084 | -6.3559
138869 | MV/LV Substation SU***869 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 2.18 |  | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | C24 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9169 | -6.9721
013029 | MV/LV Substation FO***029 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =123 kVA | --> | 0.19 | 0 | 0.01 | 0.172 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9864 | -6.9909
059991X | MV/LV Substation SW***991X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9916 | -7.3764
062694Y | MV/LV Substation OA***694Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.31 | 0.72 |  | --> | 0.38 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C16 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0006 | -6.3912
049951X | MV/LV Substation RU***951X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 0.21 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E14 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7358 | -7.8068
2664017 | MV/LV Substation CA***4017 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E11 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2426 | -7.2756
064322 | MV/LV Substation BE***322 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =69 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E18 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6438 | -6.3451
109556 | MV/LV Substation DE***556 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.378 | 0.38 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C22 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.6828 | -8.9213
293018 | MV/LV Substation WR***018 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 0.43 |  | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =347 kW | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7981 | -6.7446
293958Z | MV/LV Substation GR***958Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8207 | -6.7061
067802 | MV/LV Substation PA***802 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C16 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.6957 | -8.6164
046318X | MV/LV Substation CA***318X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 4.13 |  | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C14 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3359 | -8.527
265014Y | MV/LV Substation KI***014Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.07 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1194 | -7.5839
038689 | MV/LV Substation TE***689 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0342 | -8.8846
039147X | MV/LV Substation TE***147X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.217 | 11.03 |  | --> | 0.38 | 0 | 0 | 0.362 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2486 | -9.1995
2884157 | MV/LV Substation SA***4157 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2794 | -6.2124
062114X | MV/LV Substation LI***114X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 19.76 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E19 ex MULLAGHARLIN | Mullagharlin [T121,T122] | MULLAGHARLIN |  | 53.9791 | -6.5216
0814266 | MV/LV Substation AR***4266 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =476 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3573 | -6.546
026724X | MV/LV Substation P+***724X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.327 | 8.66 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C11 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7455 | -8.7334
209539 | MV/LV Substation ME***539 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C21 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1973 | -7.8142
009844X | MV/LV Substation CA***844X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | C12 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.2716 | -7.2153
350597 | MV/LV Substation FI***597 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4987 | -8.2268
015859Y | MV/LV Substation HA***859Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =248 kVA | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2432 | -6.5939
029471Y | MV/LV Substation TR***471Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C32 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8602 | -8.1311
182935 | MV/LV Substation WA***935 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7929 | -8.7702
047668 | MV/LV Substation BA***668 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 1.04 |  | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C18 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.8962 | -8.3014
015821Z | MV/LV Substation PO***821Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1169 | -6.5823
281662Z | MV/LV Substation PO***662Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8766 | -8.5723
064340Z | MV/LV Substation BO***340Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7389 | -6.4234
099564X | MV/LV Substation LE***564X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =471 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9462 | -7.751
116033Y | MV/LV Substation CL***033Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.8332 | -9.4761
017801X | MV/LV Substation DU***801X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.1 | 1.58 |  | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C11 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.6068 | -9.0972
293754Z | MV/LV Substation PA***754Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 0.43 |  | --> | 0.38 | 0 | 0.083 | 0 | 0 | Constrained, otherwise capacity available =308 kW | --> | E16 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8073 | -6.7214
064537 | MV/LV Substation BE***537 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6642 | -6.3567
238111Y | MV/LV Substation RA***111Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E13 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6231 | -9.2288
011308X | MV/LV Substation MI***308X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.037 | 0.04 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C11 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5443 | -7.3875
064609 | MV/LV Substation TH***609 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6503 | -6.4744
2814340 | MV/LV Substation CC***4340 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C11 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8312 | -8.3599
032289Y | MV/LV Substation SE***289Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C23 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.173 | -7.1455
363902 | MV/LV Substation GO***902 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5015 | -9.6477
108033X | MV/LV Substation AL***033X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 1.57 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.503 | -8.1974
111962X | MV/LV Substation CA***962X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.312 | 3.64 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C18 ex CASTLETOWNBERE | Castletownbere [T42] | BALLYLICKY |  | 51.6524 | -9.8994
068791 | MV/LV Substation SH***791 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.38 | 0 | 0.006 | 0.342 | 0 |  | --> | C11 ex DRUMCONDRA | Drumcondra [T41,T42] | MCDERMOTT |  | 53.3605 | -6.2575
161764 | MV/LV Substation CL***764 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.13 | 11.03 |  | --> | 0.095 | 0 | 0 | 0.099 | 0 |  | --> | C27 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.3224 | -9.1609
266248X | MV/LV Substation CR***248X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3539 | -7.3398
156776X | MV/LV Substation CA***776X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2087 | -6.8356
2514037 | MV/LV Substation MC***4037 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =6 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C12 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.3138 | -8.9867
007919X | MV/LV Substation DA***919X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2583 | -6.4461
366694 | MV/LV Substation ST***694 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.45 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2589 | -9.6065
034961X | MV/LV Substation NA***961X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 5.88 |  | --> | 0.19 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C12 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3569 | -7.6868
075281Y | MV/LV Substation CO***281Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.13 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6156 | -6.6228
0664223 | MV/LV Substation CO***4223 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5195 | -6.265
366049 | MV/LV Substation N.***049 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 0.45 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2612 | -9.6102
0894003 | MV/LV Substation RU***4003 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E22 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2329 | -8.8352
031290 | MV/LV Substation KI***290 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E12 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.208 | -7.423
054201Z | MV/LV Substation TI***201Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E19 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.028 | -7.2914
0344133 | MV/LV Substation ME***4133 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.303 | 5.88 |  | --> | 0.598 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =526 kW | --> | C11 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3621 | -7.7087
209104X | MV/LV Substation CU***104X |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.031 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C16 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0457 | -7.8274
1164094 | MV/LV Substation DR***4094 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.8198 | -9.4219
3654232 | MV/LV Substation BS***4232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C16 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2911 | -6.3751
009365 | MV/LV Substation CH***365 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 0.95 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C22 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2596 | -7.1415
030004 | MV/LV Substation FR***004 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.38 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =326 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9494 | -7.8437
031861 | MV/LV Substation FL***861 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =424 kVA | --> | 0.598 | 0 | 0.516 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2111 | -7.4258
365017 | MV/LV Substation DE***017 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0.185 | 0.446 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2711 | -6.3775
037899X | MV/LV Substation PU***899X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 13.05 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C12 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8564 | -8.9666
055407Y | MV/LV Substation MA***407Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C17 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7898 | -7.8357
029533X | MV/LV Substation SP***533X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9238 | -8.2907
180772X | MV/LV Substation NU***772X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.132 | 3.27 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C12 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7268 | -6.8938
062592Y | MV/LV Substation SE***592Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 3.12 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9621 | -6.3753
0934179 | MV/LV Substation WE***4179 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =813 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.408 | -6.1664
2044149 | MV/LV Substation CL***4149 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E13 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2629 | -7.4143
064470Y | MV/LV Substation OR***470Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | E11 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7824 | -6.4943
099207X | MV/LV Substation DO***207X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.345 | 5.45 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C18 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9616 | -7.713
0664497 | MV/LV Substation EG***4497 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E15 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5093 | -6.4026
043314 | MV/LV Substation SE***314 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.041 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9493 | -8.96
293815Z | MV/LV Substation LA***815Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 0.43 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.737 | -6.7686
368169X | MV/LV Substation CA***169X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8143 | -8.8029
0814232 | MV/LV Substation KI***4232 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =449 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3149 | -6.422
350998 | MV/LV Substation GU***998 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.455 | -8.2824
161452X | MV/LV Substation CE***452X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 0.45 |  | --> | 0.095 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =69 kW | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2365 | -9.4929
068029X | MV/LV Substation SW***029X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.404 | 2.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3467 | -6.2654
132690 | MV/LV Substation WO***690 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 1.62 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C16 ex CURRA | Curra [T41] | SOMERSET |  | 53.0478 | -8.3988
0714015 | MV/LV Substation AL***4015 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0.006 | 0.369 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1318 | -6.0717
031546Y | MV/LV Substation AP***546Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C17 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0973 | -7.6303
025532Y | MV/LV Substation TH***532Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 6.21 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.4033 | -8.7816
075383X | MV/LV Substation MI***383X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5873 | -6.4751
144954X | MV/LV Substation MA***954X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C16 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.7741 | -7.2485
495366 | MV/LV Substation BA***366 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.5 |  | --> | 0.095 | 0 | 0.005 | 0.09 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0272 | -9.8258
099010 | MV/LV Substation CR***010 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C12 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9561 | -7.7105
1654103 | MV/LV Substation IN***4103 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C14 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6006 | -8.8713
037648X | MV/LV Substation BA***648X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.347 | 13.05 |  | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C20 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8457 | -8.9843
093208 | MV/LV Substation MA***208 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.044 | 0.333 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3774 | -6.1651
012017 | MV/LV Substation SH***017 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =103 kVA | --> | 0.19 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C11 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8411 | -6.8984
058010 | MV/LV Substation SA***010 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C11 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.8716 | -8.1959
007285Z | MV/LV Substation GR***285Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 0.2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2552 | -6.7293
1164032 | MV/LV Substation RO***4032 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 8.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7975 | -9.5604
365457X | MV/LV Substation PA***457X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.19 | 0 | 0.039 | 0.143 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3027 | -6.3522
164952X | MV/LV Substation CU***952X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =613 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5594 | -9.268
0934061 | MV/LV Substation DU***4061 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 7.91 |  | --> | 0.095 | 0 | 0.006 | 0.09 | 0 |  | --> | C26 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3787 | -6.3346
136289Y | MV/LV Substation RU***289Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6896 | -8.2014
111824Z | MV/LV Substation DU***824Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C12 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6196 | -9.5248
161124 | MV/LV Substation TU***124 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =605 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C12 ex SPIDDAL |  |  |  | 53.2384 | -9.4863
0824089 | MV/LV Substation 02***4089 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6404 | -6.6625
011712Z | MV/LV Substation DA***712Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C20 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6347 | -7.2486
0694108 | MV/LV Substation BE***4108 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.28 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3287 | -6.214
0174140 | MV/LV Substation WA***4140 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.98 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4628 | -8.9233
007171X | MV/LV Substation WE***171X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.9 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3288 | -6.4922
0674369 | MV/LV Substation MI***4369 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 6.81 |  | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C03 ex AHANE | Ahane [T102] | AHANE |  | 52.6662 | -8.551
008776X | MV/LV Substation CA***776X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.205 | 0.2 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | E16 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2862 | -6.9406
0434107 | MV/LV Substation MI***4107 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.8519 | -8.8548
069548 | MV/LV Substation CA***548 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.248 | 0.98 |  | --> | 0.38 | 0 | 0.011 | 0.351 | 0 |  | --> | C11 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3299 | -6.2606
046371 | MV/LV Substation AR***371 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 4.13 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | C13 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3774 | -8.4911
009809Y | MV/LV Substation PU***809Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.148 | 0.95 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.257 | -7.1566
061317X | MV/LV Substation GR***317X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.0917 | -6.8491
1604059 | MV/LV Substation PR***4059 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =528 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C15 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1128 | -7.3207
067320X | MV/LV Substation QU***320X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.689 | -8.631
061462 | MV/LV Substation GR***462 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.0938 | -6.8509
054857X | MV/LV Substation BA***857X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9557 | -7.3023
018001 | MV/LV Substation CH***001 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.227 | 3.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C11 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4458 | -9.485
059424Y | MV/LV Substation DR***424Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C22 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9966 | -7.3492
0014111 | MV/LV Substation EN***4111 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.55 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.3016 | -6.1806
053565 | MV/LV Substation CR***565 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E20 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.3326 | -7.2773
007569Z | MV/LV Substation TA***569Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 16.12 |  | --> | 0.19 | 0 | 0 | 0.185 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3252 | -6.6581
065153Z | MV/LV Substation RO***153Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C19 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5757 | -6.1039
099321X | MV/LV Substation AS***321X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9453 | -7.6826
075549 | MV/LV Substation RA***549 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5421 | -6.3855
058637 | MV/LV Substation PO***637 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 3 |  | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8827 | -8.3516
214846 | MV/LV Substation CU***846 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C15 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7468 | -9.1483
109085 | MV/LV Substation CR***085 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 0.38 |  | --> | 0.38 | 0 | 0.019 | 0.351 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.706 | -8.8662
023215Y | MV/LV Substation DO***215Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.132 | 0.22 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C16 ex KILSHANNY | Kilshanny [T41,T42] | CAHIR |  | 52.2121 | -8.0403
365337X | MV/LV Substation RO***337X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0 | 0.367 | 0 |  | --> | C12 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2889 | -6.4032
053026 | MV/LV Substation MO***026 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.19 | 0 | 0.044 | 0.142 | 0 |  | --> | E20 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.298 | -7.2927
2564099 | MV/LV Substation WI***4099 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.104 | 1.28 |  | --> | 0.19 | 0 | 0.15 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | C22 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.8347 | -8.3207
156508X | MV/LV Substation CL***508X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3021 | -6.8937
118026 | MV/LV Substation TH***026 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.27 | 2 |  | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C12 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3262 | -8.1991
136150Y | MV/LV Substation LE***150Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.5464 | -8.052
043089 | MV/LV Substation CA***089 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9283 | -8.9545
0694032 | MV/LV Substation FR***4032 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =541 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DONNYBROOK | Donnybrook [T41,T42] | MILLTOWN (DR) |  | 53.331 | -6.2327
0054262 | MV/LV Substation GA***4262 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =493 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =571 kW | --> | C15 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6785 | -6.2893
2554098 | MV/LV Substation TA***4098 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.09 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6206 | -8.6116
0684241 | MV/LV Substation HO***4241 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3484 | -6.2633
082159Z | MV/LV Substation BL***159Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.156 | 2.01 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6554 | -6.6783
015865Y | MV/LV Substation CP***865Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C11 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.1808 | -6.5917
2814234 | MV/LV Substation RI***4234 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =381 kVA | --> | 0.38 | 0 | 0.005 | 0.374 | 0 |  | --> | C15 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8902 | -8.5394
068046 | MV/LV Substation JA***046 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.47 |  | --> | 0.95 | 0 | 0.016 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3395 | -6.322
041148Y | MV/LV Substation LI***148Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E21 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7353 | -8.9953
2884022 | MV/LV Substation RO***4022 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0.011 | 0.363 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2603 | -6.2301
2484247 | MV/LV Substation MU***4247 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4577 | -6.6352
005557X | MV/LV Substation CO***557X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 17.8 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6449 | -6.2277
068628X | MV/LV Substation GE***628X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3462 | -6.2504
136125Y | MV/LV Substation PU***125Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C18 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.5455 | -8.0522
052558Z | MV/LV Substation AR***558Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.038 | 10.9 |  | --> | 0.19 | 0 | 0.024 | 0.149 | 0 |  | --> | C18 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5245 | -7.365
2484013 | MV/LV Substation SU***4013 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4873 | -6.7217
120471Y | MV/LV Substation BE***471Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =514 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | E18 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3423 | -7.0518
067568X | MV/LV Substation RO***568X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C11 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6007 | -8.6811
029473Y | MV/LV Substation CA***473Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C18 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 52.0095 | -8.236
012423Y | MV/LV Substation DE***423Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8449 | -6.9256
119206 | MV/LV Substation KN***206 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1201 | -8.8975
276043 | MV/LV Substation DR***043 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.099 | 0.76 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C18 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0518 | -9.5006
064743Y | MV/LV Substation FO***743Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7308 | -6.3398
067231Z | MV/LV Substation CO***231Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C20 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6771 | -8.6753
050020Y | MV/LV Substation IR***020Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.176 | 7.61 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4216 | -7.9336
009847Y | MV/LV Substation BU***847Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.476 | 13.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2447 | -7.1666
109238 | MV/LV Substation KI***238 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.38 |  | --> | 0.048 | 0 | 0.01 | 0.039 | 0 |  | --> | C14 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7594 | -8.9119
161582 | MV/LV Substation CI***582 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 11.03 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C27 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.3221 | -9.1773
067097 | MV/LV Substation UN***097 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.399 | 6.81 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C05 ex AHANE | Ahane [T102] | AHANE |  | 52.6641 | -8.5036
0524504 | MV/LV Substation AL***4504 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E19 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.4529 | -7.0995
0644341 | MV/LV Substation BE***4341 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0.078 | 0 | 0 | Constrained, otherwise capacity available =318 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6599 | -6.4135
156237Z | MV/LV Substation SW***237Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C13 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2465 | -6.9793
255158X | MV/LV Substation PI***158X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =566 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6369 | -8.4404
007589Y | MV/LV Substation CO***589Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.2 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2643 | -6.744
0324240 | MV/LV Substation MA***4240 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex KILMEADEN | Kilmeaden [T42] | BUTLERSTOWN |  | 52.2386 | -7.2497
184609 | MV/LV Substation CR***609 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1594 | -6.8171
0014033 | MV/LV Substation AU***4033 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 4.01 |  | --> | 0.38 | 0 | 0.003 | 0.372 | 0 |  | --> | C19 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2654 | -6.1372
069189 | MV/LV Substation RO***189 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =438 kVA | --> | 0.598 | 0 | 0.019 | 0.5 | 0 |  | --> | C21 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.291 | -6.3001
062427Y | MV/LV Substation ME***427Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.278 | 3.47 |  | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E17 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0385 | -6.1863
005487 | MV/LV Substation BA***487 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 17.8 |  | --> | 0.19 | 0 | 0.003 | 0.183 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6432 | -6.2335
0814148 | MV/LV Substation LE***4148 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =395 kVA | --> | 0.38 | 0 | 0.005 | 0.376 | 0 |  | --> | C17 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3358 | -6.4024
0584159 | MV/LV Substation CB***4159 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C15 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.8667 | -8.1926
052573Z | MV/LV Substation LY***573Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5193 | -7.3488
037002 | MV/LV Substation CA***002 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.334 | 13.05 |  | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C17 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8433 | -8.988
029570X | MV/LV Substation BA***570X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8297 | -8.023
237200X | MV/LV Substation DA***200X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8402 | -6.2875
058718Y | MV/LV Substation CA***718Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 3 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C18 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8674 | -8.2048
063760 | MV/LV Substation ST***760 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C16 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8228 | -6.4702
008107 | MV/LV Substation CA***107 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3584 | -6.9493
001115 | MV/LV Substation CO***115 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.352 | 4.37 |  | --> | 0.598 | 0 | 0.022 | 0.5 | 0 |  | --> | C21 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2907 | -6.1338
001235 | MV/LV Substation AI***235 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0.019 | 0.353 | 0 |  | --> | C18 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3137 | -6.2294
281429 | MV/LV Substation TH***429 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 4.3 |  | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C19 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8681 | -8.3331
153052 | MV/LV Substation CL***052 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E11 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7172 | -8.4071
0034260 | MV/LV Substation BU***4260 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.58 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9873 | -6.0665
009771Y | MV/LV Substation GA***771Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2425 | -7.1654
0644386 | MV/LV Substation FR***4386 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =598 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7158 | -6.3578
068499 | MV/LV Substation WA***499 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =285 kVA | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C11 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3375 | -6.2749
052578Z | MV/LV Substation AR***578Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 10.9 |  | --> | 0.38 | 0 | 0.026 | 0.347 | 0 |  | --> | C18 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.525 | -7.3681
066354X | MV/LV Substation TH***354X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C19 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4535 | -6.1629
009019 | MV/LV Substation TY***019 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.429 | 0.95 |  | --> | 0.598 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =569 kW | --> | C18 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2565 | -7.1294
022532X | MV/LV Substation CA***532X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 4.55 |  | --> | 0.19 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C13 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1399 | -8.637
154430 | MV/LV Substation TA***430 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.138 | 7.91 |  | --> | 0.19 | 0 | 0.056 | 0.14 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3843 | -6.3668
082700Y | MV/LV Substation JO***700Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6428 | -6.6545
008126 | MV/LV Substation CL***126 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 0.2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2971 | -6.7726
111768X | MV/LV Substation CA***768X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E11 ex BALLYDEHOB | Ballydehob [T421] | DUNMANWAY |  | 51.5291 | -9.5515
209537 | MV/LV Substation CR***537 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C21 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1398 | -7.6971
009130Y | MV/LV Substation CA***130Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.162 | 3.82 |  | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C14 ex WATERFORD | Waterford [T41,T42] | WATERFORD |  | 52.2637 | -7.1318
003184 | MV/LV Substation WO***184 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.059 | 11.58 |  | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =152 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9947 | -6.0796
0494121 | MV/LV Substation BA***4121 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5789 | -7.9436
1564234 | MV/LV Substation DR***4234 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 2.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E17 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.2287 | -6.9681
007415Z | MV/LV Substation MO***415Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.279 | 16.12 |  | --> | 0.38 | 0 | 0.027 | 0.343 | 0 |  | --> | E14 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3329 | -6.4919
007167X | MV/LV Substation CO***167X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.392 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3279 | -6.4891
0294403 | MV/LV Substation BA***4403 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.8863 | -8.1573
046367X | MV/LV Substation DA***367X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.166 | 5.48 |  | --> | 0.19 | 0 | 0 | 0.185 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2712 | -8.4216
050312Y | MV/LV Substation CA***312Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C21 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4184 | -7.9919
049669 | MV/LV Substation LI***669 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7694 | -7.8186
2884179 | MV/LV Substation SU***4179 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =595 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2359 | -6.1965
067856Y | MV/LV Substation BU***856Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E12 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7211 | -8.862
059425X | MV/LV Substation DR***425X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9999 | -7.3494
3654088 | MV/LV Substation CI***4088 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.38 | 0 | 0.089 | 0.282 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2878 | -6.4213
065012 | MV/LV Substation MI***012 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C19 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5763 | -6.1068
207176 | MV/LV Substation WA***176 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.025 | 3.38 |  | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7389 | -7.5659
011298X | MV/LV Substation CA***298X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 2.8 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6426 | -7.2322
024461 | MV/LV Substation BR***461 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.14 |  | --> | 0.048 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =33 kW | --> | C18 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2336 | -8.7179
0624280 | MV/LV Substation TB***4280 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.0283 | -6.4143
118093Y | MV/LV Substation PU***093Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.288 | -8.3861
111822Z | MV/LV Substation CU***822Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C11 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6499 | -9.3792
176781X | MV/LV Substation MU***781X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 18.78 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9234 | -8.9941
136511 | MV/LV Substation CH***511 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =102 kVA | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =155 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6716 | -7.9855
050140X | MV/LV Substation SG***140X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 6.49 |  | --> | 0.095 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =67 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4583 | -7.8858
067057Z | MV/LV Substation B ***057Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =562 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6498 | -8.5739
066223Z | MV/LV Substation PO***223Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C16 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4401 | -6.1348
007845Y | MV/LV Substation RA***845Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.143 | 0.14 | Constrained, otherwise capacity available =500 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3433 | -6.4646
0094046 | MV/LV Substation KI***4046 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C15 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.3058 | -7.1736
368810 | MV/LV Substation AD***810 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.743 | -8.6346
139422X | MV/LV Substation FI***422X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C19 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8483 | -7.2399
345070X | MV/LV Substation BE***070X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2919 | -7.8764
0354120 | MV/LV Substation MO***4120 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 6.17 |  | --> | 0.048 | 0 | 0.056 | 0 | 0 | Constrained, otherwise capacity available =5 kW | --> | C24 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.4048 | -7.8679
176677 | MV/LV Substation CL***677 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 18.78 |  | --> | 0.19 | 0 | 0 | 0.185 | 0 |  | --> | E18 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9317 | -9.0239
033979X | MV/LV Substation FE***979X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.3019 | -7.4651
029938X | MV/LV Substation AG***938X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.31 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8368 | -8.2278
044674 | MV/LV Substation PU***674 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9842 | -9.1147
180656X | MV/LV Substation ST***656X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 0.68 |  | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =150 kW | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.7736 | -6.7948
248074 | MV/LV Substation SP***074 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4779 | -6.7136
017711 | MV/LV Substation FI***711 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.183 | 1.58 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C17 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.5617 | -9.1877
0094124 | MV/LV Substation WE***4124 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.463 | 13.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2496 | -7.1628
050959Y | MV/LV Substation FO***959Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =114 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4283 | -8.013
417751 | MV/LV Substation LI***751 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.1384 | -8.1397
0784074 | MV/LV Substation C-***4074 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C19 ex CHARLESTOWN |  |  |  | 53.9463 | -8.7815
160658 | MV/LV Substation AF***658 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1549 | -7.4733
065475X | MV/LV Substation BO***475X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5468 | -6.4147
0934171 | MV/LV Substation SA***4171 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =732 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3958 | -6.247
062649Y | MV/LV Substation CA***649Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.424 | 2.33 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =570 kW | --> | C18 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.0312 | -6.4063
288009 | MV/LV Substation PI***009 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =460 kVA | --> | 0.598 | 0 | 0.08 | 0.5 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2703 | -6.2557
015664Z | MV/LV Substation CO***664Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2959 | -6.7003
005985X | MV/LV Substation KI***985X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.6881 | -6.4923
029023 | MV/LV Substation CO***023 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.38 | 0 | 0.01 | 0.321 | 0 |  | --> | C17 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9168 | -8.1736
049482Y | MV/LV Substation LE***482Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8472 | -7.5316
0144059 | MV/LV Substation PE***4059 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =328 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =567 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1453 | -7.0131
0934335 | MV/LV Substation ME***4335 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3914 | -6.318
069267 | MV/LV Substation KI***267 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.401 | 7.75 |  | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C16 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3203 | -6.258
0064011 | MV/LV Substation KI***4011 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 4.38 |  | --> | 0.19 | 0 | 0.01 | 0.179 | 0 |  | --> | E11 ex CRANE | Crane [T122] | CRANE |  | 52.5227 | -6.5615
0644173 | MV/LV Substation SH***4173 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7235 | -6.4589
125220 | MV/LV Substation NE***220 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.22 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C16 ex KILSHANNY | Kilshanny [T41,T42] | CAHIR |  | 52.2699 | -8.1092
062744Y | MV/LV Substation CO***744Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.304 | 3.12 |  | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C11 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.987 | -6.3876
036058 | MV/LV Substation SP***058 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4752 | -8.1574
204553 | MV/LV Substation FA***553 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.02 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.0616 | -7.4738
067186 | MV/LV Substation GO***186 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.029 | 0.342 | 0 |  | --> | C14 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6378 | -8.6564
281127X | MV/LV Substation TH***127X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 5.49 |  | --> | 0.19 | 0 | 0.059 | 0.135 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8676 | -8.4648
355147X | MV/LV Substation SP***147X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =547 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C15 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0566 | -8.7229
052231Z | MV/LV Substation TH***231Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 10.9 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C13 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5732 | -7.3258
012458Y | MV/LV Substation RA***458Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.99 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8479 | -6.984
064332 | MV/LV Substation CA***332 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6673 | -6.4002
0644250 | MV/LV Substation BE***4250 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =395 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6975 | -6.2468
429150X | MV/LV Substation PI***150X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 5.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E15 ex ABBEYFEALE | Abbeyfeale [T421] | TRIEN |  | 52.3616 | -9.3092
001725 | MV/LV Substation MC***725 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =224 kVA | --> | 0.38 | 0 | 0.063 | 0.309 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2628 | -6.1667
136519 | MV/LV Substation LA***519 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =107 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6747 | -8.0009
0314190 | MV/LV Substation CO***4190 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.1954 | -7.4271
253011Y | MV/LV Substation BA***011Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E21 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6174 | -8.7385
009951X | MV/LV Substation ST***951X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C17 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2432 | -7.0977
255421 | MV/LV Substation BR***421 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.64 | -8.389
054945Y | MV/LV Substation CA***945Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =133 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C11 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.9759 | -7.4999
0744208 | MV/LV Substation DR***4208 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 8.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0431 | -8.0343
068015X | MV/LV Substation NE***015X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =447 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3375 | -6.2707
253107X | MV/LV Substation CA***107X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.4908 | -8.9337
039972X | MV/LV Substation RA***972X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =520 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2679 | -8.9313
064060 | MV/LV Substation LA***060 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.598 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =541 kW | --> | C14 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7147 | -6.3495
1544124 | MV/LV Substation BE***4124 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =374 kVA | --> | 0.38 | 0 | 0.047 | 0.342 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3911 | -6.4482
108007 | MV/LV Substation PY***007 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.57 |  | --> | 0.598 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | C15 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.4988 | -8.1841
0014154 | MV/LV Substation AC***4154 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2472 | -6.1493
066143X | MV/LV Substation CA***143X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =229 kVA | --> | 0.38 | 0 | 0.059 | 0 | 0 | Constrained, otherwise capacity available =312 kW | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.424 | -6.1353
377004Y | MV/LV Substation AN***004Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =217 kVA | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9458 | -10.2292
065021Z | MV/LV Substation YE***021Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5693 | -6.4556
099361X | MV/LV Substation LI***361X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =733 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =913 kW | --> | C18 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9451 | -7.7331
069628 | MV/LV Substation OR***628 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0.018 | 0.358 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2762 | -6.3181
293182X | MV/LV Substation BA***182X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7632 | -6.5512
039163 | MV/LV Substation CO***163 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C28 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.3282 | -9.0224
069422 | MV/LV Substation KN***422 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.38 | 0 | 0.176 | 0.218 | 0 |  | --> | C19 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2864 | -6.3103
041824 | MV/LV Substation K/***824 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7985 | -8.9257
021635Z | MV/LV Substation CA***635Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =970 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex FAIRHILL | Fairhill [T42] | KILBARRY |  | 51.9017 | -8.4732
008332Z | MV/LV Substation BE***332Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C18 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.388 | -6.9482
405243 | MV/LV Substation IC***243 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.317 | 3.03 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2018 | -6.9841
288969 | MV/LV Substation RI***969 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.005 | 0.181 | 0 |  | --> | C20 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2874 | -6.2415
243066 | MV/LV Substation EM***066 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1406 | -10.1927
0664326 | MV/LV Substation NE***4326 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =568 kVA | --> | 0.598 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =580 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4231 | -6.1681
237218X | MV/LV Substation TH***218X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C16 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8329 | -6.3935
251035 | MV/LV Substation LY***035 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.3071 | -8.9989
039249X | MV/LV Substation GA***249X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =559 kVA | --> | 0.598 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2507 | -8.967
182765 | MV/LV Substation KI***765 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7766 | -8.7834
122573 | MV/LV Substation NO***573 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.352 | 4.18 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8229 | -6.7481
265859X | MV/LV Substation DR***859X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 2.56 |  | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C17 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0334 | -7.5402
067270Y | MV/LV Substation HA***270Y |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =941 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =942 kW | --> | C18 ex CASTLETROY | Castletroy [T41,T42] | ARDNACRUSHA |  | 52.6721 | -8.5549
340658 | MV/LV Substation TI***658 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.8525 | -8.3141
011700X | MV/LV Substation ST***700X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 5.05 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C13 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6649 | -7.2419
046209 | MV/LV Substation BE***209 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 5.78 |  | --> | 0.048 | 0 | 0.004 | 0.042 | 0 |  | --> | C20 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2694 | -8.5964
081657X | MV/LV Substation GL***657X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3474 | -6.3664
3654166 | MV/LV Substation RO***4166 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3174 | -6.3463
156014 | MV/LV Substation AR***014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =284 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2423 | -6.9662
350476 | MV/LV Substation KI***476 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.57 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4451 | -8.2972
281159Y | MV/LV Substation ST***159Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.27 | 5.49 |  | --> | 0.38 | 0 | 0.02 | 0.347 | 0 |  | --> | C18 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8766 | -8.4418
204809 | MV/LV Substation MU***809 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1316 | -7.439
081054Z | MV/LV Substation LI***054Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =672 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =904 kW | --> | C12 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3529 | -6.3916
066102Y | MV/LV Substation GR***102Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =334 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5126 | -6.5431
034700 | MV/LV Substation AU***700 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 0.95 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =929 kW | --> | C16 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3545 | -7.7016
288653 | MV/LV Substation GL***653 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2198 | -6.2238
110332 | MV/LV Substation KI***332 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex KENMARE | Kenmare [T42] | KNOCKEARAGH |  | 51.8858 | -9.5765
1364072 | MV/LV Substation LA***4072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6734 | -7.9924
003034 | MV/LV Substation LE***034 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.105 | 11.58 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C22 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.983 | -6.0424
017461Z | MV/LV Substation BA***461Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3901 | -9.0313
161682 | MV/LV Substation PO***682 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 6.53 |  | --> | 0.048 | 0 | 0.023 | 0.028 | 0 |  | --> | C16 ex OUGHTERARD | Oughterard [T41,T42] | SCREEB |  | 53.4228 | -9.2937
0254054 | MV/LV Substation SK***4054 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.96 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3486 | -8.6581
0684114 | MV/LV Substation SI***4114 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0.043 | 0.5 | 0 |  | --> | C14 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3767 | -6.2372
031461 | MV/LV Substation BA***461 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0524 | -7.6648
017170 | MV/LV Substation SH***170 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.017 | 1.05 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C15 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4439 | -9.0736
1444070 | MV/LV Substation DA***4070 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.7696 | -7.2114
108065X | MV/LV Substation LA***065X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 1.57 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5042 | -8.1826
110636 | MV/LV Substation RO***636 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.19 | 0.76 |  | --> | 0.38 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =321 kW | --> | C16 ex KENMARE | Kenmare [T42] | KNOCKEARAGH |  | 51.8802 | -9.5817
149829 | MV/LV Substation DR***829 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6618 | -8.2074
176524X | MV/LV Substation SH***524X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8692 | -8.8443
0584431 | MV/LV Substation NE***4431 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.7842 | -8.0609
006063 | MV/LV Substation TH***063 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.29 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex MONFIN | Monfin [T41,T42] | WEXFORD |  | 52.4918 | -6.5609
052311Y | MV/LV Substation MI***311Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4426 | -7.2442
0584432 | MV/LV Substation CU***4432 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C26 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9292 | -8.2406
046797 | MV/LV Substation WO***797 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.13 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C14 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3265 | -8.4682
0394095 | MV/LV Substation KN***4095 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.112 | 11.03 |  | --> | 0.19 | 0 | 0.005 | 0.174 | 0 |  | --> | C17 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2694 | -9.1228
281956Z | MV/LV Substation DU***956Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.88 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8997 | -8.4721
019277X | MV/LV Substation CH***277X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C12 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2912 | -9.8281
020644X | MV/LV Substation PA***644X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =317 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C16 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0579 | -9.5096
030005X | MV/LV Substation CA***005X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =523 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9477 | -7.8453
220912 | MV/LV Substation MU***912 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.36 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.1021 | -9.3082
064194Z | MV/LV Substation RO***194Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C12 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7258 | -6.362
281986 | MV/LV Substation A ***986 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C18 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8641 | -8.4033
144065Y | MV/LV Substation BA***065Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =387 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C11 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.7878 | -7.2093
1964057 | MV/LV Substation KE***4057 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 0.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E31 ex TRIM | Trim [T421] | NAVAN |  | 53.5158 | -6.8419
025994 | MV/LV Substation EF***994 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C12 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.362 | -8.6119
253189X | MV/LV Substation CO***189X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.4729 | -8.6529
038405 | MV/LV Substation BA***405 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E13 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0868 | -8.8198
252277 | MV/LV Substation LI***277 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 2.76 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | C13 ex RECESS | Recess [T41] | SCREEB |  | 53.4674 | -9.7395
165999X | MV/LV Substation CR***999X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 0.88 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C12 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5678 | -9.0049
064889X | MV/LV Substation PR***889X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7148 | -6.4328
031422X | MV/LV Substation ST***422X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C11 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.1003 | -7.594
064497 | MV/LV Substation PL***497 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C20 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.6876 | -6.3944
1204333 | MV/LV Substation PR***4333 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.307 | -6.933
176523X | MV/LV Substation CO***523X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 18.78 |  | --> | 0.095 | 0 | 0 | 0.09 | 0 |  | --> | E18 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.8918 | -8.9385
001075 | MV/LV Substation PR***075 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 1.16 |  | --> | 0.38 | 0 | 0.025 | 0.346 | 0 |  | --> | C17 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2944 | -6.1976
029479Y | MV/LV Substation RO***479Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.898 | -8.1629
293838Y | MV/LV Substation BA***838Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.085 | 0 | 0 | Constrained, otherwise capacity available =299 kW | --> | E20 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9411 | -6.7105
063599X | MV/LV Substation CL***599X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.049 | 0 | 0 | Constrained, otherwise capacity available =144 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8517 | -6.5263
250620 | MV/LV Substation TO***620 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.3 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C17 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.199 | -8.1372
064410X | MV/LV Substation BR***410X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7222 | -6.3352
099045 | MV/LV Substation GL***045 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 5.45 |  | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9599 | -7.7513
012018 | MV/LV Substation ME***018 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =5 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8431 | -6.9261
365238X | MV/LV Substation WI***238X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =277 kVA | --> | 0.38 | 0 | 0.038 | 0.335 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3124 | -6.4012
288994 | MV/LV Substation OR***994 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0.056 | 0.32 | 0 |  | --> | C19 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2644 | -6.2015
009350Y | MV/LV Substation WE***350Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.323 | 13.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2489 | -7.1636
281286Y | MV/LV Substation SC***286Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C20 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8784 | -8.4856
043137 | MV/LV Substation TY***137 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9506 | -8.9689
027525X | MV/LV Substation DR***525X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.017 | 7.79 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E12 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.6644 | -9.2728
165078Y | MV/LV Substation FE***078Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6286 | -8.9065
154470Z | MV/LV Substation MI***470Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =468 kVA | --> | 0.598 | 0 | 0.079 | 0 | 0 | Constrained, otherwise capacity available =517 kW | --> | E14 ex CORDUFF |  |  |  | 53.4158 | -6.3443
293113 | MV/LV Substation BA***113 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.013 | 2.83 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | E13 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6485 | -6.9286
066167X | MV/LV Substation LI***167X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 12.96 |  | --> | 0.38 | 0 | 0.003 | 0.364 | 0 |  | --> | C28 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3905 | -6.2027
015913Y | MV/LV Substation ME***913Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =112 kVA | --> | 0.19 | 0 | 0.053 | 0 | 0 | Constrained, otherwise capacity available =138 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2962 | -6.6962
031444Y | MV/LV Substation ST***444Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =159 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C19 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0912 | -7.6285
109041 | MV/LV Substation TU***041 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.065 | 0.38 |  | --> | 0.19 | 0 | 0.06 | 0.126 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7062 | -8.8891
068072X | MV/LV Substation DO***072X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3525 | -6.2657
281409 | MV/LV Substation WE***409 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =305 kVA | --> | 0.38 | 0 | 0.027 | 0.347 | 0 |  | --> | C12 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.886 | -8.6151
067201Z | MV/LV Substation FO***201Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C16 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6174 | -8.6526
023121 | MV/LV Substation LA***121 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex CASTLELYONS | Castlelyons [T421,T422] | BARRYMORE |  | 52.0533 | -8.4026
377479X | MV/LV Substation MU***479X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1225 | -9.898
009805X | MV/LV Substation A.***805X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.2839 | -7.1886
209684X | MV/LV Substation LA***684X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =349 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0857 | -7.6967
160289Y | MV/LV Substation NE***289Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1378 | -7.0478
405157 | MV/LV Substation RE***157 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.452 | 3.03 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =574 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1589 | -7.1227
004343Y | MV/LV Substation PE***343Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C24 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7883 | -6.1669
0294404 | MV/LV Substation RO***4404 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9095 | -8.1936
064128 | MV/LV Substation AN***128 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =103 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C12 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7219 | -6.358
055263Y | MV/LV Substation GL***263Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C12 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9643 | -7.7914
0684421 | MV/LV Substation BR***4421 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3461 | -6.2511
0034068 | MV/LV Substation PR***4068 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9349 | -6.2588
050021 | MV/LV Substation BO***021 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.098 | 7.61 |  | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C11 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4192 | -7.9186
0464100 | MV/LV Substation KN***4100 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 5.78 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2711 | -8.4897
042619X | MV/LV Substation MC***619X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.11 | 1.93 |  | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =316 kW | --> | C16 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.855 | -9.3066
138031 | MV/LV Substation BE***031 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.8945 | -7.0584
047225X | MV/LV Substation CA***225X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 1.04 |  | --> | 0.095 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 54.028 | -8.2781
009928Y | MV/LV Substation DR***928Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex BELVIEW | Belview [T421,T422] | WATERFORD |  | 52.2811 | -7.0478
019319X | MV/LV Substation CE***319X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.047 | 0.05 | Constrained, otherwise capacity available =656 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =902 kW | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2702 | -9.6996
022810X | MV/LV Substation 02***810X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 4.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1426 | -8.6278
156406Y | MV/LV Substation ED***406Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =24 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3194 | -6.9968
0544325 | MV/LV Substation SU***4325 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =468 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =576 kW | --> | E17 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0142 | -7.3076
180793X | MV/LV Substation KN***793X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.7572 | -6.8719
027132 | MV/LV Substation NE***132 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 7.79 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7251 | -9.0527
0684393 | MV/LV Substation ST***4393 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.37 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex SOUTH KING STREET | South King Street [T41,T42] | FRANCIS STREET |  | 53.3414 | -6.265
160019 | MV/LV Substation SP***019 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =107 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C15 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1643 | -7.1893
019194 | MV/LV Substation TE***194 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.317 | 1.54 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C17 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2603 | -9.6883
0544573 | MV/LV Substation SA***4573 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E19 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0295 | -7.2786
066605Z | MV/LV Substation DR***605Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =524 kVA | --> | 0.598 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =571 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4421 | -6.2039
196074X | MV/LV Substation CO***074X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =387 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C18 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5505 | -6.7846
0664387 | MV/LV Substation PA***4387 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4386 | -6.1784
069826 | MV/LV Substation BO***826 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =584 kVA | --> | 0.598 | 0 | 0.009 | 0.5 | 0 |  | --> | C19 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2822 | -6.3005
038938X | MV/LV Substation GO***938X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =315 kVA | --> | 0.38 | 0 | 0.058 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C16 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0661 | -8.8265
503001X | MV/LV Substation TO***001X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0072 | -7.4903
058487Y | MV/LV Substation AB***487Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 3 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C18 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8643 | -8.1883
074567X | MV/LV Substation KN***567X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9743 | -8.1665
156623Y | MV/LV Substation CA***623Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2463 | -6.9677
009685 | MV/LV Substation NA***685 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C15 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.3174 | -7.1749
137226 | MV/LV Substation CL***226 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 2 |  | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | C12 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.4641 | -9.7244
017334Z | MV/LV Substation BU***334Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.186 | 1.05 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C18 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4269 | -9.0161
068834 | MV/LV Substation PH***834 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.192 | 7.91 |  | --> | 0.38 | 0 | 0 | 0.351 | 0 |  | --> | C29 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3734 | -6.3348
156409 | MV/LV Substation QU***409 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 2.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2669 | -7.0242
058002 | MV/LV Substation TY***002 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 3 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C20 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8569 | -8.1918
030122X | MV/LV Substation OA***122X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9546 | -7.868
058080 | MV/LV Substation DI***080 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.319 | 3 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | C20 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8579 | -8.1893
014390Z | MV/LV Substation BU***390Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.134 | 0.63 |  | --> | 0.19 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | E12 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0838 | -6.7936
059224 | MV/LV Substation DR***224 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9955 | -7.3936
0154324 | MV/LV Substation TH***4324 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =545 kVA | --> | 0.598 | 0 | 0.161 | 0 | 0 | Constrained, otherwise capacity available =467 kW | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2411 | -6.5999
013460X | MV/LV Substation RA***460X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0.014 | 0.175 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9462 | -7.0411
009413 | MV/LV Substation PO***413 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.1 | 8.16 |  | --> | 0.19 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =149 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2988 | -7.1124
110649 | MV/LV Substation BA***649 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.227 | 0.76 |  | --> | 0.38 | 0 | 0.093 | 0 | 0 | Constrained, otherwise capacity available =287 kW | --> | C16 ex KENMARE | Kenmare [T42] | KNOCKEARAGH |  | 51.8828 | -9.5925
051663 | MV/LV Substation AC***663 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.22 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E20 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3172 | -7.4945
0154065 | MV/LV Substation BA***4065 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.3019 | -6.711
253406 | MV/LV Substation TU***406 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.522 | -8.8016
064373Z | MV/LV Substation CO***373Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =284 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7023 | -6.3094
116045 | MV/LV Substation QU***045 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 7.32 |  | --> | 0.19 | 0 | 0.012 | 0.173 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7965 | -9.531
2544016 | MV/LV Substation BE***4016 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.4886 | -8.9196
042103 | MV/LV Substation IN***103 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =112 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E18 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8548 | -9.2803
020262 | MV/LV Substation GL***262 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =958 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =944 kW | --> | C12 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0593 | -9.5079
017127X | MV/LV Substation GO***127X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 1.58 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C18 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.6076 | -9.026
0214161 | MV/LV Substation BA***4161 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C18 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9791 | -8.3769
144707 | MV/LV Substation TO***707 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.78 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7346 | -7.426
153326 | MV/LV Substation KI***326 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E12 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8118 | -8.4559
1804183 | MV/LV Substation SU***4183 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.365 | 3.27 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =561 kW | --> | C12 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7308 | -6.8892
099033 | MV/LV Substation KE***033 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9471 | -7.7458
136186Y | MV/LV Substation AR***186Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6191 | -8.1772
067406Y | MV/LV Substation FA***406Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E18 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5718 | -8.6101
011144Z | MV/LV Substation KI***144Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 5.05 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6611 | -7.2274
2814309 | MV/LV Substation CR***4309 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C13 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8928 | -8.5065
066602Z | MV/LV Substation GA***602Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =313 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4383 | -6.1554
281934Z | MV/LV Substation EL***934Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8686 | -8.3932
067085 | MV/LV Substation KN***085 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 13.8 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.5834 | -8.4813
021352Z | MV/LV Substation LU***352Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C21 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9191 | -8.4257
288852 | MV/LV Substation RO***852 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 2.36 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C11 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1922 | -6.1561
028043Y | MV/LV Substation CO***043Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.336 | 19.7 |  | --> | 0.38 | 0 | 0.008 | 0.365 | 0 |  | --> | C14 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8561 | -8.2939
014701 | MV/LV Substation TA***701 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C16 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.2011 | -6.7803
054150 | MV/LV Substation TH***150 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9103 | -7.3347
0534200 | MV/LV Substation PR***4200 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2735 | -7.4787
012227Y | MV/LV Substation OV***227Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.83 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | E17 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7586 | -6.9504
250712 | MV/LV Substation KI***712 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1004 | -8.302
064159Y | MV/LV Substation HE***159Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6933 | -6.4502
025892X | MV/LV Substation BR***892X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.4268 | -8.6663
062172 | MV/LV Substation MU***172 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.376 | 0.72 |  | --> | 0.598 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C15 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 53.9931 | -6.3805
281209Z | MV/LV Substation MA***209Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 4.3 |  | --> | 0.095 | 0 | 0.012 | 0.082 | 0 |  | --> | C19 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8658 | -8.3358
426115 | MV/LV Substation SE***115 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1356 | -10.2701
2534076 | MV/LV Substation KI***4076 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5299 | -8.8477
0014181 | MV/LV Substation KA***4181 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C13 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.254 | -6.1261
116990X | MV/LV Substation KN***990X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 7.32 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7992 | -9.5055
065008 | MV/LV Substation TH***008 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =253 kVA | --> | 0.38 | 0 | 0.023 | 0.342 | 0 |  | --> | C24 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6055 | -6.1727
023337Y | MV/LV Substation CO***337Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =296 kVA | --> | 0.38 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1768 | -8.243
125205 | MV/LV Substation BA***205 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 0.22 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex KILSHANNY | Kilshanny [T41,T42] | CAHIR |  | 52.2728 | -8.0984
082105Z | MV/LV Substation BL***105Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.442 | 2.01 |  | --> | 0.598 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =535 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6555 | -6.7003
021563Z | MV/LV Substation CA***563Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0.006 | 0.375 | 0 |  | --> | C15 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9237 | -8.4002
0114422 | MV/LV Substation FR***4422 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.037 | 0.04 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C11 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5509 | -7.3772
025754Y | MV/LV Substation BA***754Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 2.96 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E13 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3019 | -8.6863
009997 | MV/LV Substation RY***997 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.002 | 13.6 |  | --> | 0.095 | 0 | 0.04 | 0.051 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2422 | -7.1608
069760 | MV/LV Substation DO***760 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.353 | 7.75 |  | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C24 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3107 | -6.2469
0254193 | MV/LV Substation GO***4193 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.3959 | -8.5677
013958Y | MV/LV Substation CO***958Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =123 kVA | --> | 0.19 | 0 | 0 | 0.179 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9808 | -6.9973
127583X | MV/LV Substation FU***583X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 5.89 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5453 | -7.8186
288257X | MV/LV Substation FA***257X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2571 | -6.2918
253035 | MV/LV Substation FA***035 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C12 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.52 | -8.853
081374X | MV/LV Substation MO***374X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =471 kVA | --> | 0.598 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =565 kW | --> | C11 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3593 | -6.3579
001146X | MV/LV Substation CH***146X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2447 | -6.1389
0104163 | MV/LV Substation FO***4163 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5193 | -7.179
176067Y | MV/LV Substation IN***067Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 18.78 |  | --> | 0.095 | 0 | 0.01 | 0.086 | 0 |  | --> | E13 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | HARTNETTS CROSS |  | 51.839 | -9.126
067064Y | MV/LV Substation BR***064Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C16 ex CORBALLY | Corbally [T41,T42] | ARDNACRUSHA |  | 52.6657 | -8.6204
116049 | MV/LV Substation CA***049 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 7.32 |  | --> | 0.19 | 0 | 0.028 | 0.16 | 0 |  | --> | C13 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8033 | -9.5109
055828X | MV/LV Substation SM***828X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C22 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7933 | -7.8291
204828 | MV/LV Substation CA***828 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 2.02 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.0721 | -7.4526
281011 | MV/LV Substation AR***011 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.184 | 7.88 |  | --> | 0.38 | 0 | 0.063 | 0.303 | 0 |  | --> | C17 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8847 | -8.4872
281027Z | MV/LV Substation BO***027Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 4.67 |  | --> | 0.19 | 0 | 0.006 | 0.177 | 0 |  | --> | C11 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8984 | -8.4449
067202Y | MV/LV Substation LO***202Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6797 | -8.636
117681X | MV/LV Substation N ***681X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.044 | 0.32 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C18 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0868 | -8.5174
0014063 | MV/LV Substation AR***4063 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.16 |  | --> | 0.598 | 0 | 0.101 | 0.5 | 0 |  | --> | C20 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2958 | -6.2273
002720 | MV/LV Substation AN***720 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.0936 | -6.2221
025443Y | MV/LV Substation KE***443Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3628 | -8.6517
081190X | MV/LV Substation HA***190X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.138 | 7.91 |  | --> | 0.19 | 0 | 0.051 | 0.144 | 0 |  | --> | C26 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3758 | -6.3571
005150 | MV/LV Substation CA***150 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.713 | -6.5028
093345Z | MV/LV Substation GR***345Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.011 | 0.357 | 0 |  | --> | C21 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4001 | -6.1531
031836 | MV/LV Substation MA***836 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2047 | -7.4983
0774154 | MV/LV Substation AN***4154 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E18 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5997 | -8.7072
065442X | MV/LV Substation CO***442X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5536 | -6.435
156965X | MV/LV Substation KN***965X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.47 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3096 | -6.9786
243130 | MV/LV Substation KE***130 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex INCH | Inch [T421,T422] | OUGHTRAGH |  | 52.2406 | -10.0063
127542 | MV/LV Substation LE***542 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =138 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6671 | -7.6735
011858Z | MV/LV Substation BR***858Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C11 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.736 | -7.1519
127316 | MV/LV Substation MI***316 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6722 | -7.7993
037028Y | MV/LV Substation ST***028Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 13.05 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C19 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8414 | -8.9079
069099 | MV/LV Substation BA***099 |  | 10 kV | _ | LV | 500 kVA :Building Structure | 0.5 | --> | 0.5 | 0.306 | 4.91 |  | --> | 0.475 | 0 | 0.062 | 0.402 | 0 |  | --> | C14 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3194 | -6.3214
0374237 | MV/LV Substation BR***4237 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 13.05 |  | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C19 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8165 | -8.8696
022770X | MV/LV Substation MA***770X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.466 | 4.55 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =576 kW | --> | C13 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1373 | -8.6412
0074052 | MV/LV Substation VO***4052 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 0.14 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C17 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3429 | -6.4853
006636 | MV/LV Substation BA***636 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E14 ex CRANE | Crane [T122] | CRANE |  | 52.5418 | -6.6804
0814083 | MV/LV Substation CH***4083 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.326 | -6.5469
016263Z | MV/LV Substation K ***263Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3073 | -6.62
099057 | MV/LV Substation QU***057 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.96 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =899 kW | --> | C15 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.954 | -7.7263
081087Z | MV/LV Substation GL***087Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.366 | -6.3779
281640X | MV/LV Substation HA***640X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =279 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =337 kW | --> | C12 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.889 | -8.492
0014009 | MV/LV Substation BR***4009 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =107 kVA | --> | 0.19 | 0 | 0.005 | 0.173 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2542 | -6.1676
368640 | MV/LV Substation NO***640 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7736 | -8.7625
1614211 | MV/LV Substation DA***4211 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.53 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex OUGHTERARD | Oughterard [T41,T42] | SCREEB |  | 53.3431 | -9.1882
064824Y | MV/LV Substation DO***824Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C20 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7013 | -6.3846
003336Y | MV/LV Substation PE***336Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.066 | 11.58 |  | --> | 0.19 | 0 | 0.061 | 0 | 0 | Constrained, otherwise capacity available =126 kW | --> | C20 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9818 | -6.0624
110184X | MV/LV Substation MU***184X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.448 | 0.76 |  | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =565 kW | --> | C16 ex KENMARE | Kenmare [T42] | KNOCKEARAGH |  | 51.8842 | -9.58
081315X | MV/LV Substation CO***315X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C14 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3374 | -6.3432
052661Z | MV/LV Substation GL***661Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.098 | 1.25 |  | --> | 0.19 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C16 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.647 | -7.2113
5904038 | MV/LV Substation NE***4038 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex CONG | Cong [T421,T422] | CLOON |  | 53.5753 | -9.2217
026482X | MV/LV Substation KI***482X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =309 kVA | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7064 | -8.521
013050 | MV/LV Substation CO***050 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.105 | 0.12 |  | --> | 0.19 | 0 | 0 | 0.177 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9963 | -6.9811
151417X | MV/LV Substation GA***417X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3729 | -8.3485
023303X | MV/LV Substation KN***303X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C18 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.1578 | -8.1809
426702 | MV/LV Substation GO***702 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1638 | -10.4119
426511 | MV/LV Substation CA***511 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.2007 | -10.3545
368728 | MV/LV Substation JE***728 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7644 | -8.7829
0584279 | MV/LV Substation BO***4279 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8148 | -8.2007
368358X | MV/LV Substation MA***358X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7643 | -8.7787
1184135 | MV/LV Substation BE***4135 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3174 | -8.2272
065763 | MV/LV Substation HY***763 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.095 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =14 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5727 | -6.2068
142670 | MV/LV Substation BR***670 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.4243 | -8.5967
064808Y | MV/LV Substation BO***808Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C14 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7919 | -6.4196
0664189 | MV/LV Substation AS***4189 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =334 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4401 | -6.1605
125965X | MV/LV Substation SL***965X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2589 | -8.259
068869 | MV/LV Substation HA***869 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.99 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3329 | -6.2633
142610 | MV/LV Substation RO***610 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.3812 | -8.5624
052992X | MV/LV Substation GO***992X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.22 |  | --> | 0.048 | 0 | 0.003 | 0.045 | 0 |  | --> | E13 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.4577 | -7.5127
426661 | MV/LV Substation CL***661 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1536 | -10.4528
030006X | MV/LV Substation CA***006X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.948 | -7.8467
158147 | MV/LV Substation SE***147 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8177 | -9.453
060494X | MV/LV Substation CO***494X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1411 | -7.2287
066395Z | MV/LV Substation RI***395Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5214 | -6.209
008388 | MV/LV Substation RA***388 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.137 | 0.2 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | E16 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2464 | -6.9173
160066Z | MV/LV Substation LA***066Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1614 | -7.5603
184210 | MV/LV Substation TU***210 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1351 | -6.7012
0554078 | MV/LV Substation SK***4078 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9233 | -7.6396
001128 | MV/LV Substation CH***128 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0.029 | 0.056 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2557 | -6.1244
066302Z | MV/LV Substation ST***302Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4284 | -6.2195
008864Y | MV/LV Substation GT***864Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.2849 | -6.9973
039565X | MV/LV Substation GO***565X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C13 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2847 | -9.0492
0634090 | MV/LV Substation HO***4090 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.2 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8129 | -6.6249
120801X | MV/LV Substation KI***801X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =18 kVA | --> | 0.048 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =26 kW | --> | E11 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.334 | -7.0685
0814093 | MV/LV Substation AN***4093 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3459 | -6.3504
167463Z | MV/LV Substation LA***463Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9815 | -8.5162
026526 | MV/LV Substation PA***526 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex KINSALE |  |  |  | 51.7306 | -8.4967
0664164 | MV/LV Substation RA***4164 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =214 kVA | --> | 0.38 | 0 | 0.068 | 0 | 0 | Constrained, otherwise capacity available =303 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4951 | -6.1367
093108 | MV/LV Substation PL***108 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =210 kVA | --> | 0.38 | 0 | 0.03 | 0.331 | 0 |  | --> | C27 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.3988 | -6.3097
255455 | MV/LV Substation SN***455 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.397 | 2.09 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6313 | -8.5961
288661 | MV/LV Substation FI***661 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2439 | -6.2017
1204395 | MV/LV Substation BR***4395 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.415 | -6.8363
082444Y | MV/LV Substation BU***444Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.01 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6448 | -6.7072
066837Z | MV/LV Substation ST***837Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.19 | 0 | 0.114 | 0.098 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4524 | -6.1839
001452 | MV/LV Substation RO***452 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 1.16 |  | --> | 0.38 | 0 | 0.14 | 0.264 | 0 |  | --> | C24 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2704 | -6.1564
022327 | MV/LV Substation MA***327 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C21 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1377 | -8.6557
051850 | MV/LV Substation GO***850 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.22 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E20 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3063 | -7.4926
026663X | MV/LV Substation SH***663X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 8.66 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7943 | -8.7873
032195Y | MV/LV Substation HI***195Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex KILMEADEN | Kilmeaden [T42] | BUTLERSTOWN |  | 52.242 | -7.2937
068781 | MV/LV Substation LA***781 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0.006 | 0.36 | 0 |  | --> | C12 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3877 | -6.2498
142606X | MV/LV Substation BA***606X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C17 ex ATHENRY |  |  |  | 53.3103 | -8.7412
067178 | MV/LV Substation JO***178 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C12 ex CORBALLY | Corbally [T41,T42] | ARDNACRUSHA |  | 52.6644 | -8.6211
0524472 | MV/LV Substation JO***4472 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C16 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.5124 | -7.3563
001091 | MV/LV Substation RE***091 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =414 kVA | --> | 0.598 | 0 | 0.121 | 0.479 | 0 |  | --> | C15 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2866 | -6.2152
066630Z | MV/LV Substation AI***630Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E17 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4487 | -6.2222
066353X | MV/LV Substation SE***353X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.068 | 0.308 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4545 | -6.1786
160033 | MV/LV Substation TO***033 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C15 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1223 | -7.3296
281963X | MV/LV Substation WO***963X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C16 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8755 | -8.5179
2094213 | MV/LV Substation IR***4213 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C16 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0668 | -7.8086
067148 | MV/LV Substation LT***148 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =638 kVA | --> | 0.95 | 0 | 0.01 | 0.5 | 0 |  | --> | C12 ex ROCHES STREET | Roches Street [T41,T42] | LIMERICK |  | 52.663 | -8.6257
014407Z | MV/LV Substation CU***407Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =127 kVA | --> | 0.19 | 0 | 0.039 | 0 | 0 | Constrained, otherwise capacity available =151 kW | --> | C17 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1646 | -6.907
249994 | MV/LV Substation CO***994 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.095 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.0903 | -8.0067
051216 | MV/LV Substation BE***216 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.22 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3362 | -7.7266
210522Y | MV/LV Substation CA***522Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9363 | -6.719
210638X | MV/LV Substation KI***638X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C17 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9672 | -6.6776
054950Y | MV/LV Substation CR***950Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =355 kW | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9481 | -7.3092
167608 | MV/LV Substation KN***608 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E12 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 52.0701 | -8.4831
210586Y | MV/LV Substation WO***586Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =353 kVA | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C21 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9708 | -6.7261
021010Y | MV/LV Substation TO***010Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9256 | -8.5938
0524253 | MV/LV Substation TY***4253 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E20 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.3866 | -7.381
127286Z | MV/LV Substation CL***286Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6287 | -7.9515
099041 | MV/LV Substation E ***041 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.17 | 2.96 |  | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C15 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9525 | -7.7327
365382 | MV/LV Substation RA***382 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.028 | 0.352 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2841 | -6.3879
039017Y | MV/LV Substation CU***017Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 11.03 |  | --> | 0.19 | 0 | 0.006 | 0.184 | 0 |  | --> | C29 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2804 | -9.0904
010023X | MV/LV Substation TH***023X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5219 | -7.1316
2934083 | MV/LV Substation PA***4083 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 0.43 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8043 | -6.7445
021120Z | MV/LV Substation BA***120Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9276 | -8.4619
167125 | MV/LV Substation BO***125 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 52.0444 | -8.5663
032431X | MV/LV Substation CA***431X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex KILMEADEN | Kilmeaden [T42] | BUTLERSTOWN |  | 52.2267 | -7.2956
167374Z | MV/LV Substation WH***374Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E16 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9782 | -8.5044
162658 | MV/LV Substation BR***658 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 7.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8505 | -7.6944
089391X | MV/LV Substation TH***391X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E18 ex MOY | Moy [T421,T422] | MOY |  | 54.115 | -9.1519
032688 | MV/LV Substation KI***688 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1669 | -7.3123
2104244 | MV/LV Substation CO***4244 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C24 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 54.0126 | -6.7346
033065Y | MV/LV Substation KI***065Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C14 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.468 | -7.2029
0444043 | MV/LV Substation RE***4043 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9826 | -9.095
009206 | MV/LV Substation LU***206 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.3985 | -7.1826
235630 | MV/LV Substation AH***630 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | E11 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8461 | -8.7884
144970 | MV/LV Substation ST***970 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.14 | 2.78 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7918 | -7.3309
0644350 | MV/LV Substation MO***4350 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6574 | -6.2792
068938 | MV/LV Substation IR***938 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.196 | 14.34 |  | --> | 0.38 | 0 | 0 | 0.351 | 0 |  | --> | C11 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3503 | -6.2072
089046 | MV/LV Substation LI***046 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 2.33 |  | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =355 kW | --> | E18 ex MOY | Moy [T421,T422] | MOY |  | 54.1204 | -9.1608
029387 | MV/LV Substation RO***387 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =466 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =576 kW | --> | C17 ex CARRIGTWOHILL |  |  |  | 51.8937 | -8.2657
252767 | MV/LV Substation AI***767 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.32 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C15 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4208 | -10.1304
365216 | MV/LV Substation SA***216 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2837 | -6.4544
071043 | MV/LV Substation AP***043 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.38 | 0 | 0.137 | 0.247 | 0 |  | --> | C15 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1466 | -6.0834
0754377 | MV/LV Substation MI***4377 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex FERNS | Ferns [T421] | CRANE |  | 52.6083 | -6.4321
0494569 | MV/LV Substation SH***4569 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8704 | -7.7163
089067X | MV/LV Substation DO***067X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.1856 | -9.1156
067117X | MV/LV Substation FO***117X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0 | 0.36 | 0 |  | --> | C16 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6188 | -8.653
162350X | MV/LV Substation WA***350X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.181 | 7.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C18 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8585 | -7.6525
210582X | MV/LV Substation LI***582X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9758 | -6.6908
016006Z | MV/LV Substation PA***006Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0.082 | 0 | 0 | Constrained, otherwise capacity available =120 kW | --> | C11 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.375 | -6.6107
0684684 | MV/LV Substation TH***4684 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3763 | -6.3277
093166Z | MV/LV Substation OW***166Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 2.86 |  | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C19 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3923 | -6.2681
281877X | MV/LV Substation AN***877X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =539 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8877 | -8.5291
012109 | MV/LV Substation BL***109 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.123 | 1.99 |  | --> | 0.19 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =156 kW | --> | C17 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8278 | -6.9292
068622X | MV/LV Substation NO***622X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =611 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3547 | -6.2653
018136 | MV/LV Substation CO***136 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.022 | 3.75 |  | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =27 kW | --> | C18 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4241 | -9.4995
265062Y | MV/LV Substation KI***062Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.015 | 0.07 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.0489 | -7.6453
345435 | MV/LV Substation CR***435 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3569 | -8.0418
032049 | MV/LV Substation CE***049 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =794 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =922 kW | --> | C16 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1612 | -7.1487
366868 | MV/LV Substation KI***868 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3257 | -9.7675
066273X | MV/LV Substation GA***273X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0.1 | 0.299 | 0 |  | --> | C20 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3955 | -6.1445
067050X | MV/LV Substation ST***050X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =293 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C17 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6683 | -8.6431
059831X | MV/LV Substation SP***831X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C22 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9972 | -7.3529
153166 | MV/LV Substation NE***166 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | E11 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7094 | -8.412
067079X | MV/LV Substation FA***079X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.049 | 0.332 | 0 |  | --> | C13 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6237 | -8.6534
068135 | MV/LV Substation NO***135 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 11.14 |  | --> | 0.95 | 0 | 0.094 | 0.5 | 0 |  | --> | C24 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3647 | -6.2752
209925X | MV/LV Substation BA***925X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1942 | -7.7278
017473 | MV/LV Substation GR***473 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.98 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4591 | -8.7647
156120X | MV/LV Substation PA***120X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 2.47 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2573 | -6.9843
249201 | MV/LV Substation LI***201 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =370 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C22 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1406 | -7.9307
025382 | MV/LV Substation BR***382 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.4261 | -8.6796
037076 | MV/LV Substation TU***076 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =331 kW | --> | C17 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8391 | -8.9842
0684101 | MV/LV Substation GR***4101 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3444 | -6.233
063739 | MV/LV Substation SM***739 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.815 | -6.5656
132026 | MV/LV Substation ES***026 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =526 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =580 kW | --> | C17 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2021 | -8.5538
068855X | MV/LV Substation JE***855X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3486 | -6.2655
365970X | MV/LV Substation ES***970X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =448 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2886 | -6.3585
011518Y | MV/LV Substation MI***518Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.037 | 0.04 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C11 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5433 | -7.384
014919 | MV/LV Substation HA***919 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.124 | 0.63 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E12 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0965 | -6.7705
068159X | MV/LV Substation NO***159X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3496 | -6.2725
0684733 | MV/LV Substation FO***4733 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.351 | -6.232
099190X | MV/LV Substation GL***190X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 2.96 |  | --> | 0.095 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =74 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9594 | -7.6895
0684481 | MV/LV Substation PE***4481 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.38 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3343 | -6.2467
093309X | MV/LV Substation RO***309X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.012 | 0.363 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3861 | -6.1416
248701X | MV/LV Substation KN***701X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 3.5 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E13 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.3858 | -6.7854
118632Y | MV/LV Substation RO***632Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E11 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.456 | -8.1448
062618Y | MV/LV Substation MA***618Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.219 | 5.69 |  | --> | 0.38 | 0 | 0.061 | 0 | 0 | Constrained, otherwise capacity available =312 kW | --> | C11 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.991 | -6.3999
125825 | MV/LV Substation BA***825 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2351 | -8.3625
039381X | MV/LV Substation GA***381X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0.115 | 0 | 0 | Constrained, otherwise capacity available =292 kW | --> | C22 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2819 | -8.923
139036Y | MV/LV Substation SL***036Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 2.68 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7852 | -7.1334
150921 | MV/LV Substation ST***921 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 3.96 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E21 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8031 | -7.7677
0934093 | MV/LV Substation CA***4093 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4088 | -6.1795
053457 | MV/LV Substation AN***457 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E20 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2551 | -7.3806
118039Y | MV/LV Substation PU***039Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.2901 | -8.1528
288243X | MV/LV Substation BE***243X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.384 | 1.16 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2772 | -6.2154
022115 | MV/LV Substation CA***115 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C15 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1213 | -8.6474
149054X | MV/LV Substation IR***054X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.7088 | -7.9745
0684559 | MV/LV Substation AR***4559 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3476 | -6.2702
127921Y | MV/LV Substation WA***921Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 5.89 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C17 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5113 | -7.8807
023434 | MV/LV Substation BA***434 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1626 | -8.3943
281117Y | MV/LV Substation TH***117Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =283 kVA | --> | 0.38 | 0 | 0.066 | 0.315 | 0 |  | --> | C22 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.876 | -8.5286
082792Y | MV/LV Substation MU***792Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.283 | 2.01 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6437 | -6.7106
0664021 | MV/LV Substation WI***4021 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5304 | -6.2362
084217X | MV/LV Substation DU***217X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1151 | -9.0693
249118 | MV/LV Substation FL***118 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1345 | -7.9288
081201Y | MV/LV Substation NE***201Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3479 | -6.508
249384Z | MV/LV Substation HE***384Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C25 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1319 | -7.754
066284Z | MV/LV Substation WO***284Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5232 | -6.2115
157216 | MV/LV Substation DR***216 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.0287 | -7.6826
070854 | MV/LV Substation BA***854 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0609 | -9.1301
132687 | MV/LV Substation WO***687 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 1.62 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C16 ex CURRA | Curra [T41] | SOMERSET |  | 53.0533 | -8.4016
1104053 | MV/LV Substation KE***4053 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 0.76 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C16 ex KENMARE | Kenmare [T42] | KNOCKEARAGH |  | 51.8882 | -9.5818
043446X | MV/LV Substation SE***446X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9292 | -9.1139
120176Y | MV/LV Substation RE***176Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =141 kVA | --> | 0.19 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | E11 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3394 | -7.0738
066744Z | MV/LV Substation EL***744Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5321 | -6.2534
065309Z | MV/LV Substation M1***309Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5731 | -6.209
164223X | MV/LV Substation FL***223X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5513 | -9.2739
0524191 | MV/LV Substation FR***4191 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.346 | 10.9 |  | --> | 0.38 | 0 | 0.08 | 0.313 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6293 | -7.3917
009690 | MV/LV Substation HO***690 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.3629 | -7.1732
075856 | MV/LV Substation NO***856 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex FERNS | Ferns [T421] | CRANE |  | 52.6123 | -6.4169
253185Y | MV/LV Substation FL***185Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.587 | -8.7746
243112 | MV/LV Substation AU***112 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex INCH | Inch [T421,T422] | OUGHTRAGH |  | 52.2386 | -9.9737
062188 | MV/LV Substation GR***188 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.251 | 3.12 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C11 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.99 | -6.3803
365146 | MV/LV Substation CI***146 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =777 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2819 | -6.4222
288896 | MV/LV Substation GL***896 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.249 | -6.3001
117472Y | MV/LV Substation MA***472Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E22 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1998 | -8.4381
156059 | MV/LV Substation MC***059 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.47 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2498 | -6.9758
055496X | MV/LV Substation TR***496X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex RATHDOWNEY | Rathdowney [T42] | IKERRIN |  | 52.854 | -7.6703
071827 | MV/LV Substation AS***827 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1496 | -6.1252
350018X | MV/LV Substation MC***018X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4436 | -8.3076
0054156 | MV/LV Substation KN***4156 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.394 | 3.03 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C17 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6672 | -6.29
0954196 | MV/LV Substation DO***4196 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C26 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.7363 | -9.539
023029Y | MV/LV Substation AN***029Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1446 | -8.2615
071084 | MV/LV Substation KI***084 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 5.58 |  | --> | 0.19 | 0 | 0.034 | 0.158 | 0 |  | --> | C13 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1013 | -6.085
056423X | MV/LV Substation AN***423X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 0.89 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C21 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0745 | -7.8922
071962 | MV/LV Substation TE***962 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1555 | -6.0968
0214325 | MV/LV Substation GO***4325 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.946 | -8.6499
111109X | MV/LV Substation DR***109X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.7014 | -9.3966
068264 | MV/LV Substation CO***264 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C03 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3455 | -6.2568
068051X | MV/LV Substation PA***051X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =562 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3507 | -6.2675
253694Z | MV/LV Substation WI***694Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6747 | -8.5842
2814380 | MV/LV Substation BA***4380 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =514 kVA | --> | 0.598 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C17 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8645 | -8.4305
019399X | MV/LV Substation ED***399X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =269 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2693 | -9.6955
0104164 | MV/LV Substation ST***4164 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5352 | -7.2235
042553 | MV/LV Substation FA***553 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =115 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | E17 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8024 | -9.1291
158149 | MV/LV Substation MU***149 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8002 | -9.408
068448 | MV/LV Substation ST***448 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.189 | 28.43 |  | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C04 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3422 | -6.2623
068026 | MV/LV Substation CI***026 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.295 | 28.43 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C10 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3437 | -6.267
1424277 | MV/LV Substation AU***4277 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E23 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.3084 | -8.4761
051512 | MV/LV Substation CH***512 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.22 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3463 | -7.6187
0554128 | MV/LV Substation DE***4128 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9228 | -7.7453
012122 | MV/LV Substation GR***122 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C23 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8259 | -6.9322
0814173 | MV/LV Substation SH***4173 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0.162 | 0.245 | 0 |  | --> | E20 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3466 | -6.4678
243146X | MV/LV Substation GR***146X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1426 | -10.1429
055619 | MV/LV Substation CL***619 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E22 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 53.0033 | -7.8736
043146X | MV/LV Substation HA***146X |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.429 | 0.43 | Constrained, otherwise capacity available =907 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =937 kW | --> | C20 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.8606 | -8.8495
293400 | MV/LV Substation GR***400 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =9 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9985 | -6.7425
130141X | MV/LV Substation FA***141X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6661 | -7.5341
017107X | MV/LV Substation DO***107X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 7.48 |  | --> | 0.19 | 0 | 0.15 | 0 | 0 | Constrained, otherwise capacity available =71 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.4565 | -9.0814
176481Y | MV/LV Substation CL***481Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 18.78 |  | --> | 0.048 | 0 | 0.006 | 0.042 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9085 | -9.142
069333 | MV/LV Substation ST***333 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.127 | 0.91 |  | --> | 0.38 | 0 | 0.035 | 0.315 | 0 |  | --> | C18 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3168 | -6.2941
255270X | MV/LV Substation TO***270X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.09 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6251 | -8.5994
066872X | MV/LV Substation BL***872X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5032 | -6.1931
119303Y | MV/LV Substation TO***303Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.16 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C20 ex NEWMARKET (SR) | Newmarket (sr) [T41,T42] | GLENLARA |  | 52.2756 | -9.0635
210453 | MV/LV Substation KN***453 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.031 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C19 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.95 | -6.7713
054941Y | MV/LV Substation BE***941Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 52.899 | -7.2093
068018 | MV/LV Substation CH***018 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.483 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3434 | -6.2698
0254237 | MV/LV Substation HA***4237 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.116 | 1.93 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C17 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.3437 | -8.9042
012520X | MV/LV Substation BA***520X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.043 | 2.83 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | E17 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7379 | -6.9852
032394 | MV/LV Substation CO***394 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.19 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =146 kW | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1512 | -7.0061
050102X | MV/LV Substation CR***102X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.378 | -7.9999
052415 | MV/LV Substation MU***415 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.131 | 10.9 |  | --> | 0.19 | 0 | 0 | 0.18 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6252 | -7.389
090904 | MV/LV Substation DE***904 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7124 | -8.933
064341Z | MV/LV Substation AN***341Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6689 | -6.28
031073 | MV/LV Substation BA***073 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.1747 | -7.3908
0824381 | MV/LV Substation AE***4381 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 2.01 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6698 | -6.6868
182698X | MV/LV Substation MU***698X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex TULLA | Tulla [T41,T42] | ENNIS |  | 52.7899 | -8.6171
153233 | MV/LV Substation WO***233 |  | 20 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.031 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =27 kW | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7068 | -8.4837
009200Y | MV/LV Substation SU***200Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.356 | 0.53 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =569 kW | --> | C20 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2468 | -7.1215
093013Z | MV/LV Substation BE***013Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.06 | 5.82 |  | --> | 0.38 | 0 | 0 | 0.331 | 0 |  | --> | C21 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3943 | -6.1964
023078 | MV/LV Substation BE***078 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1456 | -8.2703
365561X | MV/LV Substation MA***561X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0.004 | 0.18 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2978 | -6.3641
059725 | MV/LV Substation BE***725 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9356 | -7.4058
034071 | MV/LV Substation GA***071 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.294 | 0.95 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C16 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3524 | -7.6943
164102 | MV/LV Substation SH***102 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5701 | -9.1993
017040 | MV/LV Substation CH***040 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.204 | 4.23 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | C17 ex CHURCHTOWN | Churchtown [T41] | RATHKEALE |  | 52.4532 | -9.0625
2434028 | MV/LV Substation GA***4028 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1434 | -10.1383
233799 | MV/LV Substation SC***799 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C21 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.1807 | -9.4072
019131X | MV/LV Substation BR***131X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.047 | 0.05 | Constrained, otherwise capacity available =594 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C14 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2737 | -9.6739
082459Y | MV/LV Substation BA***459Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6237 | -6.6889
176357 | MV/LV Substation KI***357 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 18.78 |  | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9002 | -9.0833
0824098 | MV/LV Substation IV***4098 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7511 | -6.5644
324547X | MV/LV Substation CA***547X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.5154 | -8.3415
293303Y | MV/LV Substation BA***303Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9323 | -6.6944
156097Z | MV/LV Substation WE***097Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.47 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =940 kW | --> | E21 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2493 | -6.9696
137797 | MV/LV Substation BA***797 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 3.74 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3792 | -9.6045
034688 | MV/LV Substation LO***688 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.317 | 5.88 |  | --> | 0.38 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C11 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.369 | -7.7098
156136 | MV/LV Substation MU***136 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.47 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C18 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2468 | -6.9828
009974X | MV/LV Substation TH***974X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.2 | 0.53 |  | --> | 0.38 | 0 | 0.075 | 0 | 0 | Constrained, otherwise capacity available =296 kW | --> | C20 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2486 | -7.1186
093368Z | MV/LV Substation NO***368Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C33 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.401 | -6.257
009925Y | MV/LV Substation MO***925Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.95 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2624 | -7.1435
025218Y | MV/LV Substation ME***218Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3272 | -8.6783
066436Z | MV/LV Substation DU***436Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5261 | -6.1782
019124X | MV/LV Substation CO***124X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 1.54 |  | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C17 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2563 | -9.6913
0194008 | MV/LV Substation MI***4008 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.311 | 1.54 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2487 | -9.6771
034305Y | MV/LV Substation AR***305Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.263 | 0.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3752 | -7.7238
005220 | MV/LV Substation GO***220 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =16 kVA | --> | 0.048 | 0 | 0.047 | 0 | 0 | Constrained, otherwise capacity available =8 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6841 | -6.2732
003653 | MV/LV Substation BA***653 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 11.58 |  | --> | 0.38 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0053 | -6.1055
210847Y | MV/LV Substation AN***847Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9716 | -6.6815
009629X | MV/LV Substation PO***629X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 0.53 |  | --> | 0.19 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2473 | -7.0708
001339 | MV/LV Substation AR***339 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 15.18 |  | --> | 0.95 | 0 | 0.089 | 0.5 | 0 |  | --> | C21 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2899 | -6.2015
075164Y | MV/LV Substation CO***164Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 1.13 |  | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | E22 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6826 | -6.6842
042086Y | MV/LV Substation BR***086Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =402 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =558 kW | --> | E16 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8474 | -9.2798
046136 | MV/LV Substation GL***136 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 4.13 |  | --> | 0.095 | 0 | 0.014 | 0.081 | 0 |  | --> | C18 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.396 | -8.5284
053665Y | MV/LV Substation RA***665Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.01 | 0.038 | 0 |  | --> | E20 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.3788 | -7.347
365296 | MV/LV Substation GO***296 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.19 | 0 | 0 | 0.175 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2526 | -6.5373
1254089 | MV/LV Substation TU***4089 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2446 | -8.2633
023042 | MV/LV Substation GO***042 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =138 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1842 | -8.3552
075377Y | MV/LV Substation BU***377Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6532 | -6.6486
127878Y | MV/LV Substation AB***878Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C16 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6349 | -7.8649
075566Y | MV/LV Substation BL***566Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 1.13 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E12 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6614 | -6.6639
059443X | MV/LV Substation LO***443X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E17 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.014 | -7.3737
093167 | MV/LV Substation SE***167 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =861 kVA | --> | 0.95 | 0 | 0.04 | 0.5 | 0 |  | --> | C27 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4011 | -6.3065
132132Y | MV/LV Substation ED***132Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C17 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2048 | -8.5596
139212Z | MV/LV Substation WO***212Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7683 | -7.1361
066841X | MV/LV Substation AG***841X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5074 | -6.185
2604006 | MV/LV Substation SK***4006 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.67 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | E13 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.9218 | -9.4922
0234082 | MV/LV Substation AL***4082 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1463 | -8.2767
0684312 | MV/LV Substation OR***4312 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.347 | -6.2644
125190Y | MV/LV Substation BA***190Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2501 | -8.2727
281184Z | MV/LV Substation LI***184Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.326 | 5.49 |  | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C12 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8851 | -8.4625
156055 | MV/LV Substation CO***055 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.308 | 2.47 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C18 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2502 | -6.9748
082405Y | MV/LV Substation AR***405Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7366 | -6.5868
024036 | MV/LV Substation RO***036 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2482 | -8.5968
005967 | MV/LV Substation CO***967 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 17.8 |  | --> | 0.095 | 0 | 0.01 | 0.085 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6544 | -6.2365
137335 | MV/LV Substation BA***335 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.74 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3748 | -9.613
111078Z | MV/LV Substation MI***078Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C12 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6785 | -9.435
064654Y | MV/LV Substation CA***654Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =228 kVA | --> | 0.38 | 0 | 0.057 | 0 | 0 | Constrained, otherwise capacity available =314 kW | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7285 | -6.3482
152234 | MV/LV Substation MO***234 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E33 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.5583 | -8.3479
365792X | MV/LV Substation TH***792X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =11 kVA | --> | 0.048 | 0 | 0 | 0.042 | 0 |  | --> | C21 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.273 | -6.3604
153234 | MV/LV Substation WO***234 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7077 | -8.4853
008521Y | MV/LV Substation CL***521Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex CLONROCHE | Clonroche [T421,T422] | WEXFORD |  | 52.4435 | -6.8015
0154090 | MV/LV Substation EP***4090 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.329 | 12.6 |  | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C20 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2408 | -6.6326
156450X | MV/LV Substation BO***450X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 2.47 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2776 | -7.0766
010392X | MV/LV Substation MA***392X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5308 | -7.1364
0674285 | MV/LV Substation AM***4285 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.354 | 13.8 |  | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C21 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6568 | -8.5845
255892 | MV/LV Substation KI***892 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.09 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6226 | -8.606
081645Z | MV/LV Substation AD***645Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.109 | 0.288 | 0 |  | --> | E20 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3389 | -6.469
042935X | MV/LV Substation CH***935X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | E17 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8102 | -9.1392
050444 | MV/LV Substation MI***444 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4587 | -8.0719
2814023 | MV/LV Substation CA***4023 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C24 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8162 | -8.4052
009089Y | MV/LV Substation KI***089Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.116 | 0.53 |  | --> | 0.19 | 0 | 0.071 | 0 | 0 | Constrained, otherwise capacity available =126 kW | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2515 | -7.0714
006024 | MV/LV Substation MU***024 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.207 | 3.12 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.4955 | -6.572
281497X | MV/LV Substation OW***497X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C15 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8162 | -8.3994
089398X | MV/LV Substation GE***398X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | E17 ex MOY | Moy [T421,T422] | MOY |  | 54.1156 | -9.1575
281210Y | MV/LV Substation CE***210Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8196 | -8.3814
067252Y | MV/LV Substation CL***252Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C17 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.7267 | -8.5507
238007 | MV/LV Substation SE***007 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6224 | -9.2306
067008 | MV/LV Substation PU***008 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =393 kVA | --> | 0.598 | 0 | 0.066 | 0.5 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6501 | -8.6354
069300 | MV/LV Substation CA***300 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.395 | 4.91 |  | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C14 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3179 | -6.3084
281678 | MV/LV Substation RI***678 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.38 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =307 kW | --> | C15 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.7717 | -8.495
0674282 | MV/LV Substation SY***4282 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6464 | -8.6251
248718X | MV/LV Substation CH***718X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3919 | -6.6693
036241X | MV/LV Substation GO***241X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5168 | -8.1848
160045Z | MV/LV Substation BR***045Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.2162 | -7.1421
066265X | MV/LV Substation MA***265X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =203 kVA | --> | 0.38 | 0 | 0.083 | 0 | 0 | Constrained, otherwise capacity available =291 kW | --> | C16 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4348 | -6.134
068350 | MV/LV Substation AN***350 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.365 | 11.14 |  | --> | 0.598 | 0 | 0.043 | 0.5 | 0 |  | --> | C24 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3606 | -6.2868
117011Y | MV/LV Substation CA***011Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 5.78 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C14 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2272 | -8.4925
293452Z | MV/LV Substation TO***452Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9938 | -6.6503
288011X | MV/LV Substation BR***011X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0.01 | 0.362 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2675 | -6.2642
022802X | MV/LV Substation CL***802X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 4.55 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C21 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1521 | -8.6292
008336Z | MV/LV Substation BR***336Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C18 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3856 | -6.9393
012916X | MV/LV Substation AR***916X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 2.83 |  | --> | 0.38 | 0 | 0.112 | 0 | 0 | Constrained, otherwise capacity available =282 kW | --> | E17 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7421 | -6.9748
068625X | MV/LV Substation VI***625X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex WATLING STREET | Watling Street [T41,T42] | FRANCIS STREET |  | 53.3497 | -6.282
238592X | MV/LV Substation MC***592X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.5823 | -9.1219
237611 | MV/LV Substation BU***611 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8666 | -6.3958
008013Z | MV/LV Substation GR***013Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =112 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C18 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.387 | -6.9394
117446 | MV/LV Substation TA***446 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 5.78 |  | --> | 0.19 | 0 | 0.005 | 0.182 | 0 |  | --> | C14 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2134 | -8.5039
050067Z | MV/LV Substation BO***067Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.61 |  | --> | 0.598 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4223 | -7.9215
052902Z | MV/LV Substation DE***902Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 10.9 |  | --> | 0.095 | 0 | 0.009 | 0.083 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6226 | -7.396
0684165 | MV/LV Substation BR***4165 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.371 | 11.14 |  | --> | 0.598 | 0 | 0.017 | 0.5 | 0 |  | --> | C24 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3725 | -6.3001
051367X | MV/LV Substation RE***367X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.057 | 2.22 |  | --> | 0.095 | 0 | 0.005 | 0.085 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3456 | -7.594
003434Y | MV/LV Substation RA***434Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 11.58 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C14 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9966 | -6.0878
068020X | MV/LV Substation AS***020X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.427 | 9.02 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3466 | -6.2541
064873 | MV/LV Substation TU***873 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7367 | -6.4273
048480 | MV/LV Substation RA***480 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.183 | 2.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.8619 | -7.916
156744Y | MV/LV Substation TY***744Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3002 | -7.1227
082169 | MV/LV Substation NA***169 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C28 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6472 | -6.6877
2814344 | MV/LV Substation HA***4344 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =546 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C16 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8728 | -8.3522
082687Y | MV/LV Substation EN***687Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =501 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C32 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6451 | -6.6841
109108 | MV/LV Substation FA***108 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =296 kVA | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C22 ex SHANNON | Shannon [T41,T42] | DRUMLINE |  | 52.7066 | -8.8942
011993X | MV/LV Substation RE***993X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6331 | -7.0597
099580 | MV/LV Substation GO***580 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 2.96 |  | --> | 0.095 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9638 | -7.6862
001682 | MV/LV Substation CO***682 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.233 | 1.23 |  | --> | 0.38 | 0 | 0.027 | 0.336 | 0 |  | --> | C19 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2868 | -6.1318
093521Z | MV/LV Substation PA***521Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C20 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.3979 | -6.2884
049258Z | MV/LV Substation SI***258Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.133 | 0.21 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E19 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.6959 | -7.8075
207446X | MV/LV Substation AR***446X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.717 | -7.5793
042506X | MV/LV Substation MU***506X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8051 | -9.2272
084907 | MV/LV Substation JA***907 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1551 | -9.0673
151409X | MV/LV Substation KN***409X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.042 | 0 | 0 | Constrained, otherwise capacity available =150 kW | --> | C25 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.4378 | -8.4108
039440X | MV/LV Substation TA***440X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C12 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2678 | -9.0422
154013Z | MV/LV Substation RU***013Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.19 | 0 | 0.017 | 0.163 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3992 | -6.4208
293857X | MV/LV Substation CR***857X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9001 | -6.5829
016061Z | MV/LV Substation U ***061Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3402 | -6.5226
365629X | MV/LV Substation GR***629X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =242 kVA | --> | 0.38 | 0 | 0.03 | 0.336 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2938 | -6.3475
001257 | MV/LV Substation DU***257 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.46 | 1.23 |  | --> | 0.598 | 0 | 0.037 | 0.5 | 0 |  | --> | C16 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2792 | -6.1343
026771Y | MV/LV Substation ET***771Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.71 | -8.5151
365510X | MV/LV Substation CH***510X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.021 | 0.348 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3193 | -6.4098
136454Y | MV/LV Substation CL***454Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =584 kVA | --> | 0.598 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C12 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6364 | -8.1755
039345X | MV/LV Substation HY***345X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.316 | 3.45 |  | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C17 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2713 | -9.0511
068267 | MV/LV Substation BR***267 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.159 | 11.14 |  | --> | 0.598 | 0 | 0.027 | 0.5 | 0 |  | --> | C11 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3672 | -6.3017
0524019 | MV/LV Substation CI***4019 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.306 | 10.9 |  | --> | 0.38 | 0 | 0.04 | 0.337 | 0 |  | --> | C12 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5232 | -7.3413
265764X | MV/LV Substation HE***764X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.066 | 0.07 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E17 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1174 | -7.5839
052121Z | MV/LV Substation GR***121Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 10.9 |  | --> | 0.598 | 0 | 0.018 | 0.5 | 0 |  | --> | C12 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5208 | -7.3397
017214X | MV/LV Substation NA***214X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.398 | 4.23 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex CHURCHTOWN | Churchtown [T41] | RATHKEALE |  | 52.4515 | -9.0633
0014062 | MV/LV Substation PR***4062 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.16 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2705 | -6.2053
082331 | MV/LV Substation WH***331 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 1.82 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C15 ex RANDALSTOWN | Randalstown [T41] | NAVAN |  | 53.6748 | -6.7588
0504211 | MV/LV Substation CL***4211 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.5378 | -7.8155
0684212 | MV/LV Substation RA***4212 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =872 kVA | --> | 0.95 | 0 | 0.141 | 0.5 | 0 |  | --> | C23 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3564 | -6.2775
062015Z | MV/LV Substation CA***015Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.314 | 3.12 |  | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C12 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9808 | -6.3958
1394131 | MV/LV Substation CA***4131 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8239 | -7.1846
2494113 | MV/LV Substation BA***4113 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1089 | -7.7742
0684179 | MV/LV Substation MO***4179 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3586 | -6.2731
052749Z | MV/LV Substation AN***749Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.349 | 10.9 |  | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C19 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5248 | -7.3382
0844100 | MV/LV Substation KI***4100 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1771 | -8.8361
365079X | MV/LV Substation NE***079X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =411 kVA | --> | 0.598 | 0 | 0.029 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3139 | -6.3897
0594229 | MV/LV Substation TR***4229 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0791 | -7.2612
366692 | MV/LV Substation SE***692 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3291 | -9.7333
039640X | MV/LV Substation FE***640X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2717 | -9.1009
019144 | MV/LV Substation CL***144 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.315 | 2.18 |  | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2791 | -9.7077
365198 | MV/LV Substation VO***198 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2686 | -6.3936
081319Z | MV/LV Substation MI***319Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =583 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3621 | -6.4434
052048 | MV/LV Substation ST***048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =263 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5149 | -7.3356
111354Z | MV/LV Substation DE***354Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex BALLYDEHOB | Ballydehob [T421] | DUNMANWAY |  | 51.549 | -9.4946
021309X | MV/LV Substation CL***309X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9221 | -8.6432
350434 | MV/LV Substation BU***434 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4434 | -8.4239
0934080 | MV/LV Substation HO***4080 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =935 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.4152 | -6.2893
0654143 | MV/LV Substation KE***4143 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C18 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5258 | -6.099
277061 | MV/LV Substation MA***061 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =381 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3994 | -6.1932
068505 | MV/LV Substation CR***505 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =518 kVA | --> | 0.598 | 0 | 0.053 | 0.5 | 0 |  | --> | C11 ex CLONTARF | Clontarf [T42] | FINGLAS |  | 53.3769 | -6.2086
132102Y | MV/LV Substation DA***102Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C17 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.205 | -8.5576
288775 | MV/LV Substation AN***775 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.04 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2096 | -6.1713
013546 | MV/LV Substation MO***546 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9067 | -6.9681
220005 | MV/LV Substation PU***005 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.044 | 1.36 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C11 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.0989 | -9.3294
031559X | MV/LV Substation KI***559X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2284 | -7.4438
253067Y | MV/LV Substation CL***067Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.5617 | -8.6527
139061Z | MV/LV Substation CL***061Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.9108 | -7.1634
164449X | MV/LV Substation FI***449X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =477 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5485 | -9.2672
137205 | MV/LV Substation HE***205 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.455 | -9.6783
1964129 | MV/LV Substation KI***4129 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.34 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5256 | -6.8779
081564Z | MV/LV Substation BA***564Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =384 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3411 | -6.3583
066258Z | MV/LV Substation BO***258Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | E17 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4471 | -6.2351
136701 | MV/LV Substation KI***701 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C22 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6406 | -8.1569
266443 | MV/LV Substation PO***443 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E17 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3194 | -7.1763
011619 | MV/LV Substation BE***619 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 2.8 |  | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C12 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.5906 | -7.1843
021288Z | MV/LV Substation EA***288Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.274 | 6.78 |  | --> | 0.38 | 0 | 0 | 0.362 | 0 |  | --> | C35 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9047 | -8.3638
093218X | MV/LV Substation BE***218X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =506 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C11 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3948 | -6.1479
0814024 | MV/LV Substation AR***4024 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3261 | -6.5791
157029X | MV/LV Substation BR***029X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.55 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E17 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 53.9723 | -7.6968
149918 | MV/LV Substation R/***918 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6467 | -8.1434
0054026 | MV/LV Substation CL***4026 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C14 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6792 | -6.2881
075685X | MV/LV Substation JO***685X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.13 |  | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E22 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6927 | -6.6408
053825Y | MV/LV Substation SW***825Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.28 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C23 ex SRAH | Srah [T43] | THORNSBERRY |  | 53.2948 | -7.4935
052998Z | MV/LV Substation BA***998Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.398 | 10.9 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C25 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5802 | -7.5261
184177 | MV/LV Substation GL***177 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.346 | 3.38 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C13 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1213 | -6.7394
154336 | MV/LV Substation LE***336 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.246 | 7.91 |  | --> | 0.38 | 0 | 0 | 0.358 | 0 |  | --> | C26 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3838 | -6.3646
065296Z | MV/LV Substation EU***296Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5221 | -6.0961
249016 | MV/LV Substation ST***016 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1295 | -7.9315
0254376 | MV/LV Substation CO***4376 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.05 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.369 | -8.9856
365214X | MV/LV Substation CH***214X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.024 | 0.345 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3199 | -6.4076
216035X | MV/LV Substation KI***035X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C26 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.8262 | -8.4363
016047Z | MV/LV Substation LU***047Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =244 kVA | --> | 0.38 | 0 | 0.053 | 0.319 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4241 | -6.4798
0634158 | MV/LV Substation ME***4158 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C19 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.8545 | -6.5509
008948Y | MV/LV Substation GL***948Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.239 | 0.24 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C15 ex ROSBERCON | Rosbercon [T41,T42] | WATERFORD |  | 52.3955 | -6.9542
036034X | MV/LV Substation GR***034X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E20 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.559 | -8.0462
066497 | MV/LV Substation BU***497 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5072 | -6.1218
209575X | MV/LV Substation MU***575X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0798 | -7.6873
005058 | MV/LV Substation TA***058 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 17.8 |  | --> | 0.19 | 0 | 0 | 0.185 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6709 | -6.225
036055 | MV/LV Substation CA***055 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4773 | -8.1506
365119X | MV/LV Substation MC***119X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =478 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3299 | -6.3536
066020Y | MV/LV Substation MA***020Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4317 | -6.1434
2884172 | MV/LV Substation WO***4172 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.041 | 0.04 | Constrained, otherwise capacity available =628 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2178 | -6.1156
036608X | MV/LV Substation CL***608X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E33 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.5387 | -8.2808
066115Y | MV/LV Substation CO***115Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.477 | -6.5015
0054233 | MV/LV Substation CA***4233 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =333 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7099 | -6.4837
059621Y | MV/LV Substation TH***621Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C15 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9909 | -7.3684
122894 | MV/LV Substation MO***894 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 4.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8806 | -6.6824
046070 | MV/LV Substation O ***070 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2713 | -8.4764
081043X | MV/LV Substation KI***043X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C12 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3586 | -6.3857
0654064 | MV/LV Substation BR***4064 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5358 | -6.09
038586X | MV/LV Substation BA***586X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex GORT | Gort [T41,T42] | ENNIS |  | 53.1288 | -8.7988
023566Y | MV/LV Substation CA***566Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex CURRAGLASS | Curraglass [T41] | BARRYMORE |  | 52.0994 | -8.1222
365146Y | MV/LV Substation NE***146Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3138 | -6.3917
365111X | MV/LV Substation S.***111X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =529 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3179 | -6.381
0994091 | MV/LV Substation MV***4091 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.45 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | C19 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9653 | -7.7179
368743 | MV/LV Substation DE***743 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =23 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.76 | -8.75
2524033 | MV/LV Substation LE***4033 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 1.32 |  | --> | 0.048 | 0 | 0.006 | 0.04 | 0 |  | --> | C24 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.5541 | -9.9437
365145Y | MV/LV Substation CI***145Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =313 kVA | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.329 | -6.3461
149164X | MV/LV Substation CA***164X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6476 | -8.1962
109019 | MV/LV Substation 24***019 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.198 | 0.38 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C22 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7099 | -8.9147
0674305 | MV/LV Substation NE***4305 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C21 ex CASTLETROY | Castletroy [T41,T42] | ARDNACRUSHA |  | 52.6608 | -8.5484
2564082 | MV/LV Substation DE***4082 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.28 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.8197 | -8.41
151117X | MV/LV Substation KN***117X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6029 | -8.4358
293792Y | MV/LV Substation AL***792Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =149 kVA | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9339 | -6.6925
006442X | MV/LV Substation GO***442X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.12 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.4945 | -6.5927
0074199 | MV/LV Substation SI***4199 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.304 | -6.4636
249950 | MV/LV Substation DE***950 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1269 | -7.8971
039434X | MV/LV Substation RA***434X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2725 | -9.0846
062048Z | MV/LV Substation AR***048Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.39 | 0.72 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C12 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0067 | -6.3837
065311Z | MV/LV Substation HA***311Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =139 kVA | --> | 0.19 | 0 | 0.017 | 0.169 | 0 |  | --> | C21 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6134 | -6.197
368817 | MV/LV Substation LA***817 |  | 20 kV | _ | LV | 150 kVA :Pole Substation | 0.15 | --> | 0.15 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.142 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =142 kW | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6982 | -8.7622
064411Z | MV/LV Substation BA***411Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C20 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7387 | -6.2669
065467Z | MV/LV Substation SE***467Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0.116 | 0 | 0 | Constrained, otherwise capacity available =286 kW | --> | C18 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5265 | -6.1045
021532Z | MV/LV Substation EA***532Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.304 | 6.78 |  | --> | 0.38 | 0 | 0.01 | 0.359 | 0 |  | --> | C35 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9032 | -8.3685
0584301 | MV/LV Substation GA***4301 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 53.0125 | -8.2177
018356 | MV/LV Substation KN***356 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 3.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C18 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4341 | -9.4599
021252Z | MV/LV Substation ID***252Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9229 | -8.468
037545X | MV/LV Substation MI***545X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.457 | 13.05 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8446 | -8.9882
049073Z | MV/LV Substation YO***073Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.6935 | -7.8199
365229X | MV/LV Substation KI***229X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0.016 | 0.344 | 0 |  | --> | C17 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2923 | -6.3925
068489X | MV/LV Substation HA***489X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3479 | -6.2798
011014 | MV/LV Substation BE***014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 5.05 |  | --> | 0.38 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C13 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6636 | -7.2371
043107 | MV/LV Substation KI***107 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C20 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.937 | -8.9195
158485 | MV/LV Substation CL***485 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.83 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.7617 | -9.4685
209092X | MV/LV Substation HY***092X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =559 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.2623 | -7.6917
2074099 | MV/LV Substation DO***4099 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.743 | -7.5333
0414005 | MV/LV Substation GA***4005 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6476 | -9.0206
590901X | MV/LV Substation MC***901X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex CONG |  |  |  | 53.5453 | -9.2913
021742Z | MV/LV Substation EU***742Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9057 | -8.3502
008686Y | MV/LV Substation KN***686Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4045 | -6.935
214097 | MV/LV Substation KI***097 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7848 | -9.2149
3774156 | MV/LV Substation BR***4156 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8382 | -10.2619
060878X | MV/LV Substation BA***878X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 2.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C19 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0586 | -6.9881
021609X | MV/LV Substation WA***609X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =70 kW | --> | E11 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9025 | -8.6687
058277 | MV/LV Substation BA***277 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C25 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8672 | -8.0952
068102 | MV/LV Substation HE***102 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3519 | -6.2713
182049X | MV/LV Substation MT***049X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9317 | -8.4359
127924X | MV/LV Substation MO***924X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C16 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.735 | -7.7124
026148Z | MV/LV Substation TH***148Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | E41 ex KINSALE | Kinsale [T423] | TRABEG |  | 51.7022 | -8.5293
039874X | MV/LV Substation HI***874X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 11.03 |  | --> | 0.19 | 0 | 0.034 | 0.157 | 0 |  | --> | C13 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2708 | -9.0765
026611Y | MV/LV Substation KI***611Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7071 | -8.4937
068744 | MV/LV Substation CH***744 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C47 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.344 | -6.2608
122737 | MV/LV Substation FE***737 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.18 |  | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C17 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9046 | -6.7015
093015Z | MV/LV Substation TO***015Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.19 | 0 | 0 | 0.172 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4024 | -6.1788
036084 | MV/LV Substation EM***084 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 1.4 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | E17 ex KILROSS ROAD | Kilross Road [T421] | TIPPERARY |  | 52.4642 | -8.3535
031262Y | MV/LV Substation CR***262Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2007 | -7.4255
365727X | MV/LV Substation BE***727X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.219 | 13.91 |  | --> | 0.38 | 0 | 0.037 | 0.327 | 0 |  | --> | C23 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2932 | -6.3889
118534 | MV/LV Substation PL***534 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.4725 | -8.5109
093492Z | MV/LV Substation ST***492Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =628 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4041 | -6.15
005981X | MV/LV Substation PO***981X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.372 | 17.8 |  | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6193 | -6.2272
066448Z | MV/LV Substation HA***448Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4864 | -6.2715
207693 | MV/LV Substation BA***693 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 2.9 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex GLENGOOLE | Glengoole [T42] | THURLES |  | 52.5901 | -7.6682
192819 | MV/LV Substation RT***819 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C15 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0682 | -8.2933
119804X | MV/LV Substation RA***804X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.0967 | -8.9714
049274Z | MV/LV Substation WH***274Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 0.21 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E20 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7406 | -7.7984
182643 | MV/LV Substation MT***643 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9319 | -8.4315
093335 | MV/LV Substation ST***335 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.136 | 7.91 |  | --> | 0.19 | 0 | 0 | 0.181 | 0 |  | --> | C26 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3872 | -6.3252
249403X | MV/LV Substation PI***403X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9765 | -7.8049
156257 | MV/LV Substation DE***257 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.1803 | -6.8698
365540X | MV/LV Substation BE***540X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =822 kVA | --> | 0.95 | 0 | 0.005 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3139 | -6.3934
214858 | MV/LV Substation BO***858 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7865 | -9.2086
154397Z | MV/LV Substation BE***397Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =142 kVA | --> | 0.19 | 0 | 0.005 | 0.178 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4182 | -6.3888
025922X | MV/LV Substation RA***922X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.372 | -9.0343
082921Y | MV/LV Substation SH***921Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6338 | -6.6689
095017 | MV/LV Substation SH***017 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.176 | 0.7 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6315 | -9.4896
093363Z | MV/LV Substation FR***363Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =807 kVA | --> | 0.95 | 0 | 0.034 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4033 | -6.1578
067275 | MV/LV Substation AN***275 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.074 | 13.8 |  | --> | 0.19 | 0 | 0.014 | 0.162 | 0 |  | --> | C13 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6663 | -8.5957
281802Z | MV/LV Substation CL***802Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =313 kVA | --> | 0.38 | 0 | 0.075 | 0 | 0 | Constrained, otherwise capacity available =312 kW | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.873 | -8.407
192136 | MV/LV Substation DA***136 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.126 | 1.56 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C15 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0755 | -8.2838
206777 | MV/LV Substation PO***777 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.76 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E14 ex BANGOR ERRIS | Bangor Erris [T421] | BELLACORICK |  | 54.314 | -9.716
024792X | MV/LV Substation BA***792X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.14 |  | --> | 0.048 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =18 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2246 | -8.518
066076Z | MV/LV Substation AR***076Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C17 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4583 | -6.2064
015849Z | MV/LV Substation KI***849Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.3016 | -6.7039
238870X | MV/LV Substation CL***870X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.647 | -9.154
365982 | MV/LV Substation JO***982 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =886 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2966 | -6.3728
0394042 | MV/LV Substation JE***4042 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.225 | 3.45 |  | --> | 0.38 | 0 | 0.089 | 0.29 | 0 |  | --> | C18 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2693 | -9.0621
116633 | MV/LV Substation SH***633 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 8.1 |  | --> | 0.048 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | E15 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.803 | -9.4915
017525 | MV/LV Substation FR***525 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.98 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E11 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.6026 | -8.9661
196041X | MV/LV Substation EN***041X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.6171 | -6.8655
089770 | MV/LV Substation LO***770 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 3.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E22 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2079 | -8.8674
081275Z | MV/LV Substation PE***275Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3206 | -6.4814
021713X | MV/LV Substation SI***713X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0 | 0.18 | 0 |  | --> | C12 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9033 | -8.4257
007654Z | MV/LV Substation LA***654Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.358 | 1.4 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E12 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2483 | -6.3417
220728X | MV/LV Substation LE***728X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 1.36 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.2779 | -9.295
068014X | MV/LV Substation AU***014X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.47 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C46 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3437 | -6.2762
293119Y | MV/LV Substation BO***119Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E20 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9556 | -6.818
062045 | MV/LV Substation CA***045 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.214 | 2.33 |  | --> | 0.38 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C14 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.013 | -6.4117
015495Z | MV/LV Substation MI***495Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 12.6 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2368 | -6.6764
365444X | MV/LV Substation KI***444X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0 | 0.18 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.276 | -6.4064
184778 | MV/LV Substation CO***778 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1034 | -6.711
156226Y | MV/LV Substation CO***226Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2365 | -6.9644
001482 | MV/LV Substation RO***482 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.092 | 1.55 |  | --> | 0.19 | 0 | 0.081 | 0.115 | 0 |  | --> | C12 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2883 | -6.1703
032411X | MV/LV Substation BA***411X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1762 | -7.2893
281231Z | MV/LV Substation VI***231Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C24 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8643 | -8.5269
365293 | MV/LV Substation QU***293 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2636 | -6.5339
039607X | MV/LV Substation SA***607X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C20 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2823 | -9.0392
2814214 | MV/LV Substation HA***4214 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.79 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex FACTORY CROSS | Factory Cross [T41,T42] | BARNAHELY |  | 51.8394 | -8.2974
149805 | MV/LV Substation KE***805 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6504 | -8.2259
020065 | MV/LV Substation EM***065 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C11 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.062 | -9.506
064691Y | MV/LV Substation JO***691Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.6866 | -6.5437
071201 | MV/LV Substation GL***201 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =384 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1452 | -6.1246
014094 | MV/LV Substation LO***094 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C12 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1586 | -6.9146
0694040 | MV/LV Substation BU***4040 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.11 | 7.75 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3311 | -6.2475
053570Y | MV/LV Substation WA***570Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C23 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2766 | -7.4598
059984 | MV/LV Substation AG***984 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.15 | 0 | 0 | Constrained, otherwise capacity available =260 kW | --> | E11 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0518 | -7.3142
109046 | MV/LV Substation AI***046 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.381 | 0.38 | Constrained, otherwise capacity available =578 kVA | --> | 0.598 | 0 | 0.007 | 0.5 | 0 |  | --> | C20 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7119 | -8.8721
026179Z | MV/LV Substation TH***179Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.66 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =591 kW | --> | C12 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7466 | -8.7374
009991X | MV/LV Substation ST***991X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2407 | -7.1021
127894X | MV/LV Substation TO***894X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.6151 | -8.0258
073066X | MV/LV Substation AR***066X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C15 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.3976 | -7.7338
001802 | MV/LV Substation LA***802 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.023 | 0.162 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2572 | -6.1536
117553Y | MV/LV Substation K ***553Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E22 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1826 | -8.4839
152250 | MV/LV Substation CA***250 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.095 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =53 kW | --> | C16 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.5826 | -8.1701
017951X | MV/LV Substation RA***951X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 1.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.376 | -9.0467
007373 | MV/LV Substation WE***373 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.4 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =950 kW | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2704 | -6.423
139903X | MV/LV Substation RA***903X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =0 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C17 ex VIRGINIA | Virginia [T41,T42] | MEATH HILL |  | 53.836 | -7.0729
248857X | MV/LV Substation MC***857X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.5177 | -6.6917
002611 | MV/LV Substation CA***611 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.054 | 2.36 |  | --> | 0.095 | 0 | 0.034 | 0.063 | 0 |  | --> | C16 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1744 | -6.1508
127264 | MV/LV Substation BO***264 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C11 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7541 | -7.9554
066251X | MV/LV Substation IN***251X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =114 kVA | --> | 0.19 | 0 | 0.041 | 0.148 | 0 |  | --> | C17 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4525 | -6.1695
066262 | MV/LV Substation ST***262 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.097 | 0.293 | 0 |  | --> | C19 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3768 | -6.0956
368426X | MV/LV Substation BR***426X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7643 | -8.7947
365884X | MV/LV Substation DE***884X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.025 | 0.345 | 0 |  | --> | C12 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2773 | -6.4095
118055Y | MV/LV Substation PO***055Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3134 | -8.1918
062974Y | MV/LV Substation SP***974Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.383 | 0.72 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C15 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 53.9935 | -6.3708
077013X | MV/LV Substation EL***013X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E25 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.6293 | -8.7272
010591X | MV/LV Substation CO***591X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.5395 | -6.9676
0654352 | MV/LV Substation BA***4352 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =614 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5696 | -6.1152
2884040 | MV/LV Substation ST***4040 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2202 | -6.228
068513 | MV/LV Substation PO***513 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.477 | 3.38 |  | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C19 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3376 | -6.2438
0074558 | MV/LV Substation CO***4558 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 16.12 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3072 | -6.6883
007465Y | MV/LV Substation BA***465Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 16.12 |  | --> | 0.095 | 0 | 0.004 | 0.091 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3837 | -6.4572
009832 | MV/LV Substation KN***832 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C14 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.4076 | -7.1855
204256X | MV/LV Substation MA***256X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.02 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.0632 | -7.451
065020 | MV/LV Substation HA***020 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.598 | 0 | 0.048 | 0.5 | 0 |  | --> | C24 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6052 | -6.1795
062004 | MV/LV Substation CU***004 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.372 | 0.72 |  | --> | 0.598 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =542 kW | --> | C12 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0063 | -6.3886
067271 | MV/LV Substation AS***271 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.38 | 0 | 0 | 0.327 | 0 |  | --> | C11 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6497 | -8.6174
056563 | MV/LV Substation BA***563 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.26 |  | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =27 kW | --> | E15 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0676 | -8.1327
0934021 | MV/LV Substation ID***4021 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C31 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.3997 | -6.2195
0064026 | MV/LV Substation BE***4026 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 3.12 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C17 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5041 | -6.5768
001679 | MV/LV Substation SH***679 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =269 kVA | --> | 0.38 | 0 | 0.029 | 0.34 | 0 |  | --> | C11 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2399 | -6.1154
071704 | MV/LV Substation SE***704 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.095 | 5.58 |  | --> | 0.19 | 0 | 0.012 | 0.166 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0946 | -6.1143
052331Y | MV/LV Substation BI***331Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.491 | 10.9 |  | --> | 0.598 | 0 | 0.04 | 0.5 | 0 |  | --> | C12 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5266 | -7.344
004043Y | MV/LV Substation FI***043Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 18.08 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7893 | -6.1724
0644041 | MV/LV Substation AB***4041 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6463 | -6.424
164148X | MV/LV Substation CO***148X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C22 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5868 | -9.3641
137322X | MV/LV Substation KI***322X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.3447 | -9.8131
023995 | MV/LV Substation FO***995 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1632 | -8.256
182157 | MV/LV Substation FA***157 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C15 ex TULLA | Tulla [T41,T42] | ENNIS |  | 52.9346 | -8.6435
058020 | MV/LV Substation AN***020 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.138 | 3 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8607 | -8.2159
093308 | MV/LV Substation GO***308 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =215 kVA | --> | 0.38 | 0 | 0.02 | 0.339 | 0 |  | --> | C11 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3794 | -6.2992
293623Z | MV/LV Substation BA***623Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =60 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9921 | -6.6384
065128 | MV/LV Substation OL***128 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =248 kVA | --> | 0.38 | 0 | 0.079 | 0 | 0 | Constrained, otherwise capacity available =300 kW | --> | C18 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.523 | -6.1046
0654372 | MV/LV Substation FO***4372 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0.079 | 0.5 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6066 | -6.2101
152648X | MV/LV Substation TH***648X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6486 | -8.4052
068843 | MV/LV Substation GA***843 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =617 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3555 | -6.2563
0504382 | MV/LV Substation AR***4382 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 6.49 |  | --> | 0.598 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =573 kW | --> | C18 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4331 | -7.936
305232 | MV/LV Substation MO***232 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 4.61 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex LUMCLOON | Lumcloon [T421,T422] | DALLOW |  | 53.2602 | -7.8631
062710Y | MV/LV Substation AT***710Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.153 | 5.69 |  | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C19 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0175 | -6.3811
039148 | MV/LV Substation IN***148 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =419 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =569 kW | --> | C19 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2843 | -9.0291
293159X | MV/LV Substation PO***159X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =156 kW | --> | E13 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7988 | -6.4649
026852X | MV/LV Substation LI***852X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 8.66 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.8052 | -8.6467
050197X | MV/LV Substation BL***197X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.246 | 6.49 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C17 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4315 | -7.8953
082102 | MV/LV Substation DE***102 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 2.01 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C16 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6534 | -6.6964
066427 | MV/LV Substation KI***427 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4745 | -6.3192
071040 | MV/LV Substation CH***040 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0.067 | 0.31 | 0 |  | --> | C12 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1471 | -6.0728
138693 | MV/LV Substation MI***693 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.18 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9265 | -7.0068
068541 | MV/LV Substation SP***541 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C37 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3507 | -6.2524
015928 | MV/LV Substation LO***928 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.3003 | -6.6885
004144Y | MV/LV Substation TH***144Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0.055 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C24 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7857 | -6.166
034195Y | MV/LV Substation PO***195Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.57 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E25 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3724 | -7.6628
099131 | MV/LV Substation HO***131 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.96 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C12 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9587 | -7.7059
075790 | MV/LV Substation KI***790 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 4.38 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E14 ex CRANE | Crane [T122] | CRANE |  | 52.5433 | -6.5219
062677 | MV/LV Substation AN***677 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 4.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E16 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 53.999 | -6.2762
204064X | MV/LV Substation GL***064X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E14 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1566 | -7.4489
250752 | MV/LV Substation BA***752 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.26 |  | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C27 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1573 | -8.2973
138019X | MV/LV Substation LI***019X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.52 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex SHERCOCK | Shercock [T41,T42] | MEATH HILL |  | 53.9935 | -6.8893
067579Y | MV/LV Substation LI***579Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =540 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C11 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6969 | -8.6475
253987Z | MV/LV Substation CO***987Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5172 | -8.8606
035245X | MV/LV Substation AI***245X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 6.17 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C22 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3709 | -7.9152
206888 | MV/LV Substation CO***888 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 7.61 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E14 ex BELLACORICK | Bellacorick [T122] | BELLACORICK |  | 54.2082 | -9.9351
008137 | MV/LV Substation CU***137 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =157 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3839 | -6.9317
004283Y | MV/LV Substation CR***283Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C24 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7875 | -6.1671
068245X | MV/LV Substation WE***245X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.377 | 9.02 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3456 | -6.2579
007805X | MV/LV Substation BA***805X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.141 | 16.12 |  | --> | 0.19 | 0 | 0.016 | 0.17 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3936 | -6.3948
054814X | MV/LV Substation DU***814X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =552 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0397 | -7.3074
139296X | MV/LV Substation LI***296X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8782 | -7.2379
288878 | MV/LV Substation PI***878 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2446 | -6.1912
049739Y | MV/LV Substation RO***739Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.31 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.8256 | -7.9202
013030 | MV/LV Substation KI***030 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =263 kVA | --> | 0.38 | 0 | 0.014 | 0.35 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9932 | -6.9793
039102X | MV/LV Substation TH***102X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 11.03 |  | --> | 0.048 | 0 | 0.01 | 0.037 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.254 | -9.1608
180650X | MV/LV Substation ED***650X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.27 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7746 | -7.0011
014750 | MV/LV Substation HI***750 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.63 |  | --> | 0.048 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E12 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0683 | -6.837
0814211 | MV/LV Substation HE***4211 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3592 | -6.4315
054150Z | MV/LV Substation PA***150Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =820 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =925 kW | --> | E16 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.027 | -7.301
365236X | MV/LV Substation CH***236X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =252 kVA | --> | 0.38 | 0 | 0.02 | 0.344 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.318 | -6.4123
281021Z | MV/LV Substation MU***021Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.216 | 5.49 |  | --> | 0.38 | 0 | 0.04 | 0.324 | 0 |  | --> | C12 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.882 | -8.4708
032535X | MV/LV Substation RE***535X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1945 | -7.2112
0814289 | MV/LV Substation AD***4289 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =486 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3419 | -6.4713
032183 | MV/LV Substation ST***183 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2008 | -6.9797
062711Y | MV/LV Substation AT***711Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.31 | 5.69 |  | --> | 0.38 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C19 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0177 | -6.378
071095 | MV/LV Substation GR***095 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =288 kVA | --> | 0.38 | 0 | 0.024 | 0.347 | 0 |  | --> | C17 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1431 | -6.0606
011627Z | MV/LV Substation CE***627Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6605 | -7.211
093007 | MV/LV Substation BA***007 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.38 | 0 | 0.022 | 0.335 | 0 |  | --> | C16 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3868 | -6.2935
012191Y | MV/LV Substation DE***191Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.376 | 1.99 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C18 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8422 | -6.9359
015622Z | MV/LV Substation SA***622Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =157 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2478 | -6.6614
116318Y | MV/LV Substation BR***318Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.32 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7981 | -9.5117
062556Y | MV/LV Substation SA***556Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.317 | 2.33 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C18 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.0173 | -6.4236
127853Y | MV/LV Substation KI***853Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6871 | -7.8458
152310 | MV/LV Substation KI***310 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E31 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6909 | -8.1463
071971 | MV/LV Substation NE***971 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.58 |  | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C13 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0909 | -6.1139
122427 | MV/LV Substation MU***427 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 4.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8312 | -6.772
433086X | MV/LV Substation SE***086X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8973 | -8.5604
150765 | MV/LV Substation KI***765 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7901 | -7.8215
081071Y | MV/LV Substation VA***071Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.341 | -6.5481
008100 | MV/LV Substation BA***100 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.158 | 0.2 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2804 | -6.8378
127511X | MV/LV Substation KI***511X |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6179 | -7.8394
093341X | MV/LV Substation RE***341X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =533 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3975 | -6.2472
120689X | MV/LV Substation BA***689X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4398 | -6.8648
017411Z | MV/LV Substation CA***411Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.189 | 1.05 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C18 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4269 | -9.0191
281213Z | MV/LV Substation BU***213Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.264 | 5.49 |  | --> | 0.38 | 0 | 0 | 0.361 | 0 |  | --> | C23 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8492 | -8.4782
139697X | MV/LV Substation MU***697X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7375 | -7.1501
017291Z | MV/LV Substation ST***291Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.39 | 1.05 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3775 | -9.0537
054178Z | MV/LV Substation TR***178Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C12 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.9709 | -7.4262
009648Y | MV/LV Substation MO***648Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.025 | 0.95 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2631 | -7.1449
127764Y | MV/LV Substation CR***764Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =296 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C14 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6771 | -7.8159
005550X | MV/LV Substation BA***550X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6822 | -6.2203
365549X | MV/LV Substation TA***549X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.19 | 0 | 0 | 0.168 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3191 | -6.3552
008724 | MV/LV Substation CL***724 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 0.2 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.298 | -6.7688
0424252 | MV/LV Substation EC***4252 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =534 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C13 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8571 | -9.2854
034981X | MV/LV Substation OL***981X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.317 | 0.95 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C16 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3504 | -7.6912
069530 | MV/LV Substation KI***530 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 0.91 |  | --> | 0.38 | 0 | 0.018 | 0.354 | 0 |  | --> | C18 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3171 | -6.2924
046468 | MV/LV Substation ST***468 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 5.48 |  | --> | 0.095 | 0 | 0 | 0.074 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2589 | -8.3857
062403 | MV/LV Substation RO***403 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.12 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9884 | -6.3709
2814010 | MV/LV Substation OR***4010 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =698 kVA | --> | 0.95 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =890 kW | --> | C13 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8892 | -8.5048
009433Y | MV/LV Substation SO***433Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2378 | -7.1456
0464070 | MV/LV Substation BO***4070 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.48 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3112 | -8.5585
0024061 | MV/LV Substation CA***4061 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.475 | 0.48 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C20 ex KILMARTIN | Kilmartin [T41] | ARKLOW |  | 53.0637 | -6.2238
281377Z | MV/LV Substation GL***377Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C24 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8228 | -8.466
0584327 | MV/LV Substation KI***4327 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C25 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8416 | -8.1254
054393Y | MV/LV Substation MO***393Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =619 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | E14 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.8948 | -7.2804
377984X | MV/LV Substation GU***984X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9339 | -10.2328
001534 | MV/LV Substation KN***534 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 1.16 |  | --> | 0.38 | 0 | 0.006 | 0.368 | 0 |  | --> | C14 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2754 | -6.1798
281131 | MV/LV Substation DE***131 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.67 |  | --> | 0.598 | 0 | 0.017 | 0.5 | 0 |  | --> | C19 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8991 | -8.466
120551Y | MV/LV Substation JO***551Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 3.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.3941 | -6.8429
026682X | MV/LV Substation AB***682X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.052 | 0 | 0 | Constrained, otherwise capacity available =142 kW | --> | C16 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7075 | -8.5332
237699 | MV/LV Substation SH***699 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C18 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8291 | -6.4045
015437X | MV/LV Substation AS***437X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E18 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1937 | -6.5093
0694007 | MV/LV Substation TE***4007 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.28 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C06 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.331 | -6.2352
377552X | MV/LV Substation RE***552X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8309 | -10.1721
164781 | MV/LV Substation GL***781 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 0.88 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5666 | -9.1207
237182X | MV/LV Substation GL***182X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.7824 | -6.2533
377882X | MV/LV Substation BE***882X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8239 | -10.273
377988 | MV/LV Substation QU***988 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9485 | -10.2256
0604171 | MV/LV Substation PQ***4171 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.351 | 2.57 |  | --> | 0.38 | 0 | 0.16 | 0 | 0 | Constrained, otherwise capacity available =255 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0718 | -7.1005
0394173 | MV/LV Substation MB***4173 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.196 | 11.03 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C17 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2705 | -9.1159
062160X | MV/LV Substation MA***160X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 3.47 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =317 kW | --> | E17 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0404 | -6.1878
0674142 | MV/LV Substation BO***4142 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C20 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6405 | -8.5845
281270Z | MV/LV Substation GR***270Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =221 kVA | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C17 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8608 | -8.4415
426486 | MV/LV Substation FE***486 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1385 | -10.4583
0664328 | MV/LV Substation BE***4328 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =561 kVA | --> | 0.598 | 0 | 0.039 | 0 | 0 | Constrained, otherwise capacity available =560 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.4919 | -6.1551
164820X | MV/LV Substation GL***820X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 0.88 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5645 | -9.109
028036 | MV/LV Substation TE***036 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C13 ex COW CROSS |  |  |  | 51.8569 | -8.2964
034007 | MV/LV Substation WI***007 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.274 | 5.88 |  | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =341 kW | --> | C12 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3664 | -7.6979
209413X | MV/LV Substation FA***413X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.2351 | -7.692
0174444 | MV/LV Substation OC***4444 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.23 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C13 ex CHURCHTOWN | Churchtown [T41] | RATHKEALE |  | 52.4586 | -9.0559
281075Z | MV/LV Substation BR***075Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0.041 | 0 | 0 | Constrained, otherwise capacity available =335 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8212 | -8.382
005671X | MV/LV Substation ES***671X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.038 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.087 | 0 |  | --> | E19 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6279 | -6.3063
0094439 | MV/LV Substation M9***4439 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C14 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.3616 | -7.1729
008471Y | MV/LV Substation CU***471Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3755 | -6.855
011638X | MV/LV Substation DA***638X |  | 10 kV | _ | LV | 75 kVA :Pole Substation | 0.075 | --> | 0.075 | 0.067 | 2.8 |  | --> | 0.071 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =70 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6385 | -7.2278
120431 | MV/LV Substation DU***431 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.135 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.3961 | -6.8345
017116 | MV/LV Substation BA***116 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.05 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3968 | -9.0265
368002 | MV/LV Substation MA***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7644 | -8.7664
1544278 | MV/LV Substation CL***4278 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3853 | -6.3714
151230 | MV/LV Substation BA***230 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3888 | -8.4396
066474Z | MV/LV Substation MI***474Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =353 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C23 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4522 | -6.2251
060032 | MV/LV Substation CL***032 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 2.57 |  | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0766 | -7.0947
0654268 | MV/LV Substation GR***4268 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C18 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5266 | -6.1137
082949 | MV/LV Substation KE***949 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =154 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6278 | -6.5396
281425Y | MV/LV Substation HE***425Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =502 kVA | --> | 0.598 | 0 | 0.056 | 0 | 0 | Constrained, otherwise capacity available =539 kW | --> | C15 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8243 | -8.3924
008454X | MV/LV Substation BA***454X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4265 | -6.9145
377940 | MV/LV Substation KI***940 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8243 | -10.2737
0814089 | MV/LV Substation LI***4089 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =720 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3522 | -6.3952
377039Y | MV/LV Substation CA***039Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8317 | -10.1728
233280X | MV/LV Substation CL***280X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C23 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.24 | -9.4588
026661X | MV/LV Substation SH***661X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 8.66 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C20 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7918 | -8.7762
050122Y | MV/LV Substation CL***122Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.377 | 7.61 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4252 | -7.9179
084509 | MV/LV Substation ST***509 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =57 kVA | --> | 0.095 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1393 | -8.955
209205X | MV/LV Substation FI***205X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1984 | -7.691
164367 | MV/LV Substation CA***367 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C22 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5942 | -9.3943
064377 | MV/LV Substation CO***377 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6581 | -6.4191
160292Y | MV/LV Substation KI***292Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =52 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1335 | -7.0462
0434203 | MV/LV Substation ST***4203 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 0.43 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C13 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9421 | -8.9384
050522Y | MV/LV Substation BA***522Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 6.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4338 | -7.85
066532Z | MV/LV Substation BA***532Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5082 | -6.166
067783 | MV/LV Substation QU***783 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C11 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.694 | -8.636
016154Z | MV/LV Substation PR***154Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3364 | -6.5487
1824261 | MV/LV Substation RE***4261 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9309 | -8.4293
118047Y | MV/LV Substation GA***047Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 2 |  | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C17 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3241 | -8.2404
164462 | MV/LV Substation AG***462 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5677 | -9.1306
0934262 | MV/LV Substation BA***4262 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0 | 0.365 | 0 |  | --> | C18 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4037 | -6.2643
204271 | MV/LV Substation PI***271 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E14 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1462 | -7.4588
039102 | MV/LV Substation GA***102 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =387 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =564 kW | --> | C20 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2806 | -9.0459
127551 | MV/LV Substation CL***551 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.626 | -7.9396
009148 | MV/LV Substation MU***148 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.184 | 8.16 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2865 | -7.1217
067239Y | MV/LV Substation CU***239Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.3 | 13.8 |  | --> | 0.38 | 0 | 0.016 | 0.354 | 0 |  | --> | C19 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6646 | -8.5775
002175 | MV/LV Substation RE***175 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 2.36 |  | --> | 0.19 | 0 | 0.026 | 0.164 | 0 |  | --> | C12 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1936 | -6.1307
031398Y | MV/LV Substation CI***398Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =559 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | C21 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0915 | -7.623
027060 | MV/LV Substation CA***060 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.136 | 7.79 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C13 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7219 | -9.1159
154738 | MV/LV Substation CL***738 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4105 | -6.4445
0824368 | MV/LV Substation RU***4368 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.01 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =591 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6564 | -6.6747
031201Y | MV/LV Substation TE***201Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.115 | -7.5531
158213X | MV/LV Substation CL***213X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.8745 | -9.2411
0994127 | MV/LV Substation JM***4127 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9462 | -7.6855
233284 | MV/LV Substation DR***284 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C21 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.1904 | -9.4256
007034 | MV/LV Substation ST***034 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =229 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3313 | -6.4685
293268Z | MV/LV Substation TI***268Z |  | 20 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.031 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | E13 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7913 | -6.4578
377311 | MV/LV Substation AG***311 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8381 | -10.329
031800 | MV/LV Substation GR***800 |  | 20 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | E17 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.1971 | -7.4345
010498X | MV/LV Substation DU***498X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.532 | -7.1357
377971 | MV/LV Substation GL***971 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8497 | -10.3346
034843X | MV/LV Substation MO***843X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.189 | 0.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.5218 | -7.72
281696Z | MV/LV Substation HE***696Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8257 | -8.3825
0824375 | MV/LV Substation CL***4375 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5909 | -6.5359
067442Y | MV/LV Substation CA***442Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.26 | 6.81 |  | --> | 0.38 | 0 | 0.062 | 0.314 | 0 |  | --> | C03 ex AHANE | Ahane [T102] | AHANE |  | 52.6638 | -8.5346
062741Y | MV/LV Substation CA***741Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 3.47 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E17 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0373 | -6.1827
162009 | MV/LV Substation LE***009 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.062 | 0.25 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C11 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8347 | -7.4864
012808 | MV/LV Substation GR***808 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C24 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8558 | -6.8774
281080X | MV/LV Substation PO***080X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C19 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8158 | -8.3951
281665Z | MV/LV Substation HE***665Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =545 kVA | --> | 0.598 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =574 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.825 | -8.385
288341 | MV/LV Substation FE***341 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2754 | -6.2534
2524169 | MV/LV Substation MO***4169 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.76 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex RECESS | Recess [T41] | SCREEB |  | 53.5605 | -9.8926
136512 | MV/LV Substation LA***512 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6712 | -7.9832
251308X | MV/LV Substation RI***308X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C28 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3448 | -8.941
035901X | MV/LV Substation KI***901X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.17 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C22 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3593 | -7.9408
010081 | MV/LV Substation BA***081 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.4964 | -7.1845
0664090 | MV/LV Substation TH***4090 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.062 | 0 | 0 | Constrained, otherwise capacity available =319 kW | --> | E17 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.448 | -6.2526
293752Y | MV/LV Substation ST***752Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9978 | -6.6706
164428 | MV/LV Substation LI***428 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.556 | -9.1494
0414079 | MV/LV Substation KN***4079 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7892 | -8.9265
062269X | MV/LV Substation ED***269X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.1106 | -6.343
0544548 | MV/LV Substation CA***4548 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C21 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0116 | -7.1438
011306 | MV/LV Substation RA***306 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.02 | 2.8 |  | --> | 0.031 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =15 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6261 | -7.2147
120223 | MV/LV Substation PU***223 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =61 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2778 | -6.8248
054241Z | MV/LV Substation DI***241Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C21 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0128 | -7.1419
293626Z | MV/LV Substation ST***626Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9829 | -6.6714
017082 | MV/LV Substation AB***082 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.343 | 1.05 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C15 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.447 | -9.0659
111644Y | MV/LV Substation SC***644Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex BALLYDEHOB | Ballydehob [T421] | DUNMANWAY |  | 51.5463 | -9.5328
495804 | MV/LV Substation PU***804 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9647 | -10.0985
111510 | MV/LV Substation RO***510 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C16 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6749 | -9.4581
056570 | MV/LV Substation KI***570 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.26 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E15 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0561 | -8.1817
068179 | MV/LV Substation RU***179 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex DRUMCONDRA | Drumcondra [T41,T42] | MCDERMOTT |  | 53.3589 | -6.2553
065485Z | MV/LV Substation NA***485Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6077 | -6.2044
069289 | MV/LV Substation MO***289 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.228 | 4.91 |  | --> | 0.38 | 0 | 0.049 | 0.32 | 0 |  | --> | C14 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3174 | -6.321
081597Z | MV/LV Substation WE***597Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C12 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3691 | -6.3777
377810X | MV/LV Substation RE***810X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9517 | -10.2136
005894 | MV/LV Substation BA***894 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =14 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.698 | -6.3447
139654 | MV/LV Substation DR***654 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 2.68 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E12 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7199 | -7.151
248782X | MV/LV Substation RY***782X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =309 kVA | --> | 0.38 | 0 | 0.058 | 0 | 0 | Constrained, otherwise capacity available =324 kW | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4074 | -6.6765
068274 | MV/LV Substation ST***274 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =454 kVA | --> | 0.598 | 0 | 0.017 | 0.5 | 0 |  | --> | C13 ex DRUMCONDRA | Drumcondra [T41,T42] | MCDERMOTT |  | 53.371 | -6.253
066209Z | MV/LV Substation BR***209Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =143 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E15 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5099 | -6.398
039239X | MV/LV Substation GO***239X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =522 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C14 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2835 | -9.0386
426649 | MV/LV Substation HO***649 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E17 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.145 | -10.2746
001049 | MV/LV Substation FO***049 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.253 | 1.16 |  | --> | 0.38 | 0 | 0.058 | 0.316 | 0 |  | --> | C14 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2745 | -6.1756
038563X | MV/LV Substation KI***563X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex GORT | Gort [T41,T42] | ENNIS |  | 53.1269 | -8.9189
0684317 | MV/LV Substation HA***4317 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.98 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3363 | -6.258
039337 | MV/LV Substation LI***337 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =117 kVA | --> | 0.38 | 0 | 0.06 | 0.295 | 0 |  | --> | C23 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2846 | -9.0365
065385Z | MV/LV Substation BA***385Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.005 | 0.368 | 0 |  | --> | C21 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6159 | -6.1951
0154357 | MV/LV Substation HI***4357 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =245 kVA | --> | 0.38 | 0 | 0.07 | 0 | 0 | Constrained, otherwise capacity available =306 kW | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2483 | -6.5812
288218 | MV/LV Substation MO***218 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.034 | 0.156 | 0 |  | --> | C20 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2757 | -6.2239
111905 | MV/LV Substation WE***905 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =237 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C16 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.672 | -9.4738
243933 | MV/LV Substation DE***933 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1427 | -10.1574
017007Z | MV/LV Substation MI***007Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 4.23 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C17 ex CHURCHTOWN | Churchtown [T41] | RATHKEALE |  | 52.4494 | -9.0619
265048Y | MV/LV Substation GO***048Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.066 | 0.07 | Constrained, otherwise capacity available =395 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1143 | -7.5773
0694078 | MV/LV Substation ST***4078 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.99 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.326 | -6.2777
0694079 | MV/LV Substation WH***4079 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.275 | -6.3152
064691X | MV/LV Substation BI***691X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =303 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =355 kW | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7618 | -6.266
160820Y | MV/LV Substation SU***820Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1426 | -7.0581
093336 | MV/LV Substation BE***336 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.243 | 12.96 |  | --> | 0.38 | 0 | 0.026 | 0.339 | 0 |  | --> | C20 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3854 | -6.2193
067130X | MV/LV Substation PR***130X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E18 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.576 | -8.6995
053446 | MV/LV Substation DE***446 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C21 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2409 | -7.4771
252755X | MV/LV Substation CL***755X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.32 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4903 | -10.0187
3654138 | MV/LV Substation PA***4138 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.287 | -6.4346
026928 | MV/LV Substation BA***928 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =21 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7119 | -8.6282
5034064 | MV/LV Substation HE***4064 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.387 | 1.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9958 | -7.5104
0684019 | MV/LV Substation EM***4019 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =962 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3552 | -6.25
027546X | MV/LV Substation CA***546X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 3.16 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7985 | -9.0003
345007X | MV/LV Substation LI***007X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3178 | -8.0741
0824040 | MV/LV Substation LI***4040 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =116 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C32 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6438 | -6.6872
0664126 | MV/LV Substation DA***4126 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =386 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4157 | -6.2371
032154Y | MV/LV Substation KI***154Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =23 kVA | --> | 0.048 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =21 kW | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1631 | -7.0009
013905Y | MV/LV Substation CO***905Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0 | 0.182 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9819 | -6.9988
160061 | MV/LV Substation ST***061 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | C16 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.153 | -7.1786
068972 | MV/LV Substation HO***972 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.2 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3408 | -6.2435
026957Y | MV/LV Substation CO***957Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.057 | 0 | 0 | Constrained, otherwise capacity available =323 kW | --> | E41 ex KINSALE | Kinsale [T423] | TRABEG |  | 51.7003 | -8.5315
252485 | MV/LV Substation WE***485 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.101 | 1.32 |  | --> | 0.19 | 0 | 0.015 | 0.165 | 0 |  | --> | C26 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4902 | -10.0192
005089 | MV/LV Substation CL***089 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =63 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C14 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6763 | -6.2781
062811X | MV/LV Substation HA***811X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 3.12 |  | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9689 | -6.3837
068411 | MV/LV Substation CO***411 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =524 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C11 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3539 | -6.2651
365220Y | MV/LV Substation KI***220Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.281 | -6.4803
377533X | MV/LV Substation DO***533X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9747 | -10.1668
060488X | MV/LV Substation SA***488X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 2.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0989 | -7.0866
071857 | MV/LV Substation SE***857 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.314 | 5.58 |  | --> | 0.38 | 0 | 0.05 | 0.331 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1061 | -6.0578
082978Y | MV/LV Substation CR***978Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6455 | -6.6059
111766 | MV/LV Substation CU***766 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C11 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6511 | -9.3763
039419 | MV/LV Substation HO***419 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C13 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2865 | -9.0424
281336Z | MV/LV Substation WE***336Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | C15 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8192 | -8.4042
281432 | MV/LV Substation BA***432 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 6.78 |  | --> | 0.38 | 0 | 0.008 | 0.36 | 0 |  | --> | C26 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8903 | -8.4062
0014163 | MV/LV Substation TB***4163 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.16 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2969 | -6.2113
024646X | MV/LV Substation NE***646X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.14 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2316 | -8.674
244291 | MV/LV Substation KP***291 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.0933 | -9.8377
192932 | MV/LV Substation CR***932 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 1.56 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0243 | -8.2643
0174022 | MV/LV Substation AS***4022 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5994 | -8.9663
2094079 | MV/LV Substation PO***4079 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.2055 | -7.6375
139170 | MV/LV Substation GR***170 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =12 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E16 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8671 | -7.4423
054994X | MV/LV Substation CA***994X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.9795 | -7.4926
033652Y | MV/LV Substation KI***652Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =487 kVA | --> | 0.598 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =560 kW | --> | C15 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3473 | -7.4143
049761Y | MV/LV Substation MO***761Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5693 | -7.7794
070761 | MV/LV Substation GN***761 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 0.76 |  | --> | 0.095 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | E15 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.1165 | -9.2711
1164241 | MV/LV Substation N5***4241 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.8043 | -9.4977
209729X | MV/LV Substation MU***729X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0236 | -7.6408
0074434 | MV/LV Substation CA***4434 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E13 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.1978 | -6.3643
053031Z | MV/LV Substation TU***031Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0 | 0.369 | 0 |  | --> | C17 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2709 | -7.4967
069563 | MV/LV Substation ED***563 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =247 kVA | --> | 0.38 | 0 | 0.029 | 0.337 | 0 |  | --> | C17 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.275 | -6.2892
065218Z | MV/LV Substation RO***218Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5157 | -6.1516
005064Y | MV/LV Substation PE***064Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =558 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =580 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6789 | -6.3047
082384 | MV/LV Substation ST***384 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.01 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C17 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.663 | -6.6809
067775Y | MV/LV Substation CO***775Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =529 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex BALLINACURRA | Ballinacurra [T41,T42] | LIMERICK |  | 52.6397 | -8.6471
1204271 | MV/LV Substation NE***4271 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.215 | 3.5 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4143 | -6.8285
068502 | MV/LV Substation JE***502 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 14.34 |  | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C11 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3476 | -6.2061
3774030 | MV/LV Substation RE***4030 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9516 | -10.2154
0524040 | MV/LV Substation RK***4040 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C15 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.5242 | -7.1571
082909Y | MV/LV Substation KI***909Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E15 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6288 | -6.6596
305437 | MV/LV Substation CU***437 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.112 | 0.3 |  | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | C15 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.1883 | -7.9766
0504230 | MV/LV Substation PI***4230 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.489 | -7.8085
281711Z | MV/LV Substation WO***711Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.456 | 5.49 |  | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C13 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8799 | -8.4664
0254384 | MV/LV Substation DE***4384 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 2.96 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E17 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3628 | -8.688
093513Z | MV/LV Substation MI***513Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =624 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C25 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4056 | -6.3425
165580 | MV/LV Substation FA***580 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C12 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.6955 | -8.8152
248625X | MV/LV Substation SU***625X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4838 | -6.7291
0394320 | MV/LV Substation CA***4320 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.3057 | -8.9109
068706X | MV/LV Substation TH***706X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3458 | -6.2457
238804 | MV/LV Substation BA***804 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.7226 | -9.1745
0694055 | MV/LV Substation SC***4055 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.279 | -6.3048
154317Z | MV/LV Substation DE***317Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.008 | 0.364 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.392 | -6.437
064572Y | MV/LV Substation SL***572Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7038 | -6.5351
093007X | MV/LV Substation WH***007X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 12.96 |  | --> | 0.38 | 0 | 0.036 | 0.337 | 0 |  | --> | C20 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3835 | -6.2219
067130 | MV/LV Substation UN***130 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.81 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C05 ex AHANE | Ahane [T102] | AHANE |  | 52.6634 | -8.5057
068112 | MV/LV Substation KI***112 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 2.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3402 | -6.2564
1544295 | MV/LV Substation LI***4295 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3872 | -6.5792
365038X | MV/LV Substation DE***038X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =258 kVA | --> | 0.38 | 0 | 0.003 | 0.358 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3281 | -6.4222
032791 | MV/LV Substation BA***791 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1952 | -7.1206
067048 | MV/LV Substation BA***048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C20 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.644 | -8.6453
207009 | MV/LV Substation KI***009 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.105 | 2.9 |  | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C18 ex GLENGOOLE | Glengoole [T42] | THURLES |  | 52.5658 | -7.6725
081350Z | MV/LV Substation KI***350Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.3104 | -6.4662
041307Y | MV/LV Substation SI***307Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =491 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =579 kW | --> | E13 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7251 | -8.9964
033109 | MV/LV Substation KI***109 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3864 | -7.3288
160868Y | MV/LV Substation HE***868Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0417 | -7.2615
029738Y | MV/LV Substation RO***738Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =347 kVA | --> | 0.38 | 0 | 0.056 | 0.331 | 0 |  | --> | C17 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9077 | -8.1651
0684293 | MV/LV Substation TR***4293 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.2 | 7.2 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C12 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3426 | -6.2491
003219Y | MV/LV Substation MA***219Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 11.58 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C22 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9794 | -6.0563
0684451 | MV/LV Substation OP***4451 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C33 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3367 | -6.3342
068381 | MV/LV Substation HA***381 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.406 | 1.86 |  | --> | 0.598 | 0 | 0.021 | 0.5 | 0 |  | --> | C16 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3648 | -6.2328
116118Y | MV/LV Substation MO***118Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 7.32 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7881 | -9.4946
068011X | MV/LV Substation GR***011X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =298 kVA | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C14 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3527 | -6.2588
214588 | MV/LV Substation KI***588 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C15 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.6744 | -9.1086
151786 | MV/LV Substation KN***786 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C25 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.4347 | -8.4084
005455 | MV/LV Substation MA***455 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 3.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C17 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6684 | -6.2729
046052X | MV/LV Substation ST***052X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =478 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2721 | -8.4736
127135X | MV/LV Substation MI***135X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.724 | -7.5864
007603Y | MV/LV Substation CA***603Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.164 | 0.9 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.2891 | -6.4876
081363Y | MV/LV Substation AR***363Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3365 | -6.539
046199X | MV/LV Substation CA***199X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 5.78 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C11 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2574 | -8.4759
1544210 | MV/LV Substation ST***4210 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =815 kVA | --> | 0.95 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =910 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.386 | -6.4376
021696X | MV/LV Substation SI***696X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.033 | 0.341 | 0 |  | --> | C11 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9098 | -8.4227
022325 | MV/LV Substation CA***325 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 4.55 |  | --> | 0.095 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | C11 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1397 | -8.6288
0544154 | MV/LV Substation DR***4154 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 53.0416 | -7.5032
081668X | MV/LV Substation FO***668X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.018 | 0.349 | 0 |  | --> | C18 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3427 | -6.4265
281975Y | MV/LV Substation PA***975Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C17 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8785 | -8.4675
062403X | MV/LV Substation D ***403X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.017 | 4.25 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0506 | -6.3424
5904005 | MV/LV Substation CR***4005 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5391 | -9.2201
0064150 | MV/LV Substation KE***4150 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 4.38 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E13 ex CRANE | Crane [T122] | CRANE |  | 52.4978 | -6.4901
365961X | MV/LV Substation HU***961X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2719 | -6.3336
007677 | MV/LV Substation GR***677 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 1.4 |  | --> | 0.095 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =63 kW | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2736 | -6.3985
065363Z | MV/LV Substation KI***363Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0.015 | 0.176 | 0 |  | --> | C29 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5958 | -6.1821
019090 | MV/LV Substation AR***090 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.156 | 2.18 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2766 | -9.7147
288172 | MV/LV Substation MI***172 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.095 | 0 | 0.025 | 0.069 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2586 | -6.2092
0254354 | MV/LV Substation BO***4354 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.3147 | -8.846
156918Y | MV/LV Substation EN***918Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.356 | 2.47 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C12 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2626 | -6.9465
064566X | MV/LV Substation SA***566X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.654 | -6.2585
023282X | MV/LV Substation UP***282X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C16 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.1324 | -8.2726
165025 | MV/LV Substation KE***025 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =316 kW | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6225 | -8.8894
0044258 | MV/LV Substation TR***4258 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 18.08 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.796 | -6.1432
053345 | MV/LV Substation I ***345 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.146 | 3.28 |  | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | C25 ex SRAH | Srah [T43] | THORNSBERRY |  | 53.2799 | -7.5065
014507X | MV/LV Substation CO***507X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0308 | -6.7524
062810X | MV/LV Substation MO***810X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.03 |  | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =22 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9181 | -6.4072
052329Z | MV/LV Substation US***329Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =544 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5185 | -7.34
164978 | MV/LV Substation AR***978 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5401 | -9.277
074463 | MV/LV Substation MA***463 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 8.5 |  | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0477 | -8.0472
2374105 | MV/LV Substation CA***4105 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8534 | -6.4212
031747 | MV/LV Substation WO***747 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =388 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.125 | -7.4757
062071 | MV/LV Substation RI***071 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.305 | 5.69 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =545 kW | --> | C14 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0026 | -6.4026
008374Z | MV/LV Substation BA***374Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2738 | -6.8363
110082X | MV/LV Substation LI***082X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 0.76 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E11 ex KILGARVAN | Kilgarvan [T421] | KNOCKEARAGH |  | 51.9047 | -9.4427
021512Z | MV/LV Substation DI***512Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =572 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9155 | -8.474
037016 | MV/LV Substation CO***016 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | C11 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.947 | -9.0587
001110 | MV/LV Substation RO***110 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =219 kVA | --> | 0.38 | 0 | 0.056 | 0.313 | 0 |  | --> | C12 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2982 | -6.2368
016161Z | MV/LV Substation MA***161Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =442 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =565 kW | --> | C28 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3648 | -6.5852
021047 | MV/LV Substation EL***047 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =263 kVA | --> | 0.38 | 0 | 0.016 | 0.349 | 0 |  | --> | C17 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9153 | -8.4609
012940 | MV/LV Substation FI***940 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.058 | 0 | 0 | Constrained, otherwise capacity available =142 kW | --> | C11 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8471 | -6.8992
025713Y | MV/LV Substation AR***713Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3265 | -8.6272
0554442 | MV/LV Substation BA***4442 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9521 | -7.6901
252637X | MV/LV Substation TH***637X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.36 | 1.32 |  | --> | 0.38 | 0 | 0.01 | 0.367 | 0 |  | --> | C26 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4928 | -10.0186
012297Y | MV/LV Substation CA***297Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.396 | 1.99 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C14 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8377 | -6.9286
144869 | MV/LV Substation ST***869 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =133 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | E25 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.7253 | -7.4048
1604182 | MV/LV Substation CL***4182 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0.051 | 0 | 0 | Constrained, otherwise capacity available =331 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1386 | -7.0504
1804121 | MV/LV Substation EU***4121 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 3.27 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C12 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7305 | -6.8867
007377Z | MV/LV Substation BA***377Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.362 | 16.12 |  | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.2743 | -6.7295
281109 | MV/LV Substation AS***109 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =210 kVA | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | C19 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8858 | -8.4938
033353 | MV/LV Substation MU***353 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.5041 | -7.5047
2814460 | MV/LV Substation JA***4460 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =604 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C16 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8288 | -8.3888
007599X | MV/LV Substation DA***599X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2487 | -6.7359
039066 | MV/LV Substation LO***066 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 3.45 |  | --> | 0.95 | 0 | 0.005 | 0.5 | 0 |  | --> | C13 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.273 | -9.0551
039061 | MV/LV Substation ST***061 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.25 | 3.45 |  | --> | 0.38 | 0 | 0.006 | 0.354 | 0 |  | --> | C19 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2718 | -9.0635
001298 | MV/LV Substation OA***298 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.019 | 0.356 | 0 |  | --> | C13 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2518 | -6.1309
426447 | MV/LV Substation RE***447 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1704 | -10.3869
0544535 | MV/LV Substation SA***4535 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E19 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0285 | -7.2799
067327Y | MV/LV Substation TE***327Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C20 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6403 | -8.6456
093229 | MV/LV Substation AR***229 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 12.96 |  | --> | 0.38 | 0 | 0.017 | 0.359 | 0 |  | --> | C20 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3875 | -6.2232
039010 | MV/LV Substation WH***010 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =558 kW | --> | C16 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2725 | -9.0508
066615 | MV/LV Substation RA***615 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4889 | -6.2859
065136 | MV/LV Substation SU***136 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.598 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =537 kW | --> | C19 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5777 | -6.1079
0664148 | MV/LV Substation FL***4148 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4802 | -6.4015
081416Z | MV/LV Substation ST***416Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C11 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3701 | -6.5934
1544029 | MV/LV Substation ST***4029 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.376 | 7.91 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.386 | -6.3767
281925X | MV/LV Substation AS***925X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8225 | -8.3907
054096X | MV/LV Substation BO***096X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =146 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0437 | -7.2869
011445Z | MV/LV Substation MA***445Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C23 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6791 | -7.0229
0994112 | MV/LV Substation ED***4112 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.388 | 2.96 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9609 | -7.7087
058934X | MV/LV Substation BU***934X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9869 | -8.1323
053952Y | MV/LV Substation CO***952Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =280 kVA | --> | 0.38 | 0 | 0 | 0.363 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2774 | -7.4908
035438X | MV/LV Substation LE***438X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.352 | 0.49 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3112 | -7.879
233181 | MV/LV Substation MA***181 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =593 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C22 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2307 | -9.4582
0994200 | MV/LV Substation SC***4200 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9499 | -7.7126
042028 | MV/LV Substation CH***028 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.442 | 1.51 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | C19 ex TURLOUGH ROAD | Turlough Road [T43] | CASTLEBAR |  | 53.8543 | -9.3012
068000X | MV/LV Substation CH***000X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.342 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3426 | -6.2705
0424100 | MV/LV Substation BV***4100 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.93 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C18 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8872 | -9.1548
365235X | MV/LV Substation GA***235X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0.011 | 0.085 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2924 | -6.4186
081580Y | MV/LV Substation ST***580Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3116 | -6.6281
281538 | MV/LV Substation DU***538 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.7915 | -8.2974
058101Y | MV/LV Substation CI***101Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 3 |  | --> | 0.19 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =157 kW | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8594 | -8.207
0264236 | MV/LV Substation GA***4236 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.6443 | -8.5692
590109 | MV/LV Substation CO***109 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5309 | -9.2744
011443 | MV/LV Substation RA***443 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C17 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6102 | -7.288
042774X | MV/LV Substation AN***774X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.166 | 1.93 |  | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C13 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8648 | -9.2858
052005Y | MV/LV Substation KE***005Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C18 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.4422 | -7.5856
0684433 | MV/LV Substation SO***4433 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 7.2 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3448 | -6.242
204645 | MV/LV Substation TR***645 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1245 | -7.2112
066866X | MV/LV Substation TH***866X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4872 | -6.141
2884118 | MV/LV Substation CU***4118 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.269 | -6.2281
281248Z | MV/LV Substation KI***248Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =497 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =580 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8096 | -8.3668
265978 | MV/LV Substation SW***978 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 0.07 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E17 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1939 | -7.7037
002722 | MV/LV Substation RO***722 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.005 | 0.042 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1685 | -6.1553
067232 | MV/LV Substation MA***232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =270 kVA | --> | 0.38 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =328 kW | --> | C19 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6718 | -8.6431
0554404 | MV/LV Substation KI***4404 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 53.016 | -7.8059
074203X | MV/LV Substation LI***203X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =515 kVA | --> | 0.598 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =576 kW | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9526 | -8.0858
074214X | MV/LV Substation KE***214X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =539 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9498 | -8.0691
0584454 | MV/LV Substation BA***4454 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.948 | -8.1342
276261 | MV/LV Substation SC***261 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 0.76 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C13 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0382 | -9.4675
082300Y | MV/LV Substation OB***300Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5782 | -6.5476
015657X | MV/LV Substation L ***657X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 12.6 |  | --> | 0.38 | 0 | 0.015 | 0.359 | 0 |  | --> | C22 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2145 | -6.6743
069375 | MV/LV Substation CR***375 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.336 | 0.91 |  | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C16 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3224 | -6.3064
255020X | MV/LV Substation DO***020X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6539 | -8.4325
018222Z | MV/LV Substation KE***222Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.75 |  | --> | 0.598 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =573 kW | --> | C11 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4467 | -9.4687
020517 | MV/LV Substation KN***517 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C15 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0623 | -9.5264
377661 | MV/LV Substation KE***661 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E17 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9299 | -10.2771
067885Y | MV/LV Substation BA***885Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =371 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C18 ex BALLINACURRA | Ballinacurra [T41,T42] | LIMERICK |  | 52.6531 | -8.6339
164059 | MV/LV Substation BR***059 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5068 | -9.3494
006051 | MV/LV Substation FR***051 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 3.12 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C14 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5056 | -6.5581
066909 | MV/LV Substation NE***909 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0.005 | 0.089 | 0 |  | --> | C24 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4917 | -6.4739
075508X | MV/LV Substation BA***508X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.064 | 0.58 |  | --> | 0.095 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =56 kW | --> | E17 ex FERNS | Ferns [T421] | CRANE |  | 52.6107 | -6.4461
154416Z | MV/LV Substation TY***416Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =599 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4207 | -6.3817
377476X | MV/LV Substation CR***476X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =6 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.111 | -9.9017
0284015 | MV/LV Substation MA***4015 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.386 | 19.7 |  | --> | 0.38 | 0 | 0.022 | 0.362 | 0 |  | --> | C12 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8508 | -8.318
1544110 | MV/LV Substation DI***4110 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =278 kVA | --> | 0.38 | 0 | 0.108 | 0 | 0 | Constrained, otherwise capacity available =283 kW | --> | C12 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3678 | -6.3832
001094 | MV/LV Substation WO***094 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.429 | 13.42 |  | --> | 0.598 | 0 | 0.012 | 0.5 | 0 |  | --> | C17 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2761 | -6.143
067250 | MV/LV Substation FR***250 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C12 ex CORBALLY | Corbally [T41,T42] | ARDNACRUSHA |  | 52.6661 | -8.6258
276035 | MV/LV Substation PA***035 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 0.76 |  | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C11 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0537 | -9.4907
012152Y | MV/LV Substation MU***152Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 2.83 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E11 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.698 | -6.9803
196106X | MV/LV Substation DU***106X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =19 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5925 | -6.7601
050665X | MV/LV Substation WI***665X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 6.49 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4379 | -7.8999
108490 | MV/LV Substation BR***490 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5377 | -7.852
0684431 | MV/LV Substation AP***4431 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 9.02 |  | --> | 0.95 | 0 | 0.001 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3464 | -6.2553
165802X | MV/LV Substation DE***802X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =351 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C16 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6277 | -8.8701
165933X | MV/LV Substation LA***933X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.052 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | C14 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6164 | -8.9045
058484Y | MV/LV Substation CO***484Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.362 | 3 |  | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C18 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8646 | -8.2009
136728Y | MV/LV Substation CA***728Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.28 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C21 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7207 | -8.4155
035002X | MV/LV Substation MO***002X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 6.17 |  | --> | 0.095 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kW | --> | C24 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3781 | -7.8432
1764068 | MV/LV Substation BA***4068 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 18.78 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.8974 | -9.0704
015528X | MV/LV Substation BO***528X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C14 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2587 | -6.667
093468Z | MV/LV Substation BE***468Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =580 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4064 | -6.1726
013637Y | MV/LV Substation RH***637Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =241 kVA | --> | 0.38 | 0 | 0.02 | 0.343 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9941 | -6.9742
2884020 | MV/LV Substation GR***4020 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 2.36 |  | --> | 0.38 | 0 | 0 | 0.267 | 0 |  | --> | C11 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1985 | -6.1399
064745Y | MV/LV Substation KN***745Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C18 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.6998 | -6.3686
253397Y | MV/LV Substation MO***397Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.4881 | -8.5728
156365Z | MV/LV Substation LA***365Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.163 | 2.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E21 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2485 | -6.9465
288944 | MV/LV Substation HI***944 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0.021 | 0.356 | 0 |  | --> | C14 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2774 | -6.2456
0034262 | MV/LV Substation BA***4262 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.033 | 11.58 |  | --> | 0.031 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C18 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9646 | -6.1492
054210X | MV/LV Substation ME***210X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C26 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0273 | -7.311
281068Y | MV/LV Substation BR***068Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0.061 | 0 | 0 | Constrained, otherwise capacity available =311 kW | --> | C17 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8612 | -8.4358
021259Z | MV/LV Substation KI***259Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C11 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9206 | -8.4755
154373 | MV/LV Substation HA***373 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =256 kVA | --> | 0.38 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =335 kW | --> | C15 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3939 | -6.4237
004259Y | MV/LV Substation HA***259Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 0.45 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C15 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.843 | -6.3587
066425 | MV/LV Substation RO***425 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4899 | -6.3022
210023 | MV/LV Substation FA***023 |  | 10 kV | _ | LV | 100 kVA :Building Structure | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9777 | -6.7252
288305X | MV/LV Substation FU***305X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =903 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2744 | -6.215
064723X | MV/LV Substation BA***723X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6129 | -6.4783
082118Z | MV/LV Substation KE***118Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.164 | 2.01 |  | --> | 0.19 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6552 | -6.703
007711Y | MV/LV Substation KN***711Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.4 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2132 | -6.5626
059129Y | MV/LV Substation DR***129Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E11 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.094 | -7.3187
0294359 | MV/LV Substation KI***4359 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9216 | -8.0882
017662 | MV/LV Substation DU***662 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.98 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E12 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4773 | -8.9145
026094 | MV/LV Substation OL***094 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 8.66 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C13 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7354 | -8.7542
052845Z | MV/LV Substation CO***845Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 10.9 |  | --> | 0.095 | 0 | 0.017 | 0.079 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6227 | -7.3877
204385X | MV/LV Substation MU***385X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =111 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.0664 | -7.2705
062110 | MV/LV Substation DA***110 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.149 | 3.12 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C12 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9853 | -6.392
019077X | MV/LV Substation PI***077X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 1.54 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C11 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2637 | -9.7049
0144427 | MV/LV Substation BL***4427 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1497 | -6.7887
009943X | MV/LV Substation BA***943X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2357 | -7.0391
066088X | MV/LV Substation NE***088X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =4 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4477 | -6.3313
066789 | MV/LV Substation BA***789 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4669 | -6.3169
158637X | MV/LV Substation SP***637X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.36 | 0.83 |  | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C18 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8484 | -9.4343
281429Y | MV/LV Substation OV***429Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8753 | -8.4099
064842Y | MV/LV Substation CA***842Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C13 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7104 | -6.2756
139054Z | MV/LV Substation RE***054Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C17 ex VIRGINIA | Virginia [T41,T42] | MEATH HILL |  | 53.8368 | -7.0729
165091 | MV/LV Substation CA***091 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.012 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C21 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.6313 | -8.9951
154390Z | MV/LV Substation DU***390Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.428 | -6.4806
015532Z | MV/LV Substation KI***532Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C19 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2245 | -6.6463
293980X | MV/LV Substation BA***980X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.83 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7112 | -6.7472
125402 | MV/LV Substation BR***402 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2606 | -8.2611
003833X | MV/LV Substation NE***833X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 11.58 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9649 | -6.147
081652Z | MV/LV Substation WI***652Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.34 | -6.6029
150064X | MV/LV Substation MC***064X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7647 | -7.7081
081208Y | MV/LV Substation BA***208Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =4 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3425 | -6.5152
209360 | MV/LV Substation KI***360 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C21 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.2029 | -7.8159
065599 | MV/LV Substation LO***599 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5595 | -6.1265
007286Z | MV/LV Substation RA***286Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.387 | 16.12 |  | --> | 0.38 | 0 | 0.023 | 0.361 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3901 | -6.3703
142069 | MV/LV Substation SK***069 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E21 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.4151 | -8.6346
144573 | MV/LV Substation NE***573 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.863 | -7.1085
014898Z | MV/LV Substation KI***898Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.111 | -6.9935
162411X | MV/LV Substation BU***411X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.25 |  | --> | 0.048 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.9584 | -7.4567
055046 | MV/LV Substation AS***046 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C12 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9633 | -7.7926
081115Z | MV/LV Substation GR***115Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.38 | 0 | 0.024 | 0.342 | 0 |  | --> | C13 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3399 | -6.4393
210052 | MV/LV Substation MA***052 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =232 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C19 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9386 | -6.7838
019374X | MV/LV Substation CU***374X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.54 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2425 | -9.7797
281549 | MV/LV Substation KI***549 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8042 | -8.2864
006496Y | MV/LV Substation MA***496Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 3.12 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C14 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5158 | -6.5745
2884219 | MV/LV Substation FE***4219 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C17 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2687 | -6.2188
116790 | MV/LV Substation WO***790 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 8.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E16 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7673 | -9.5555
081118X | MV/LV Substation CL***118X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =132 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3449 | -6.3669
041210 | MV/LV Substation BA***210 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | E18 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6699 | -8.9565
068587X | MV/LV Substation SO***587X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.47 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3383 | -6.2794
2534025 | MV/LV Substation DU***4025 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E21 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6192 | -8.7491
082149Z | MV/LV Substation RM***149Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7502 | -6.5619
137166X | MV/LV Substation CI***166X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.74 |  | --> | 0.598 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =557 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.4034 | -9.6188
137332X | MV/LV Substation RI***332X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 3.74 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3963 | -9.69
018353 | MV/LV Substation TA***353 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4465 | -9.5157
137497 | MV/LV Substation AR***497 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C15 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.3331 | -9.7907
0664455 | MV/LV Substation ST***4455 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E15 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4977 | -6.388
288201X | MV/LV Substation WO***201X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =378 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.25 | -6.1873
0214321 | MV/LV Substation CO***4321 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9323 | -8.4555
015982Z | MV/LV Substation CL***982Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2937 | -6.6836
117794 | MV/LV Substation QU***794 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.32 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0509 | -8.6214
345042X | MV/LV Substation BA***042X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E16 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3157 | -8.2052
2514083 | MV/LV Substation CL***4083 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C28 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.346 | -8.9476
288242X | MV/LV Substation BE***242X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.16 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2773 | -6.2154
001226 | MV/LV Substation JO***226 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.482 | 13.42 |  | --> | 0.598 | 0 | 0.071 | 0.5 | 0 |  | --> | C20 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2677 | -6.1467
081575X | MV/LV Substation MO***575X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 7.91 |  | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C26 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3787 | -6.3515
011973Y | MV/LV Substation LA***973Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.037 | 0.04 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C16 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5365 | -7.2317
266567 | MV/LV Substation CO***567 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2628 | -7.2729
012407Y | MV/LV Substation EI***407Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =112 kVA | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =140 kW | --> | C23 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8297 | -6.9166
016173Z | MV/LV Substation HI***173Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4218 | -6.4797
281606Z | MV/LV Substation BU***606Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0.018 | 0.5 | 0 |  | --> | C26 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8962 | -8.4087
137281 | MV/LV Substation KI***281 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.186 | 3.74 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3496 | -9.6246
0324040 | MV/LV Substation IC***4040 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1723 | -7.2609
068345X | MV/LV Substation BE***345X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =544 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3526 | -6.2499
125885X | MV/LV Substation BA***885X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.256 | -8.4634
0824387 | MV/LV Substation BA***4387 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.01 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6533 | -6.7018
368270X | MV/LV Substation WE***270X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7502 | -8.7714
082778Y | MV/LV Substation KE***778Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =468 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =576 kW | --> | C26 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6535 | -6.686
180482X | MV/LV Substation DR***482X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 1.4 |  | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C23 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7251 | -6.9413
062196 | MV/LV Substation CO***196 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 19.76 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | E19 ex MULLAGHARLIN | Mullagharlin [T121,T122] | MULLAGHARLIN |  | 53.9419 | -6.4887
429364 | MV/LV Substation CO***364 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.4348 | -9.2557
054548Y | MV/LV Substation GR***548Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =159 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0403 | -7.306
065405Z | MV/LV Substation BR***405Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =464 kVA | --> | 0.598 | 0 | 0.022 | 0.5 | 0 |  | --> | C22 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6122 | -6.21
046087 | MV/LV Substation AV***087 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.19 | 0 | 0 | 0.175 | 0 |  | --> | C15 ex FINISKLIN | Finisklin [T41,T42] | SLIGO |  | 54.2775 | -8.498
003958X | MV/LV Substation BR***958X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 11.58 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9903 | -6.0775
061281X | MV/LV Substation CA***281X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.0816 | -6.9176
122572 | MV/LV Substation NO***572 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 4.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8241 | -6.7518
031457X | MV/LV Substation BA***457X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0512 | -7.6447
350050 | MV/LV Substation DR***050 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 1.57 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4806 | -8.2677
018318Z | MV/LV Substation IN***318Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 3.75 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C13 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4513 | -9.4904
001208X | MV/LV Substation TH***208X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0.005 | 0.371 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2391 | -6.1314
288357X | MV/LV Substation MO***357X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.04 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2041 | -6.1824
021013Z | MV/LV Substation TO***013Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | E18 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9221 | -8.6078
099221X | MV/LV Substation WI***221X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 5.45 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9666 | -7.7582
034091 | MV/LV Substation MO***091 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 0.57 |  | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | E23 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3493 | -7.744
209144 | MV/LV Substation OI***144 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0407 | -7.6576
068401 | MV/LV Substation FI***401 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.98 |  | --> | 0.95 | 0 | 0.007 | 0.5 | 0 |  | --> | C22 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3347 | -6.2514
127201Y | MV/LV Substation TR***201Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =548 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C18 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6867 | -7.8269
011718Z | MV/LV Substation FR***718Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.037 | 0.04 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C11 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5495 | -7.3779
081214Z | MV/LV Substation MI***214Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.009 | 0.357 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3252 | -6.4009
109442 | MV/LV Substation AE***442 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =540 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex SHANNON | Shannon [T41,T42] | DRUMLINE |  | 52.7041 | -8.8945
345024X | MV/LV Substation ME***024X |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =909 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3082 | -8.1733
160015Y | MV/LV Substation ST***015Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.0662 | -7.2645
156400X | MV/LV Substation DR***400X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3696 | -6.9364
067086 | MV/LV Substation ME***086 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =341 kW | --> | C18 ex CORBALLY | Corbally [T41,T42] | ARDNACRUSHA |  | 52.6854 | -8.6238
111598Z | MV/LV Substation WE***598Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.104 | 0.94 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E15 ex CASTLETOWNBERE | Castletownbere [T421] | BALLYLICKY |  | 51.6484 | -9.9151
075433Y | MV/LV Substation KI***433Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 4.38 |  | --> | 0.19 | 0 | 0.007 | 0.181 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.5126 | -6.2858
154574 | MV/LV Substation RI***574 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =125 kVA | --> | 0.19 | 0 | 0.01 | 0.172 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3862 | -6.3711
160093Y | MV/LV Substation AV***093Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1233 | -7.3515
0564183 | MV/LV Substation CL***4183 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 0.89 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0004 | -8.0787
288018 | MV/LV Substation SA***018 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.037 | 0.343 | 0 |  | --> | C12 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2677 | -6.2209
015931X | MV/LV Substation MO***931X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =353 kVA | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =337 kW | --> | C12 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2337 | -6.621
007741Y | MV/LV Substation KI***741Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 16.12 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3606 | -6.5091
052954Y | MV/LV Substation AS***954Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.263 | 10.9 |  | --> | 0.38 | 0 | 0.048 | 0.325 | 0 |  | --> | C14 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5303 | -7.3547
288741 | MV/LV Substation KI***741 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.36 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C11 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1871 | -6.1551
345079X | MV/LV Substation CL***079X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3073 | -8.171
248876X | MV/LV Substation CL***876X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4551 | -6.6723
068376 | MV/LV Substation BR***376 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 11.14 |  | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C14 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3704 | -6.2924
030003 | MV/LV Substation TO***003 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9517 | -7.8486
0154137 | MV/LV Substation TH***4137 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =217 kVA | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C19 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2878 | -6.7553
0244006 | MV/LV Substation BA***4006 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 2.14 |  | --> | 0.048 | 0 | 0.041 | 0 | 0 | Constrained, otherwise capacity available =10 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.1986 | -8.5237
206516 | MV/LV Substation EA***516 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 2.76 |  | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | E12 ex BANGOR ERRIS | Bangor Erris [T421] | BELLACORICK |  | 54.0747 | -9.9255
248696X | MV/LV Substation BR***696X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3999 | -6.6781
244546X | MV/LV Substation IV***546X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1065 | -9.7937
065093Z | MV/LV Substation SA***093Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.521 | -6.0986
0694158 | MV/LV Substation BR***4158 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.91 |  | --> | 0.95 | 0 | 0.009 | 0.5 | 0 |  | --> | C11 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3298 | -6.304
2074085 | MV/LV Substation NU***4085 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =593 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C14 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7162 | -7.5895
005892X | MV/LV Substation TI***892X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.7129 | -6.2667
184220X | MV/LV Substation AL***220X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 3.38 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C20 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1162 | -6.734
054588Y | MV/LV Substation LA***588Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | E19 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0204 | -7.2716
039083X | MV/LV Substation TR***083X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 11.03 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2551 | -9.1525
266063X | MV/LV Substation BU***063X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3222 | -7.1827
081006Z | MV/LV Substation PA***006Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =280 kVA | --> | 0.38 | 0 | 0 | 0.363 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3337 | -6.3667
084580 | MV/LV Substation KI***580 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.2222 | -8.8601
139092Y | MV/LV Substation CL***092Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8667 | -7.5469
081432X | MV/LV Substation FO***432X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =257 kVA | --> | 0.38 | 0 | 0.005 | 0.356 | 0 |  | --> | C14 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3396 | -6.4097
151767X | MV/LV Substation SK***767X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex BRUFF | Bruff [T42,T421] | LIMERICK |  | 52.5512 | -8.5623
064119Z | MV/LV Substation ST***119Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | C20 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7161 | -6.3498
081260Z | MV/LV Substation FI***260Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C13 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3444 | -6.446
0934162 | MV/LV Substation CA***4162 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =562 kVA | --> | 0.598 | 0 | 0.059 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4104 | -6.1796
066871 | MV/LV Substation CO***871 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4565 | -6.3477
3654174 | MV/LV Substation PA***4174 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2867 | -6.4374
068500X | MV/LV Substation LO***500X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.48 | 1.47 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3384 | -6.2872
2814157 | MV/LV Substation AL***4157 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.67 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8977 | -8.4633
162003 | MV/LV Substation TO***003 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 7.25 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C12 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8624 | -7.6695
052058 | MV/LV Substation BE***058 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.19 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =142 kW | --> | C17 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5273 | -7.3229
120516Y | MV/LV Substation DE***516Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E18 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3351 | -7.0403
522020 | MV/LV Substation ST***020 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C16 ex MEELICK |  |  |  | 53.0192 | -7.2975
249673 | MV/LV Substation RE***673 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C22 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1753 | -8.0073
0644449 | MV/LV Substation GO***4449 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =601 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C11 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.725 | -6.3942
046589 | MV/LV Substation LA***589 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2494 | -8.4391
064517 | MV/LV Substation HA***517 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E15 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6309 | -6.2616
048015 | MV/LV Substation ST***015 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 2.03 |  | --> | 0.19 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =146 kW | --> | E17 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9196 | -7.8619
281641Z | MV/LV Substation ST***641Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.333 | 4.3 |  | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C11 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8715 | -8.3352
281763X | MV/LV Substation DE***763X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.09 | 7.88 |  | --> | 0.19 | 0 | 0.02 | 0.16 | 0 |  | --> | C17 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8886 | -8.4785
2074016 | MV/LV Substation BA***4016 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.6135 | -7.6038
006726 | MV/LV Substation KI***726 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 4.38 |  | --> | 0.048 | 0 | 0.025 | 0.028 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.4542 | -6.339
293186 | MV/LV Substation GO***186 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7957 | -6.7347
003450Y | MV/LV Substation TH***450Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 11.58 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9874 | -6.0726
288143 | MV/LV Substation BR***143 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0.043 | 0.335 | 0 |  | --> | C14 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2759 | -6.2592
033953X | MV/LV Substation CA***953X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.5096 | -7.5037
007856Z | MV/LV Substation LU***856Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =349 kVA | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3236 | -6.4763
118577 | MV/LV Substation TA***577 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3349 | -8.2038
007147X | MV/LV Substation CL***147X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.304 | 16.12 |  | --> | 0.38 | 0 | 0.005 | 0.363 | 0 |  | --> | E14 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3322 | -6.497
026097 | MV/LV Substation TR***097 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =441 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =568 kW | --> | E41 ex KINSALE | Kinsale [T423] | TRABEG |  | 51.701 | -8.5187
005824X | MV/LV Substation KI***824X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.7079 | -6.2107
058204X | MV/LV Substation CL***204X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C26 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.947 | -8.2298
1544150 | MV/LV Substation CL***4150 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =288 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =921 kW | --> | C18 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4065 | -6.3712
011607Y | MV/LV Substation IR***607Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.8 |  | --> | 0.95 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =929 kW | --> | C18 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6448 | -7.2102
050046X | MV/LV Substation GO***046X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.109 | 7.61 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C11 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4161 | -7.9267
255865 | MV/LV Substation WO***865 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6538 | -8.4267
0394183 | MV/LV Substation WE***4183 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.181 | 11.03 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C34 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2772 | -9.0754
048046X | MV/LV Substation GR***046X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9245 | -7.8657
026708Y | MV/LV Substation HA***708Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7021 | -8.4983
068871 | MV/LV Substation PE***871 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 2.6 |  | --> | 0.38 | 0 | 0.001 | 0.374 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3461 | -6.2479
249745 | MV/LV Substation SH***745 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1269 | -8.0783
007613 | MV/LV Substation CR***613 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.054 | 1.4 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.1763 | -6.5879
288224X | MV/LV Substation TO***224X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2867 | -6.2403
009208Y | MV/LV Substation CO***208Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.094 | 8.16 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C12 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2647 | -7.0986
160875X | MV/LV Substation TH***875X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.12 |  | --> | 0.048 | 0 | 0.004 | 0.044 | 0 |  | --> | E64 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0855 | -7.0878
052594Z | MV/LV Substation CR***594Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.4478 | -7.5743
039060 | MV/LV Substation CL***060 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.45 |  | --> | 0.598 | 0 | 0.043 | 0.5 | 0 |  | --> | C17 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2667 | -9.0595
017323 | MV/LV Substation KI***323 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.98 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E11 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5856 | -8.9356
0524589 | MV/LV Substation BA***4589 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.6319 | -7.2148
009272Y | MV/LV Substation TE***272Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.241 | -7.1328
067013 | MV/LV Substation CO***013 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.494 | 13.8 |  | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C17 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6712 | -8.5794
055436Y | MV/LV Substation CH***436Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C17 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7962 | -7.8274
089294X | MV/LV Substation GA***294X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.1 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C14 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1143 | -9.1577
0824446 | MV/LV Substation WO***4446 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =566 kVA | --> | 0.598 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C30 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6499 | -6.6531
043016X | MV/LV Substation DO***016X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 54.0109 | -8.9787
1204422 | MV/LV Substation BA***4422 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.5 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E12 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4149 | -6.8158
2814311 | MV/LV Substation ME***4311 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.396 | 5.49 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8612 | -8.4561
249534 | MV/LV Substation BA***534 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C25 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.2133 | -7.7358
082077 | MV/LV Substation TR***077 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.319 | 2.01 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | C15 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6519 | -6.6856
063783X | MV/LV Substation MC***783X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8336 | -6.6405
068822X | MV/LV Substation CO***822X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.471 | 7.61 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex SHERIFF STREET | Sheriff Street [T41,T42] | FRANCIS STREET |  | 53.3534 | -6.2446
119900 | MV/LV Substation AV***900 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =576 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =591 kW | --> | C15 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1455 | -8.8446
255443 | MV/LV Substation WO***443 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6524 | -8.2674
068619 | MV/LV Substation GR***619 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0.043 | 0.334 | 0 |  | --> | C14 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3777 | -6.2356
018819 | MV/LV Substation LA***819 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.339 | 3.75 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C13 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4504 | -9.4855
029697 | MV/LV Substation BL***697 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0 | 0.089 | 0 |  | --> | C13 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9349 | -8.1629
116053 | MV/LV Substation TH***053 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 7.32 |  | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7953 | -9.5247
024845 | MV/LV Substation MO***845 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.057 | 2.14 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C18 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.1752 | -8.7213
081477Z | MV/LV Substation CU***477Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0.08 | 0.5 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3297 | -6.3744
116324 | MV/LV Substation TR***324 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 8.1 |  | --> | 0.598 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | E11 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7623 | -9.8065
067035 | MV/LV Substation NE***035 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 13.8 |  | --> | 0.095 | 0 | 0.035 | 0.065 | 0 |  | --> | C18 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6661 | -8.5607
0144408 | MV/LV Substation HO***4408 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1749 | -6.7976
0814244 | MV/LV Substation AR***4244 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.321 | -6.5897
064791Y | MV/LV Substation RA***791Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.6672 | -6.511
034089 | MV/LV Substation K***089 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E25 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3634 | -7.6704
204359X | MV/LV Substation SA***359X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1549 | -7.3831
0684594 | MV/LV Substation TE***4594 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3546 | -6.2586
019084 | MV/LV Substation AB***084 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.252 | 2.18 |  | --> | 0.38 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C19 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2709 | -9.7045
0294271 | MV/LV Substation SE***4271 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8547 | -8.0282
067179 | MV/LV Substation RO***179 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0.047 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C18 ex CORBALLY | Corbally [T41,T42] | ARDNACRUSHA |  | 52.6761 | -8.6114
293192Y | MV/LV Substation TI***192Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 53.0025 | -6.8068
082823Y | MV/LV Substation CR***823Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 2.01 |  | --> | 0.38 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =296 kW | --> | C11 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.643 | -6.7084
007810X | MV/LV Substation JO***810X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.176 | 0.9 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.2985 | -6.5053
069215 | MV/LV Substation VI***215 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.402 | 2.93 |  | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C11 ex DODDER ROAD | Dodder Road [T42] | MILLTOWN (DR) |  | 53.3084 | -6.2749
127172Z | MV/LV Substation LO***172Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 5.89 |  | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5663 | -7.8928
030224X | MV/LV Substation YO***224X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =266 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.936 | -7.859
055132Y | MV/LV Substation FA***132Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9673 | -7.839
0014182 | MV/LV Substation FO***4182 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.16 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.317 | -6.2087
156877 | MV/LV Substation MA***877 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C17 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.2166 | -7.1116
049175Z | MV/LV Substation MA***175Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.133 | 0.13 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C18 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5658 | -7.7638
156250X | MV/LV Substation D/***250X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.071 | 2.47 |  | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2828 | -7.0623
2884130 | MV/LV Substation WA***4130 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.281 | -6.2407
216540 | MV/LV Substation MO***540 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C23 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7563 | -8.4112
119696X | MV/LV Substation PO***696X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1371 | -8.8764
0324049 | MV/LV Substation BA***4049 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1922 | -7.1202
1274464 | MV/LV Substation DO***4464 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5265 | -7.8502
025583 | MV/LV Substation TH***583 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 1.93 |  | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C17 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.3467 | -8.9705
162041X | MV/LV Substation MC***041X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 0.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.7968 | -7.5583
1504171 | MV/LV Substation TR***4171 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.373 | 3.96 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | E20 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7945 | -7.7853
122693 | MV/LV Substation MO***693 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 4.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9009 | -6.8077
281752X | MV/LV Substation ID***752X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8295 | -8.3504
0294280 | MV/LV Substation GL***4280 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.31 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E13 ex AGHADA | Aghada [T721] | N/A |  | 51.8158 | -8.2531
043321 | MV/LV Substation BO***321 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C13 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9019 | -9.0139
081089Z | MV/LV Substation GR***089Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3235 | -6.4299
069446 | MV/LV Substation KI***446 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.333 | 9.99 |  | --> | 0.598 | 0 | 0.016 | 0.5 | 0 |  | --> | C21 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3244 | -6.2967
001028X | MV/LV Substation ST***028X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.285 | 13.42 |  | --> | 0.38 | 0 | 0.005 | 0.36 | 0 |  | --> | C20 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2645 | -6.1499
019409 | MV/LV Substation FO***409 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.011 | 0.05 |  | --> | 0.048 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =24 kW | --> | C14 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2883 | -9.6779
068372 | MV/LV Substation BL***372 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.339 | 9.99 |  | --> | 0.598 | 0 | 0.026 | 0.5 | 0 |  | --> | C23 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3318 | -6.2719
167194Z | MV/LV Substation OW***194Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | E12 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 52.0398 | -8.4253
253569Z | MV/LV Substation KE***569Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4221 | -9.1071
026665X | MV/LV Substation KI***665X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 8.66 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.797 | -8.7929
2884076 | MV/LV Substation ON***4076 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.364 | 15.18 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2722 | -6.1999
120661Y | MV/LV Substation CO***661Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2565 | -6.8526
461244 | MV/LV Substation RE***244 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0854 | -9.1684
017027Y | MV/LV Substation C.***027Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.05 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4299 | -9.0135
0934007 | MV/LV Substation TU***4007 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4085 | -6.2289
023754X | MV/LV Substation W ***754X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =550 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1402 | -8.2607
1844095 | MV/LV Substation RA***4095 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 3.38 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C20 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1187 | -6.749
026196Z | MV/LV Substation KN***196Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 8.66 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7458 | -8.6524
164126X | MV/LV Substation FA***126X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =529 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5486 | -9.2563
0934277 | MV/LV Substation HI***4277 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C13 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4285 | -6.3026
130926 | MV/LV Substation CR***926 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.7148 | -7.5829
2934434 | MV/LV Substation BA***4434 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8376 | -6.6615
066250X | MV/LV Substation MO***250X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =417 kVA | --> | 0.598 | 0 | 0.045 | 0.5 | 0 |  | --> | C13 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3928 | -6.1272
293258Y | MV/LV Substation TU***258Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8037 | -6.7033
067259 | MV/LV Substation RO***259 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =386 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C20 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.648 | -8.6201
005011 | MV/LV Substation ST***011 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =327 kW | --> | C15 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6753 | -6.2891
093033Z | MV/LV Substation CO***033Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0 | 0.36 | 0 |  | --> | C14 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.378 | -6.2879
122985 | MV/LV Substation FA***985 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 4.18 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9033 | -6.8103
064858 | MV/LV Substation BA***858 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C20 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7415 | -6.2778
108955 | MV/LV Substation DO***955 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5068 | -8.1881
070145 | MV/LV Substation DR***145 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.24 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E11 ex CLOONBANNIN | Cloonbannin [T421] | GLENLARA |  | 52.0687 | -9.0472
1964142 | MV/LV Substation PO***4142 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5532 | -6.7831
066818 | MV/LV Substation RA***818 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E21 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5257 | -6.4114
012939 | MV/LV Substation EA***939 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.139 | 2.83 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E11 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.702 | -6.9745
021212 | MV/LV Substation KI***212 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 6.78 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C16 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.91 | -8.3632
220134X | MV/LV Substation AS***134X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1951 | -9.2047
099485X | MV/LV Substation DR***485X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9454 | -7.6934
039152X | MV/LV Substation FO***152X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 11.03 |  | --> | 0.095 | 0 | 0.005 | 0.087 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2493 | -9.2038
144879 | MV/LV Substation FA***879 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.8669 | -7.1282
012029Y | MV/LV Substation CA***029Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =373 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.841 | -6.9232
127509Y | MV/LV Substation GE***509Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =554 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.5867 | -7.8216
149112X | MV/LV Substation AR***112X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6527 | -8.1001
1094007 | MV/LV Substation GL***4007 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 0.38 | Constrained, otherwise capacity available =385 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7008 | -8.8842
020491 | MV/LV Substation FO***491 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C18 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0709 | -9.5892
003585Y | MV/LV Substation GR***585Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 18.08 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C18 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8895 | -6.162
009236Y | MV/LV Substation OZ***236Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.53 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | C14 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2502 | -7.1123
118173 | MV/LV Substation LA***173 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 0.3 |  | --> | 0.048 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | C17 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.241 | -8.1717
026909Y | MV/LV Substation KN***909Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex KINSALE |  |  |  | 51.725 | -8.5273
071575 | MV/LV Substation KI***575 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 5.58 |  | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1024 | -6.0495
0014127 | MV/LV Substation OU***4127 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2549 | -6.1514
059406Y | MV/LV Substation RE***406Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E11 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.1002 | -7.3242
0594294 | MV/LV Substation BO***4294 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =370 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =568 kW | --> | C11 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9575 | -7.3769
1494116 | MV/LV Substation PC***4116 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6603 | -8.091
014677X | MV/LV Substation BA***677X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0 | 0.181 | 0 |  | --> | C12 ex ATHY | Athy [T101,T102] | ATHY |  | 53.009 | -6.815
0894136 | MV/LV Substation DU***4136 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E22 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2843 | -8.9676
081266Y | MV/LV Substation BA***266Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C15 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.335 | -6.572
007757Z | MV/LV Substation KI***757Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 1.4 |  | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E12 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2393 | -6.3587
495800 | MV/LV Substation KE***800 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.089 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.975 | -10.0855
127326 | MV/LV Substation CL***326 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6953 | -7.7146
042259 | MV/LV Substation WA***259 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C13 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8409 | -9.2926
003788X | MV/LV Substation IN***788X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0183 | -6.1032
061588 | MV/LV Substation BA***588 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.159 | 2.04 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C14 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1278 | -6.9058
139805Y | MV/LV Substation WE***805Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E18 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7739 | -7.2991
012790X | MV/LV Substation MO***790X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.167 | 1.99 |  | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C20 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8363 | -6.9458
158586X | MV/LV Substation GA***586X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C19 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 53.1166 | -9.1483
276002 | MV/LV Substation PA***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =550 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C11 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.06 | -9.4888
0054017 | MV/LV Substation HU***4017 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =510 kVA | --> | 0.598 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6816 | -6.3026
012571X | MV/LV Substation CO***571X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7855 | -7.0694
036741X | MV/LV Substation BL***741X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E16 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4764 | -8.1435
081566X | MV/LV Substation LA***566X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.38 | 0 | 0.007 | 0.341 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3433 | -6.3556
249319 | MV/LV Substation SH***319 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1258 | -8.0768
046068 | MV/LV Substation SL***068 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.406 | 5.78 |  | --> | 0.598 | 0 | 0.021 | 0.5 | 0 |  | --> | C11 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2549 | -8.4715
021987X | MV/LV Substation HO***987X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =283 kVA | --> | 0.38 | 0 | 0 | 0.364 | 0 |  | --> | C25 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9035 | -8.5081
127484Y | MV/LV Substation CA***484Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C17 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.7477 | -7.9463
041085Y | MV/LV Substation KN***085Y |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7981 | -8.902
0524819 | MV/LV Substation GR***4819 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.9 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5297 | -7.3569
051048 | MV/LV Substation PO***048 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.384 | 2.22 |  | --> | 0.38 | 0 | 0.14 | 0.274 | 0 |  | --> | E12 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3706 | -7.508
0174521 | MV/LV Substation RO***4521 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.58 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.5714 | -9.1065
003826 | MV/LV Substation RO***826 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 11.58 |  | --> | 0.048 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =21 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0019 | -6.0988
037049 | MV/LV Substation AU***049 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C19 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8652 | -8.9824
068026X | MV/LV Substation CA***026X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.041 | 28.43 |  | --> | 0.38 | 0 | 0 | 0.328 | 0 |  | --> | C10 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3435 | -6.2692
021009X | MV/LV Substation JA***009X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =234 kVA | --> | 0.38 | 0 | 0.015 | 0.346 | 0 |  | --> | C14 ex FAIRHILL | Fairhill [T42] | KILBARRY |  | 51.8996 | -8.4919
068989 | MV/LV Substation SO***989 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 1.86 |  | --> | 0.38 | 0 | 0.017 | 0.357 | 0 |  | --> | C12 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3604 | -6.1996
069882 | MV/LV Substation OL***882 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C34 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3298 | -6.3398
238050Y | MV/LV Substation BA***050Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6373 | -9.1697
082141Z | MV/LV Substation KE***141Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C30 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6479 | -6.6536
013597Y | MV/LV Substation GR***597Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.121 | 0.12 | Constrained, otherwise capacity available =384 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9911 | -6.9885
120953 | MV/LV Substation AL***953 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2886 | -6.8737
130296X | MV/LV Substation CA***296X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7888 | -7.4802
064066 | MV/LV Substation GE***066 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =319 kW | --> | C11 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7194 | -6.358
014069X | MV/LV Substation KI***069X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =29 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1529 | -6.8928
253133X | MV/LV Substation GO***133X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.5971 | -8.5663
258013X | MV/LV Substation BA***013X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.86 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.1517 | -7.8707
1394186 | MV/LV Substation QU***4186 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =413 kVA | --> | 0.598 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =507 kW | --> | E18 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7807 | -7.3873
071129 | MV/LV Substation CR***129 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.042 | 5.58 |  | --> | 0.38 | 0 | 0.025 | 0.316 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1007 | -6.0674
067591Y | MV/LV Substation IP***591Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C20 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6505 | -8.6663
116994 | MV/LV Substation NO***994 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 8.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E11 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7556 | -9.8136
0664316 | MV/LV Substation CH***4316 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 12.96 |  | --> | 0.95 | 0 | 0.006 | 0.5 | 0 |  | --> | C28 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3871 | -6.2015
068425 | MV/LV Substation CL***425 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C16 ex DRUMCONDRA | Drumcondra [T41,T42] | MCDERMOTT |  | 53.3649 | -6.2534
065692 | MV/LV Substation KN***692 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E15 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6267 | -6.2228
1544128 | MV/LV Substation PA***4128 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4051 | -6.3987
461995 | MV/LV Substation BI***995 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.123 | 0.74 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C15 ex RAHANS | Rahans [T41] | MOY |  | 54.0834 | -9.1623
078001 | MV/LV Substation BA***001 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C12 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9622 | -8.7947
305299 | MV/LV Substation AT***299 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 4.61 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E12 ex LUMCLOON | Lumcloon [T421,T422] | DALLOW |  | 53.2752 | -7.8269
0594252 | MV/LV Substation SH***4252 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9177 | -7.393
036050 | MV/LV Substation KI***050 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.76 |  | --> | 0.598 | 0 | 0.047 | 0 | 0 | Constrained, otherwise capacity available =550 kW | --> | C16 ex KILROSS ROAD | Kilross Road [T42] | TIPPERARY |  | 52.4727 | -8.1668
093465Z | MV/LV Substation CL***465Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =931 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =940 kW | --> | C15 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.4046 | -6.2223
068018X | MV/LV Substation AR***018X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =530 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3405 | -6.2728
116305Y | MV/LV Substation RI***305Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 8.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7615 | -9.8079
017073 | MV/LV Substation CA***073 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 1.05 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C16 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4937 | -9.1476
048851 | MV/LV Substation FE***851 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.03 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 54.0158 | -7.8358
009730Y | MV/LV Substation RA***730Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.53 | Constrained, otherwise capacity available =836 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =927 kW | --> | C14 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2551 | -7.1115
0664220 | MV/LV Substation ST***4220 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =222 kVA | --> | 0.38 | 0 | 0.054 | 0 | 0 | Constrained, otherwise capacity available =315 kW | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4173 | -6.1482
1604083 | MV/LV Substation GR***4083 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.1296 | -7.1578
089021X | MV/LV Substation TH***021X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 3.56 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E20 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2127 | -9.0857
053381 | MV/LV Substation GL***381 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 3.28 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C23 ex SRAH | Srah [T43] | THORNSBERRY |  | 53.2854 | -7.4816
015036Z | MV/LV Substation AY***036Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 12.6 |  | --> | 0.19 | 0 | 0.025 | 0.162 | 0 |  | --> | C20 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2361 | -6.65
117279Y | MV/LV Substation OB***279Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.32 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0497 | -8.6047
365013Y | MV/LV Substation CO***013Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =551 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3134 | -6.5109
138807 | MV/LV Substation TU***807 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.18 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | C18 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.8801 | -6.9709
281912X | MV/LV Substation RO***912X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 10.79 |  | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C12 ex FACTORY CROSS | Factory Cross [T41,T42] | BARNAHELY |  | 51.8313 | -8.3113
248641X | MV/LV Substation RA***641X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3338 | -6.6895
066150Z | MV/LV Substation BO***150Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E17 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4458 | -6.2333
068623X | MV/LV Substation MO***623X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.14 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3722 | -6.2951
365947X | MV/LV Substation FA***947X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =423 kVA | --> | 0.598 | 0 | 0.04 | 0.5 | 0 |  | --> | C12 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3073 | -6.3501
127517X | MV/LV Substation ST***517X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5178 | -7.8842
014030 | MV/LV Substation CO***030 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C17 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1759 | -6.7956
0814138 | MV/LV Substation RO***4138 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3446 | -6.3945
136698Y | MV/LV Substation LA***698Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C13 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6324 | -8.1836
0824408 | MV/LV Substation BA***4408 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =525 kVA | --> | 0.598 | 0 | 0.153 | 0 | 0 | Constrained, otherwise capacity available =471 kW | --> | E15 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6426 | -6.6761
176423 | MV/LV Substation SH***423 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E12 ex MACROOM | Macroom [T422] | MACROOM |  | 51.929 | -8.9167
021192 | MV/LV Substation WE***192 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.078 | 4.67 |  | --> | 0.38 | 0 | 0.003 | 0.331 | 0 |  | --> | C17 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.9022 | -8.4653
127372 | MV/LV Substation CA***372 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6698 | -7.8203
019391 | MV/LV Substation WO***391 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.125 | 2.18 |  | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C11 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2796 | -9.7012
253887Y | MV/LV Substation TO***887Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6599 | -8.6953
011322X | MV/LV Substation PA***322X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.326 | 2.8 |  | --> | 0.38 | 0 | 0.063 | 0 | 0 | Constrained, otherwise capacity available =323 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6386 | -7.2437
160936Y | MV/LV Substation SL***936Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1697 | -7.1869
007849Z | MV/LV Substation BA***849Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.9 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.2932 | -6.4723
0294346 | MV/LV Substation BA***4346 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8669 | -8.0183
0654097 | MV/LV Substation GA***4097 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5659 | -6.4558
0534309 | MV/LV Substation BA***4309 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.2226 | -7.3139
1544206 | MV/LV Substation PA***4206 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =896 kVA | --> | 0.95 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =922 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3877 | -6.4401
093294X | MV/LV Substation TH***294X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.38 | 0 | 0.01 | 0.364 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3756 | -6.1635
204298 | MV/LV Substation LI***298 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.426 | 2.02 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =570 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.1111 | -7.4632
067683Y | MV/LV Substation SH***683Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.039 | 6.81 |  | --> | 0.095 | 0 | 0 | 0.086 | 0 |  | --> | C06 ex AHANE | Ahane [T102] | AHANE |  | 52.7078 | -8.429
154437Z | MV/LV Substation PA***437Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0 | 0.362 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3958 | -6.439
081556X | MV/LV Substation CA***556X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.017 | 0.17 | 0 |  | --> | C15 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3501 | -6.4472
065072 | MV/LV Substation LA***072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C21 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6148 | -6.1871
082896Y | MV/LV Substation ME***896Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6107 | -6.7978
026946 | MV/LV Substation BA***946 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.6715 | -8.6087
039448X | MV/LV Substation CA***448X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.136 | 11.03 |  | --> | 0.19 | 0 | 0.016 | 0.169 | 0 |  | --> | C22 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.275 | -9.1072
281268 | MV/LV Substation BA***268 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.005 | 0.364 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8662 | -8.5991
0684604 | MV/LV Substation ST***4604 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3312 | -6.2863
012791 | MV/LV Substation SP***791 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 1.99 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C11 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8337 | -6.9423
001687 | MV/LV Substation CH***687 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =518 kVA | --> | 0.598 | 0 | 0.031 | 0.5 | 0 |  | --> | C12 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2475 | -6.1333
244353 | MV/LV Substation TI***353 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1204 | -9.7522
066520Z | MV/LV Substation WI***520Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =535 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.474 | -6.2324
368340X | MV/LV Substation GO***340X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7645 | -8.7963
0734153 | MV/LV Substation PR***4153 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C16 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.3935 | -7.7061
0604162 | MV/LV Substation DR***4162 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.57 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.1078 | -7.14
031058 | MV/LV Substation MC***058 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =296 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C14 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.093 | -7.6073
099388X | MV/LV Substation HO***388X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.96 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 55.0008 | -7.6623
046175X | MV/LV Substation JF***175X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2711 | -8.4689
032072 | MV/LV Substation RI***072 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =576 kVA | --> | 0.598 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C16 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1639 | -7.1408
053729Y | MV/LV Substation ES***729Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.068 | 2.39 |  | --> | 0.19 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =148 kW | --> | C12 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2933 | -7.4973
160487Y | MV/LV Substation BE***487Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =629 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1437 | -7.0679
1524088 | MV/LV Substation LI***4088 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.599 | -8.2315
069494 | MV/LV Substation SE***494 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =250 kVA | --> | 0.38 | 0 | 0.019 | 0.345 | 0 |  | --> | C17 ex DONNYBROOK | Donnybrook [T41,T42] | MILLTOWN (DR) |  | 53.3234 | -6.2071
082581X | MV/LV Substation KE***581X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6179 | -6.6698
004723 | MV/LV Substation KI***723 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =351 kVA | --> | 0.38 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C23 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7319 | -6.2868
153918 | MV/LV Substation NE***918 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | E11 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7134 | -8.3986
099070 | MV/LV Substation RE***070 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =159 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9352 | -7.6268
081596Z | MV/LV Substation HA***596Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =473 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.355 | -6.4073
009384 | MV/LV Substation BA***384 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 8.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.3323 | -7.0645
054013 | MV/LV Substation BA***013 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.095 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =66 kW | --> | E14 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.8744 | -7.3114
011789Z | MV/LV Substation PL***789Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6692 | -7.2297
015260Z | MV/LV Substation ME***260Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C15 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2319 | -6.6417
1564345 | MV/LV Substation LA***4345 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2363 | -6.8835
0664061 | MV/LV Substation FE***4061 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4454 | -6.2013
068837X | MV/LV Substation CL***837X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.366 | 1.47 |  | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | C15 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.338 | -6.292
196018X | MV/LV Substation HA***018X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C18 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5592 | -6.7799
034745X | MV/LV Substation BA***745X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 5.88 |  | --> | 0.095 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =66 kW | --> | C14 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.5369 | -7.6272
365054X | MV/LV Substation SM***054X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.006 | 0.358 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3302 | -6.3454
039315 | MV/LV Substation MO***315 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.19 | 0 | 0.005 | 0.162 | 0 |  | --> | C29 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2835 | -9.0337
015084 | MV/LV Substation CA***084 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E17 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.0937 | -6.5161
127072 | MV/LV Substation DW***072 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =619 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C17 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6868 | -7.8129
090459 | MV/LV Substation DE***459 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 3.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C20 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7202 | -8.922
137278X | MV/LV Substation MC***278X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.4587 | -9.7136
050203X | MV/LV Substation GL***203X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 6.49 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4724 | -7.8647
047286 | MV/LV Substation DE***286 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.04 |  | --> | 0.048 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.982 | -8.2958
281418X | MV/LV Substation CI***418X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =103 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C17 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8708 | -8.4816
180033 | MV/LV Substation SO***033 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.27 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C12 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7288 | -6.8879
001050X | MV/LV Substation BO***050X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.046 | 13.42 |  | --> | 0.19 | 0 | 0.006 | 0.163 | 0 |  | --> | C21 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2599 | -6.1476
066715Z | MV/LV Substation CA***715Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =382 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4154 | -6.2416
158330Y | MV/LV Substation SE***330Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8054 | -9.4826
093439Z | MV/LV Substation TH***439Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =549 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3764 | -6.1666
033066 | MV/LV Substation CA***066 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C15 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.34 | -7.4089
037861X | MV/LV Substation SH***861X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =147 kVA | --> | 0.19 | 0 | 0.041 | 0 | 0 | Constrained, otherwise capacity available =152 kW | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8495 | -9.0128
281324Z | MV/LV Substation SO***324Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.78 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8878 | -8.4034
011029 | MV/LV Substation VH***029 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.136 | 2.8 |  | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =328 kW | --> | C18 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.646 | -7.2146
127029Y | MV/LV Substation CL***029Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5967 | -7.9666
071913 | MV/LV Substation TH***913 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0.02 | 0.36 | 0 |  | --> | C17 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1396 | -6.0604
021218Z | MV/LV Substation PI***218Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex FAIRHILL | Fairhill [T42] | KILBARRY |  | 51.9018 | -8.4719
248870 | MV/LV Substation HI***870 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3972 | -6.675
093383Z | MV/LV Substation TA***383Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0.004 | 0.186 | 0 |  | --> | C12 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3992 | -6.1491
120556Y | MV/LV Substation TU***556Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.2578 | -7.0823
059578Y | MV/LV Substation BU***578Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =337 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C15 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9892 | -7.3596
007852Y | MV/LV Substation TA***852Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2454 | -6.3813
001002 | MV/LV Substation ST***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.301 | 13.42 |  | --> | 0.38 | 0 | 0.021 | 0.351 | 0 |  | --> | C14 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2682 | -6.1693
1184229 | MV/LV Substation EI***4229 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =593 kW | --> | C17 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.323 | -8.2215
004062 | MV/LV Substation WO***062 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 0.45 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C12 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8303 | -6.2346
070114X | MV/LV Substation MI***114X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.283 | 0.76 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | E17 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0632 | -9.0672
1254035 | MV/LV Substation TA***4035 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2503 | -8.4637
021638Z | MV/LV Substation HE***638Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C11 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9083 | -8.4739
154532 | MV/LV Substation RA***532 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4162 | -6.4618
248250 | MV/LV Substation SP***250 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4785 | -6.7165
021247Z | MV/LV Substation MA***247Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 6.78 |  | --> | 0.38 | 0 | 0.043 | 0.333 | 0 |  | --> | C18 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9257 | -8.3831
154091Z | MV/LV Substation RE***091Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =732 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =913 kW | --> | C19 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.396 | -6.3924
281835X | MV/LV Substation LE***835X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.008 | 0.173 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8919 | -8.5837
021262X | MV/LV Substation KN***262X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =347 kW | --> | C22 ex KILBARRY |  |  |  | 51.9047 | -8.5059
014315Z | MV/LV Substation SI***315Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1821 | -6.7783
156601 | MV/LV Substation KI***601 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2812 | -7.1533
293148Y | MV/LV Substation MO***148Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E20 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9725 | -6.8178
031012 | MV/LV Substation SP***012 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0865 | -7.6384
0264349 | MV/LV Substation CU***4349 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.383 | 8.66 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C13 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7486 | -8.7568
127263X | MV/LV Substation SA***263X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.4963 | -7.817
3654077 | MV/LV Substation PO***4077 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2961 | -6.3664
054133X | MV/LV Substation GU***133X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 0.12 |  | --> | 0.095 | 0 | 0.014 | 0.08 | 0 |  | --> | C21 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0112 | -7.139
068830 | MV/LV Substation RO***830 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.14 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3757 | -6.2916
0534238 | MV/LV Substation SI***4238 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.283 | 2.39 |  | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C12 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.295 | -7.5001
038750X | MV/LV Substation GO***750X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =510 kVA | --> | 0.598 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =570 kW | --> | C16 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0635 | -8.8216
216027X | MV/LV Substation SP***027X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C26 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7973 | -8.2808
120101Y | MV/LV Substation PR***101Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =76 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3483 | -7.2044
1424029 | MV/LV Substation CU***4029 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E23 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.2716 | -8.6771
068435 | MV/LV Substation RO***435 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.358 | 11.14 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3719 | -6.2915
062107Y | MV/LV Substation CO***107Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.72 |  | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C12 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0038 | -6.3873
281128 | MV/LV Substation PE***128 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.88 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8977 | -8.4702
258556 | MV/LV Substation GL***556 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 1.86 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E18 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.0383 | -7.9648
007997 | MV/LV Substation BL***997 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2188 | -6.648
007470X | MV/LV Substation LE***470X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 0.9 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.2889 | -6.4642
075002 | MV/LV Substation BU***002 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.124 | 1.13 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E12 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6547 | -6.6492
002046X | MV/LV Substation AT***046X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.465 | 4.51 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1825 | -6.1184
017377Z | MV/LV Substation CA***377Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5144 | -8.8097
061852 | MV/LV Substation RO***852 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.072 | 2.04 |  | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C12 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1173 | -7.0143
065443Z | MV/LV Substation CO***443Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5565 | -6.4378
192456X | MV/LV Substation MU***456X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.56 |  | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0313 | -8.3708
071019 | MV/LV Substation QU***019 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0.077 | 0.299 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1383 | -6.0647
093373X | MV/LV Substation TO***373X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4029 | -6.2847
001570 | MV/LV Substation WA***570 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =217 kVA | --> | 0.38 | 0 | 0.128 | 0.259 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2598 | -6.1339
063132X | MV/LV Substation GL***132X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C18 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.9142 | -6.5309
032002 | MV/LV Substation PA***002 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =115 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2381 | -6.9735
025651Y | MV/LV Substation TH***651Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.339 | 2.96 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E14 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3574 | -8.6963
059813Y | MV/LV Substation LA***813Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9213 | -7.4236
051252 | MV/LV Substation LI***252 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 2.22 |  | --> | 0.19 | 0 | 0.005 | 0.186 | 0 |  | --> | E17 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.395 | -7.4861
0994072 | MV/LV Substation ST***4072 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C12 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9492 | -7.7117
067212Y | MV/LV Substation TH***212Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0.088 | 0 | 0 | Constrained, otherwise capacity available =296 kW | --> | C13 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6297 | -8.6664
281531 | MV/LV Substation HO***531 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.7925 | -8.3155
021662X | MV/LV Substation HA***662X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.19 | 0 | 0.02 | 0.159 | 0 |  | --> | C12 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.932 | -8.3958
021473 | MV/LV Substation BA***473 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0.014 | 0.082 | 0 |  | --> | C15 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9403 | -8.3462
144131X | MV/LV Substation TA***131X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 2.78 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7488 | -7.3984
069186 | MV/LV Substation PA***186 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C17 ex DONNYBROOK | Donnybrook [T41,T42] | MILLTOWN (DR) |  | 53.3245 | -6.2117
109423 | MV/LV Substation SH***423 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =250 kVA | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =322 kW | --> | E16 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7151 | -8.8617
293889Z | MV/LV Substation SL***889Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.389 | 0.43 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8394 | -6.7809
021164X | MV/LV Substation LI***164X |  | 10 kV | _ | LV | 100 kVA :Kiosk Substation | 0.1 | --> | 0.1 | 0.016 | 6.78 |  | --> | 0.095 | 0 | 0.04 | 0.053 | 0 |  | --> | C35 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9007 | -8.3522
1544316 | MV/LV Substation ST***4316 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =883 kVA | --> | 0.95 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =926 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3865 | -6.4396
288142 | MV/LV Substation BR***142 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =209 kVA | --> | 0.38 | 0 | 0.14 | 0.249 | 0 |  | --> | C19 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2766 | -6.2552
118210Y | MV/LV Substation LA***210Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.2357 | -8.1758
099029 | MV/LV Substation KN***029 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 5.45 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =73 kW | --> | C17 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9624 | -7.7275
059001 | MV/LV Substation FA***001 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =216 kVA | --> | 0.598 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =502 kW | --> | C15 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9899 | -7.363
049216Y | MV/LV Substation KI***216Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 1.31 |  | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7831 | -8.1035
012131Y | MV/LV Substation TH***131Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.068 | 1.99 |  | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =150 kW | --> | C18 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8436 | -6.9476
254435 | MV/LV Substation SH***435 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.5301 | -9.078
237509 | MV/LV Substation MI***509 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8826 | -6.3757
015433Z | MV/LV Substation OL***433Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =263 kVA | --> | 0.38 | 0 | 0.044 | 0 | 0 | Constrained, otherwise capacity available =328 kW | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2431 | -6.6702
064108Z | MV/LV Substation SW***108Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.713 | -6.3744
035617X | MV/LV Substation GA***617X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.287 | -7.8056
062013 | MV/LV Substation ST***013 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.348 | 5.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C19 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0091 | -6.3926
256019X | MV/LV Substation NC***019X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.28 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7694 | -8.489
062723Y | MV/LV Substation NA***723Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.158 | 3.12 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C18 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9818 | -6.3785
288175 | MV/LV Substation MU***175 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0.027 | 0.343 | 0 |  | --> | C17 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2662 | -6.2107
127201X | MV/LV Substation BA***201X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.7363 | -7.788
288299 | MV/LV Substation BA***299 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.041 | 0.04 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.032 | 0.158 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2259 | -6.1275
020650X | MV/LV Substation BR***650X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C12 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0721 | -9.5158
281773X | MV/LV Substation RI***773X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C25 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8869 | -8.4129
220058X | MV/LV Substation G ***058X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 2.33 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.173 | -9.1911
066035Y | MV/LV Substation BE***035Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =213 kVA | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =317 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4618 | -6.2494
053301 | MV/LV Substation ID***301 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.598 | 0 | 0.036 | 0.5 | 0 |  | --> | C23 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2702 | -7.4715
012747X | MV/LV Substation BA***747X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 2.83 |  | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =73 kW | --> | E11 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7006 | -6.972
276127 | MV/LV Substation CL***127 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0979 | -9.4718
120562Y | MV/LV Substation CL***562Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E11 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3513 | -7.052
154551Z | MV/LV Substation BC***551Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C18 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4099 | -6.3662
015940 | MV/LV Substation PR***940 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C19 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2915 | -6.7532
0144176 | MV/LV Substation MC***4176 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1586 | -7.0213
281780X | MV/LV Substation LE***780X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.013 | 0.359 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8923 | -8.5819
069834 | MV/LV Substation BL***834 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.75 |  | --> | 0.95 | 0 | 0.006 | 0.5 | 0 |  | --> | C23 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3262 | -6.2443
154724 | MV/LV Substation SP***724 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.026 | 0.35 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3897 | -6.3849
033639Y | MV/LV Substation KI***639Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C18 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.473 | -7.2026
052745 | MV/LV Substation BA***745 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.22 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E13 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.4094 | -7.5461
059734Y | MV/LV Substation AR***734Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9248 | -7.4144
0054305 | MV/LV Substation WA***4305 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E19 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6408 | -6.2956
023683X | MV/LV Substation AR***683X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.22 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex KILSHANNY | Kilshanny [T41,T42] | CAHIR |  | 52.2153 | -8.0985
0504477 | MV/LV Substation CU***4477 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.488 | -8.097
154115Z | MV/LV Substation ES***115Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4072 | -6.3594
007129Z | MV/LV Substation SH***129Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 16.12 |  | --> | 0.38 | 0 | 0.005 | 0.367 | 0 |  | --> | E14 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3344 | -6.4889
008697Y | MV/LV Substation LA***697Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E17 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3937 | -6.8802
149224X | MV/LV Substation DR***224X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6027 | -8.1379
111697Y | MV/LV Substation KN***697Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex BALLYDEHOB | Ballydehob [T421] | DUNMANWAY |  | 51.5671 | -9.4411
052622Y | MV/LV Substation TA***622Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.519 | -7.3447
065067 | MV/LV Substation BR***067 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =284 kVA | --> | 0.38 | 0 | 0.009 | 0.357 | 0 |  | --> | C21 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6137 | -6.1916
1374149 | MV/LV Substation AG***4149 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 3.74 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.4074 | -9.6696
0494197 | MV/LV Substation ST***4197 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.391 | 2.8 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C17 ex GLEBE | Glebe [T41,T42] | RICHMOND |  | 53.7276 | -7.7972
2884167 | MV/LV Substation CA***4167 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.041 | 0.04 | Constrained, otherwise capacity available =507 kVA | --> | 0.598 | 0 | 0.049 | 0.5 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2263 | -6.1216
060045 | MV/LV Substation AN***045 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C18 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1772 | -7.2292
281956X | MV/LV Substation KN***956X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.263 | 4.67 |  | --> | 0.38 | 0 | 0.019 | 0.347 | 0 |  | --> | C20 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8891 | -8.4543
075390Y | MV/LV Substation KI***390Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6236 | -6.654
0594067 | MV/LV Substation SH***4067 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C20 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9949 | -7.2872
365396X | MV/LV Substation B.***396X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.293 | -6.4192
220616 | MV/LV Substation ER***616 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.199 | 1.36 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.0535 | -9.2871
001165X | MV/LV Substation GL***165X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.041 | 0.04 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2347 | -6.1167
108151X | MV/LV Substation IT***151X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.382 | 1.57 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C16 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4959 | -8.201
069054 | MV/LV Substation MO***054 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.75 |  | --> | 0.95 | 0 | 0.015 | 0.5 | 0 |  | --> | C13 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | POOLBEG |  | 53.3255 | -6.2397
014767X | MV/LV Substation NO***767X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2234 | -6.9913
001540 | MV/LV Substation CO***540 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =208 kVA | --> | 0.38 | 0 | 0.067 | 0.303 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2355 | -6.1156
062172X | MV/LV Substation GE***172X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 3.12 |  | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9646 | -6.4031
0584395 | MV/LV Substation BO***4395 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8113 | -8.2007
161614X | MV/LV Substation UD***614X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C13 ex SPIDDAL |  |  |  | 53.2494 | -9.2818
011708X | MV/LV Substation BA***708X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | C15 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6614 | -7.3426
062015 | MV/LV Substation QU***015 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.124 | 0.72 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | C12 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0072 | -6.383
069434 | MV/LV Substation ER***434 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.455 | 4.91 |  | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C13 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3296 | -6.324
288086 | MV/LV Substation CU***086 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 0.04 |  | --> | 0.048 | 0 | 0.004 | 0.042 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2189 | -6.1273
0664442 | MV/LV Substation CU***4442 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C19 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4502 | -6.167
288190 | MV/LV Substation PL***190 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 15.18 |  | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C26 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.276 | -6.2114
066257X | MV/LV Substation ST***257X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0.019 | 0.347 | 0 |  | --> | C15 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4587 | -6.2179
0384028 | MV/LV Substation SH***4028 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0463 | -8.8577
029037 | MV/LV Substation CA***037 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.01 | 0.04 | 0 |  | --> | C18 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.935 | -8.1862
062424X | MV/LV Substation TH***424X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 4.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0457 | -6.363
059461Y | MV/LV Substation GA***461Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =468 kVA | --> | 0.598 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | E17 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0143 | -7.3607
039519 | MV/LV Substation MU***519 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =277 kVA | --> | 0.38 | 0 | 0.051 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C20 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2823 | -9.0409
074991 | MV/LV Substation AC***991 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.065 | 8.5 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0392 | -8.0481
005592X | MV/LV Substation SE***592X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 17.8 |  | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6365 | -6.2321
281780Z | MV/LV Substation CO***780Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 4.67 |  | --> | 0.19 | 0 | 0 | 0.157 | 0 |  | --> | C26 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8959 | -8.4673
2664040 | MV/LV Substation BU***4040 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3211 | -7.1806
127036 | MV/LV Substation CH***036 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C17 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.7529 | -7.9543
014028X | MV/LV Substation WA***028X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1588 | -6.7981
081628Y | MV/LV Substation SI***628Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0.057 | 0 | 0 | Constrained, otherwise capacity available =314 kW | --> | C20 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3768 | -6.5923
069686 | MV/LV Substation SE***686 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.28 |  | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | C15 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3407 | -6.2227
050133 | MV/LV Substation TH***133 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.132 | 7.61 |  | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C11 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4203 | -7.9081
067298 | MV/LV Substation AV***298 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =313 kVA | --> | 0.38 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C15 ex CASTLETROY | Castletroy [T41,T42] | ARDNACRUSHA |  | 52.6693 | -8.5655
039652X | MV/LV Substation DU***652X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C12 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2758 | -8.9753
281745X | MV/LV Substation BA***745X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.414 | 5.49 |  | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8662 | -8.4757
050617Y | MV/LV Substation RO***617Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.3909 | -7.9914
019181X | MV/LV Substation OA***181X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.047 | 0.05 | Constrained, otherwise capacity available =607 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | C18 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.286 | -9.6792
081003Z | MV/LV Substation CA***003Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.027 | 0.159 | 0 |  | --> | C20 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3459 | -6.4315
117435Y | MV/LV Substation HI***435Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =323 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E14 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1797 | -8.4901
1924188 | MV/LV Substation BR***4188 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.56 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C15 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.1288 | -8.2728
288309X | MV/LV Substation PA***309X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =787 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.252 | -6.187
069408 | MV/LV Substation LI***408 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 4.47 |  | --> | 0.38 | 0 | 0.005 | 0.369 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3058 | -6.3366
288286 | MV/LV Substation DU***286 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.293 | 19.52 |  | --> | 0.38 | 0 | 0.013 | 0.356 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2881 | -6.2463
281125 | MV/LV Substation WA***125 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.254 | 7.88 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8971 | -8.4815
001255 | MV/LV Substation WA***255 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.237 | 1.16 |  | --> | 0.38 | 0 | 0.058 | 0.314 | 0 |  | --> | C18 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2977 | -6.1883
281774X | MV/LV Substation GR***774X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0.062 | 0.322 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8863 | -8.5741
365123X | MV/LV Substation CA***123X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.95 | 0 | 0.145 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.326 | -6.3499
093036Y | MV/LV Substation GL***036Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0.008 | 0.363 | 0 |  | --> | C14 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3765 | -6.289
0814376 | MV/LV Substation TH***4376 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3367 | -6.4716
062180X | MV/LV Substation MI***180X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 19.76 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E19 ex MULLAGHARLIN | Mullagharlin [T121,T122] | MULLAGHARLIN |  | 53.9658 | -6.476
0644484 | MV/LV Substation US***4484 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7318 | -6.3563
075452X | MV/LV Substation BA***452X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.5258 | -6.4847
073052X | MV/LV Substation ST***052X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =284 kVA | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C15 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.3982 | -7.7202
011866Y | MV/LV Substation VO***866Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.04 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5489 | -7.3927
003789 | MV/LV Substation DE***789 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 53.004 | -6.303
2934298 | MV/LV Substation HU***4298 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7205 | -6.5041
035662X | MV/LV Substation V ***662X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 6.17 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C17 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3804 | -7.9168
734001 | MV/LV Substation GR***001 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2942 | -6.4731
035041Y | MV/LV Substation PA***041Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 0.49 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.2703 | -7.8087
1764089 | MV/LV Substation GL***4089 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 18.78 |  | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | E18 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9229 | -8.9933
023840X | MV/LV Substation AR***840X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.2015 | -8.1321
149783 | MV/LV Substation SE***783 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6445 | -8.1153
137027 | MV/LV Substation AR***027 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 2 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C12 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.4687 | -9.7055
158189Y | MV/LV Substation EN***189Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C21 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9344 | -9.3013
036061 | MV/LV Substation CU***061 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E18 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5108 | -8.2736
068832 | MV/LV Substation WA***832 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.363 | 3.38 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3367 | -6.2427
433303X | MV/LV Substation ST***303X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =522 kVA | --> | 0.598 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =575 kW | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9007 | -8.5793
276022 | MV/LV Substation RY***022 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =253 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C11 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0605 | -9.4847
067260 | MV/LV Substation MA***260 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C14 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6776 | -8.6404
075803 | MV/LV Substation CR***803 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 0.58 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E12 ex FERNS | Ferns [T421] | CRANE |  | 52.5719 | -6.5201
001192X | MV/LV Substation EN***192X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.86 |  | --> | 0.598 | 0 | 0.352 | 0.329 | 0 |  | --> | C17 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3128 | -6.2048
002915 | MV/LV Substation IR***915 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.388 | 4.51 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C23 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1818 | -6.1173
154286Y | MV/LV Substation CA***286Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.598 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =531 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3824 | -6.5884
130256X | MV/LV Substation MO***256X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.4 | 2.55 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | E16 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6988 | -7.6166
233163 | MV/LV Substation WA***163 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C22 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2319 | -9.4427
039519X | MV/LV Substation IN***519X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =574 kVA | --> | 0.598 | 0 | 0.06 | 0.5 | 0 |  | --> | C18 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2857 | -9.0267
0664047 | MV/LV Substation TU***4047 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =257 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | E22 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4923 | -6.1977
037089 | MV/LV Substation VI***089 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.19 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =142 kW | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8501 | -8.9975
089200X | MV/LV Substation FA***200X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 9.1 |  | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E21 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.107 | -9.1359
081030Y | MV/LV Substation IN***030Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C16 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.34 | -6.5244
066693Z | MV/LV Substation KE***693Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =594 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4875 | -6.1494
001571 | MV/LV Substation WY***571 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 4.01 |  | --> | 0.38 | 0 | 0.038 | 0.339 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2685 | -6.1153
011005 | MV/LV Substation DE***005 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =442 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | C18 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6556 | -7.2573
281823Z | MV/LV Substation BI***823Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =16 kVA | --> | 0.048 | 0 | 0 | 0.043 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8324 | -8.5503
093021Z | MV/LV Substation FI***021Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =466 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.3999 | -6.2936
165299 | MV/LV Substation SL***299 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6317 | -8.9034
293765Y | MV/LV Substation WO***765Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.056 | 0.43 |  | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E12 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7971 | -6.7308
093073Z | MV/LV Substation FI***073Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.015 | 0.359 | 0 |  | --> | C27 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4005 | -6.3081
162319 | MV/LV Substation CA***319 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 0.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8931 | -7.4863
081289X | MV/LV Substation LU***289X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =133 kVA | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =144 kW | --> | C12 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3561 | -6.3924
158195X | MV/LV Substation CA***195X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.015 | 0.83 |  | --> | 0.048 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =23 kW | --> | C15 ex MILLTOWN MALBAY | Milltown Malbay [T42] | TULLABRACK |  | 52.8302 | -9.443
065425X | MV/LV Substation HO***425X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5585 | -6.2583
041030 | MV/LV Substation JA***030 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =261 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | E13 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7186 | -8.9986
035475X | MV/LV Substation CR***475X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 0.49 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E11 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.2895 | -8.053
265871X | MV/LV Substation TR***871X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.56 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0084 | -7.5206
049652Y | MV/LV Substation TH***652Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.073 | 1.31 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7819 | -8.1038
118042Y | MV/LV Substation FA***042Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C11 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3292 | -8.2245
039390 | MV/LV Substation AS***390 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0.041 | 0.5 | 0 |  | --> | C17 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.265 | -9.1149
016223Z | MV/LV Substation EA***223Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C22 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3637 | -6.5167
007653X | MV/LV Substation CO***653X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 16.12 |  | --> | 0.048 | 0 | 0.003 | 0.041 | 0 |  | --> | E12 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3875 | -6.5713
039777X | MV/LV Substation FE***777X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | C21 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2844 | -8.9875
064390 | MV/LV Substation MO***390 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =71 kW | --> | C13 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7187 | -6.2546
017130Y | MV/LV Substation GL***130Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.004 | 1.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C17 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.5686 | -9.295
0584188 | MV/LV Substation SU***4188 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C25 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.7738 | -8.0431
074480 | MV/LV Substation SP***480 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9466 | -8.1345
288065 | MV/LV Substation DU***065 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 19.52 |  | --> | 0.38 | 0 | 0.07 | 0.314 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.282 | -6.2367
118177 | MV/LV Substation BN***177 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.2859 | -8.0648
059330Y | MV/LV Substation SW***330Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =369 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C15 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9876 | -7.3754
1104003 | MV/LV Substation DE***4003 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.191 | 0.76 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8342 | -9.7898
0814251 | MV/LV Substation HA***4251 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =527 kVA | --> | 0.598 | 0 | 0.046 | 0.5 | 0 |  | --> | E20 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3466 | -6.4767
058072 | MV/LV Substation R ***072 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8802 | -8.2974
120563X | MV/LV Substation KI***563X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E19 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3982 | -7.0162
288158 | MV/LV Substation PT***158 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0.04 |  | --> | 0.38 | 0 | 0.04 | 0.279 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2306 | -6.1248
1654222 | MV/LV Substation AL***4222 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C16 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6207 | -8.8846
265889 | MV/LV Substation RA***889 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.127 | 2.56 |  | --> | 0.19 | 0 | 0.004 | 0.177 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0136 | -7.5313
006744X | MV/LV Substation BA***744X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E13 ex CRANE | Crane [T122] | CRANE |  | 52.4257 | -6.4618
011571X | MV/LV Substation CL***571X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6553 | -7.1477
050325X | MV/LV Substation CA***325X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.5087 | -8.0471
075798X | MV/LV Substation KI***798X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 4.38 |  | --> | 0.048 | 0 | 0.03 | 0.024 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.5173 | -6.3828
365456X | MV/LV Substation BA***456X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =212 kVA | --> | 0.38 | 0 | 0.078 | 0.296 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2737 | -6.3487
0224185 | MV/LV Substation QU***4185 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C15 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1263 | -8.6698
058193 | MV/LV Substation BU***193 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C15 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.8687 | -8.193
136709Y | MV/LV Substation AR***709Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C17 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.627 | -8.1664
433001 | MV/LV Substation CA***001 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9027 | -8.5791
0524802 | MV/LV Substation TY***4802 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E20 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.3936 | -7.3807
118341 | MV/LV Substation BL***341 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =65 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E15 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.2757 | -8
156229X | MV/LV Substation BO***229X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.152 | 2.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2754 | -7.0704
060483Y | MV/LV Substation NA***483Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0296 | -7.0407
048456 | MV/LV Substation HA***456 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9041 | -7.8795
0624205 | MV/LV Substation ME***4205 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 3.47 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E17 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0324 | -6.1773
021177Z | MV/LV Substation FA***177Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0 | 0.18 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9167 | -8.4935
214060 | MV/LV Substation ME***060 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7407 | -9.1245
0934097 | MV/LV Substation WO***4097 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.379 | 5.82 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C22 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3909 | -6.1754
065197Z | MV/LV Substation DU***197Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =149 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5257 | -6.1756
075777 | MV/LV Substation SU***777 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5413 | -6.5104
1604192 | MV/LV Substation DE***4192 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C11 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1711 | -7.1868
014542X | MV/LV Substation GL***542X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =118 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2215 | -7.0037
158918X | MV/LV Substation WA***918X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C20 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.8692 | -9.1545
066238 | MV/LV Substation ST***238 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0.013 | 0.361 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3756 | -6.0903
012310Y | MV/LV Substation BR***310Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 1.99 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C18 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8434 | -6.9413
139734X | MV/LV Substation OM***734X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E21 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8501 | -7.3284
0174012 | MV/LV Substation GR***4012 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 4.23 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C13 ex CHURCHTOWN | Churchtown [T41] | RATHKEALE |  | 52.4517 | -9.0522
009530X | MV/LV Substation CO***530X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C12 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.2901 | -7.242
136404Y | MV/LV Substation AB***404Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C13 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6252 | -8.1924
029949 | MV/LV Substation LI***949 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C32 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8544 | -8.1363
176331 | MV/LV Substation DR***331 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.049 | 0 | 0 | Constrained, otherwise capacity available =10 kW | --> | E11 ex MACROOM | Macroom [T422] | MACROOM |  | 51.9281 | -8.7551
154624Z | MV/LV Substation CA***624Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C14 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4042 | -6.3964
054507X | MV/LV Substation CO***507X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9556 | -7.3452
009354Y | MV/LV Substation BA***354Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2402 | -7.065
0334088 | MV/LV Substation CL***4088 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex PORTLAW | Portlaw [T41,T42] | BUTLERSTOWN |  | 52.2998 | -7.3252
0094253 | MV/LV Substation PR***4253 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C30 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2531 | -7.1282
021682Z | MV/LV Substation SE***682Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9097 | -8.4764
034253 | MV/LV Substation BE***253 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.5303 | -7.7535
160725Y | MV/LV Substation ME***725Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0466 | -7.2628
025282 | MV/LV Substation CL***282 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 6.21 |  | --> | 0.048 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =25 kW | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.3908 | -8.8894
082987 | MV/LV Substation CU***987 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6448 | -6.551
038904X | MV/LV Substation PU***904X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C16 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0568 | -8.8144
052080X | MV/LV Substation HI***080X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.053 | 0 | 0 | Constrained, otherwise capacity available =330 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5118 | -7.3401
590225 | MV/LV Substation DO***225 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex CONG |  |  |  | 53.5262 | -9.3504
068117X | MV/LV Substation RI***117X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =682 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3511 | -6.2772
064343Z | MV/LV Substation AV***343Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =368 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C18 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7054 | -6.3528
068449 | MV/LV Substation PH***449 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =21 kVA | --> | 0.598 | 0 | 0.035 | 0.484 | 0 |  | --> | C11 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3603 | -6.2783
046301X | MV/LV Substation PL***301X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.78 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2572 | -8.4785
065316Z | MV/LV Substation KI***316Z |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E14 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5473 | -6.447
021083Y | MV/LV Substation FL***083Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 6.78 |  | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C41 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9025 | -8.4123
1364436 | MV/LV Substation CL***4436 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C12 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6376 | -8.1926
0524276 | MV/LV Substation BR***4276 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.5044 | -7.4544
048019 | MV/LV Substation CA***019 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.231 | 2.03 |  | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =341 kW | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9225 | -7.8643
049491Z | MV/LV Substation BA***491Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.191 | 0.21 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8645 | -7.7159
093004X | MV/LV Substation CA***004X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =485 kVA | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C20 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4014 | -6.2752
082464 | MV/LV Substation VE***464 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6255 | -6.55
014851Z | MV/LV Substation PU***851Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C19 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2047 | -6.9884
288006 | MV/LV Substation TH***006 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0.022 | 0.349 | 0 |  | --> | C19 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2739 | -6.2511
252866 | MV/LV Substation BA***866 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.32 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C15 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4284 | -10.0934
039886X | MV/LV Substation OR***886X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2569 | -8.9301
066863X | MV/LV Substation AS***863X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4259 | -6.1936
067059Z | MV/LV Substation CR***059Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =810 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex BALLINACURRA | Ballinacurra [T41,T42] | LIMERICK |  | 52.6397 | -8.6437
056299Y | MV/LV Substation TE***299Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0588 | -8.2168
006775X | MV/LV Substation CL***775X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex CLONROCHE | Clonroche [T421,T422] | WEXFORD |  | 52.4467 | -6.714
220493X | MV/LV Substation LA***493X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.36 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.0428 | -9.3261
081686Y | MV/LV Substation BA***686Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E23 ex ADAMSTOWN |  |  |  | 53.3388 | -6.4938
021112 | MV/LV Substation SP***112 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =149 kVA | --> | 0.38 | 0 | 0.031 | 0.321 | 0 |  | --> | C24 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.915 | -8.4842
020071 | MV/LV Substation QU***071 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C16 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0582 | -9.5107
013630Y | MV/LV Substation KI***630Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E62 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0647 | -6.8633
0084373 | MV/LV Substation DU***4373 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.205 | 0.2 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | E16 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.2226 | -6.9349
0124127 | MV/LV Substation KI***4127 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 2.83 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6985 | -6.9342
156128X | MV/LV Substation SH***128X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 2.47 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2898 | -7.1236
503956 | MV/LV Substation GR***956 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 1.69 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.054 | -7.4053
144004Y | MV/LV Substation SU***004Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.346 | 2.78 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.788 | -7.333
253704Z | MV/LV Substation MO***704Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.4847 | -8.5595
164036 | MV/LV Substation ST***036 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =626 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5386 | -9.276
031062 | MV/LV Substation SC***062 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0471 | -7.5753
011798Z | MV/LV Substation JO***798Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.702 | -7.1706
039904X | MV/LV Substation CH***904X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.128 | 11.03 |  | --> | 0.19 | 0 | 0.003 | 0.178 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2658 | -9.1288
099031 | MV/LV Substation MC***031 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 5.45 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9583 | -7.7456
1764304 | MV/LV Substation CA***4304 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 18.78 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 52.0062 | -9.0779
093431Z | MV/LV Substation PR***431Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4028 | -6.1628
004920 | MV/LV Substation BO***920 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C23 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.729 | -6.2428
0354141 | MV/LV Substation CA***4141 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.2905 | -7.9506
011255 | MV/LV Substation BE***255 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.312 | 2.8 |  | --> | 0.38 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C12 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.5922 | -7.1834
182851X | MV/LV Substation CL***851X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.8078 | -8.7436
244004 | MV/LV Substation EL***004 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.598 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =542 kW | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1069 | -9.7889
0154242 | MV/LV Substation AB***4242 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =541 kVA | --> | 0.598 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =576 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.293 | -6.699
249579 | MV/LV Substation BA***579 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C16 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.14 | -7.7924
043157 | MV/LV Substation PU***157 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 0.43 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C20 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.8706 | -8.8518
160112Z | MV/LV Substation PR***112Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C15 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1538 | -7.1821
007290X | MV/LV Substation FE***290X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 16.12 |  | --> | 0.048 | 0 | 0.011 | 0.038 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3617 | -6.5166
2764088 | MV/LV Substation GO***4088 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.76 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C13 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0306 | -9.4738
015458Z | MV/LV Substation OA***458Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C11 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2084 | -6.6503
144156X | MV/LV Substation GA***156X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.78 |  | --> | 0.048 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7682 | -7.4744
008368Z | MV/LV Substation MO***368Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.239 | 0.24 | Constrained, otherwise capacity available =486 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C27 ex ROSBERCON | Rosbercon [T41,T42] | WATERFORD |  | 52.3968 | -6.9491
049071Y | MV/LV Substation KN***071Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.31 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C14 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.8353 | -7.9167
156337Z | MV/LV Substation CA***337Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.2529 | -6.8816
082671 | MV/LV Substation BA***671 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6329 | -6.6885
032068Y | MV/LV Substation BE***068Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C16 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1595 | -7.1479
068450 | MV/LV Substation KI***450 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.397 | 3 |  | --> | 0.598 | 0 | 0.03 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3356 | -6.336
068958 | MV/LV Substation MA***958 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.255 | 9.02 |  | --> | 0.38 | 0 | 0.005 | 0.356 | 0 |  | --> | C13 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3379 | -6.2389
154765 | MV/LV Substation WE***765 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0.011 | 0.175 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4007 | -6.4178
046840 | MV/LV Substation ST***840 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 4.13 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C18 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3956 | -8.5645
020063 | MV/LV Substation OK***063 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =561 kVA | --> | 0.598 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C12 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0653 | -9.5131
0714073 | MV/LV Substation AR***4073 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.38 | 0 | 0.067 | 0.296 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1287 | -6.0803
2554064 | MV/LV Substation MA***4064 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6328 | -8.4451
081154Z | MV/LV Substation PA***154Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3295 | -6.3708
255034X | MV/LV Substation MU***034X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6495 | -8.2653
064570 | MV/LV Substation CO***570 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E15 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6229 | -6.2704
015625Z | MV/LV Substation GR***625Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | C19 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2856 | -6.8003
082170Y | MV/LV Substation LA***170Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7468 | -6.67
1564201 | MV/LV Substation TH***4201 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2845 | -7.104
164028 | MV/LV Substation BR***028 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =109 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5506 | -9.2795
161977X | MV/LV Substation KY***977X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 11.03 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C27 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.3329 | -9.1886
031882X | MV/LV Substation SH***882X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0936 | -7.7115
184919 | MV/LV Substation DR***919 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.154 | -6.6785
032123 | MV/LV Substation GA***123 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1721 | -7.3458
160891Y | MV/LV Substation KI***891Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =629 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C23 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1332 | -7.1561
006500X | MV/LV Substation FA***500X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 3.12 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5033 | -6.6075
066015 | MV/LV Substation SU***015 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =137 kVA | --> | 0.38 | 0 | 0.037 | 0.315 | 0 |  | --> | C19 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3895 | -6.111
023421 | MV/LV Substation CR***421 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1374 | -8.3455
154142Z | MV/LV Substation MA***142Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =254 kVA | --> | 0.38 | 0 | 0.033 | 0.335 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3974 | -6.4236
025141Y | MV/LV Substation BR***141Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E17 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3597 | -8.6914
0524173 | MV/LV Substation TR***4173 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.6898 | -7.364
007534Y | MV/LV Substation SL***534Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 16.12 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3623 | -6.5236
180466 | MV/LV Substation BA***466 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.008 | 1.4 |  | --> | 0.048 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =16 kW | --> | C23 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7057 | -6.9235
015793Z | MV/LV Substation CE***793Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 12.6 |  | --> | 0.38 | 0 | 0.04 | 0.34 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2375 | -6.7282
019211X | MV/LV Substation SK***211X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.119 | 1.54 |  | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2545 | -9.6876
281028X | MV/LV Substation GI***028X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.223 | 7.88 |  | --> | 0.38 | 0 | 0.01 | 0.348 | 0 |  | --> | C17 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8937 | -8.4822
118638X | MV/LV Substation KI***638X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E15 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3285 | -8.1857
081648Y | MV/LV Substation CE***648Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3314 | -6.5292
005048 | MV/LV Substation WE***048 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 17.8 |  | --> | 0.095 | 0 | 0.01 | 0.085 | 0 |  | --> | E21 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6733 | -6.311
066698Z | MV/LV Substation PA***698Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =523 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4555 | -6.2196
238230 | MV/LV Substation RO***230 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6455 | -9.1076
081549Y | MV/LV Substation DU***549Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.19 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =157 kW | --> | C18 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.366 | -6.4898
012097Y | MV/LV Substation CA***097Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C19 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8349 | -6.9158
025197X | MV/LV Substation BA***197X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4479 | -8.4521
095507X | MV/LV Substation MA***507X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.7 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6752 | -9.565
082684 | MV/LV Substation WI***684 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6127 | -6.6754
034411X | MV/LV Substation BA***411X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 0.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E23 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3729 | -7.772
020145 | MV/LV Substation CR***145 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0856 | -9.5975
0694142 | MV/LV Substation KI***4142 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =892 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2807 | -6.3124
184138 | MV/LV Substation MO***138 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1209 | -6.7788
4954006 | MV/LV Substation PO***4006 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E16 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9393 | -9.9153
154430Z | MV/LV Substation AR***430Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =310 kVA | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4047 | -6.4077
056807X | MV/LV Substation AG***807X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E20 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0259 | -8.0645
004205 | MV/LV Substation GL***205 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C25 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7919 | -6.1458
0144295 | MV/LV Substation CU***4295 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =270 kVA | --> | 0.38 | 0 | 0.079 | 0 | 0 | Constrained, otherwise capacity available =303 kW | --> | C11 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1689 | -6.8169
066854X | MV/LV Substation IR***854X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =188 kVA | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4367 | -6.2261
051575 | MV/LV Substation DU***575 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.383 | 2.22 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | E12 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3479 | -7.3891
0294363 | MV/LV Substation LA***4363 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =543 kVA | --> | 0.598 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.9047 | -8.1663
366613 | MV/LV Substation MO***613 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.45 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2596 | -9.6221
054169Z | MV/LV Substation TO***169Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =565 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | E16 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0237 | -7.3154
030212X | MV/LV Substation PI***212X |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =911 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =938 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9553 | -7.8472
0244071 | MV/LV Substation BO***4071 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.211 | -8.731
025684Y | MV/LV Substation OL***684Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 2.96 |  | --> | 0.19 | 0 | 0.138 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.4245 | -8.6662
007273X | MV/LV Substation MO***273X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3083 | -6.4901
1274540 | MV/LV Substation CA***4540 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6566 | -7.8247
137587 | MV/LV Substation AB***587 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 3.74 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C11 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3471 | -9.6855
019112X | MV/LV Substation SM***112X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.047 | 0.05 | Constrained, otherwise capacity available =344 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =558 kW | --> | C19 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2613 | -9.6787
118030 | MV/LV Substation LE***030 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.249 | 2 |  | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =337 kW | --> | C11 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3334 | -8.2344
130575 | MV/LV Substation BA***575 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.684 | -7.5826
011215 | MV/LV Substation LA***215 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C14 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6463 | -7.2447
054377X | MV/LV Substation AU***377X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.906 | -7.3187
365527X | MV/LV Substation HA***527X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =317 kVA | --> | 0.38 | 0 | 0.075 | 0.313 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3241 | -6.3562
055329Y | MV/LV Substation BU***329Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.8838 | -7.9344
108556 | MV/LV Substation PE***556 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.035 | 1.57 |  | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5489 | -7.8351
093293 | MV/LV Substation WE***293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.291 | 7.91 |  | --> | 0.38 | 0 | 0.003 | 0.363 | 0 |  | --> | C20 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3828 | -6.3186
015803 | MV/LV Substation NE***803 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2107 | -6.708
073811 | MV/LV Substation GO***811 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C16 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.5018 | -7.7305
0494405 | MV/LV Substation KI***4405 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5917 | -7.7171
0634134 | MV/LV Substation FE***4134 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C17 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.855 | -6.5233
067055X | MV/LV Substation MU***055X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =345 kVA | --> | 0.38 | 0 | 0.044 | 0.34 | 0 |  | --> | C19 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6302 | -8.6472
365182X | MV/LV Substation WH***182X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.007 | 0.042 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3059 | -6.3755
001118 | MV/LV Substation MO***118 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.485 | 4.37 |  | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C14 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2931 | -6.1519
003480Y | MV/LV Substation GR***480Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C23 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9576 | -6.0978
365963X | MV/LV Substation CO***963X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =738 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2979 | -6.3737
365825X | MV/LV Substation WO***825X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =202 kVA | --> | 0.38 | 0 | 0.011 | 0.344 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2759 | -6.3298
0824200 | MV/LV Substation CO***4200 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0.142 | 0 | 0 | Constrained, otherwise capacity available =260 kW | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6353 | -6.657
034225Y | MV/LV Substation CR***225Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.333 | 5.88 |  | --> | 0.38 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C11 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3714 | -7.7048
111586Z | MV/LV Substation CU***586Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6512 | -9.383
099352X | MV/LV Substation CA***352X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.363 | 5.45 |  | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =359 kW | --> | C18 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9733 | -7.708
062932Y | MV/LV Substation CL***932Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.132 | 3.47 |  | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | E17 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0375 | -6.1779
3664093 | MV/LV Substation RO***4093 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.195 | 0.45 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C14 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2685 | -9.5592
039451X | MV/LV Substation CE***451X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =524 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C12 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2703 | -9.0486
0754136 | MV/LV Substation CL***4136 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5464 | -6.3627
068064X | MV/LV Substation JA***064X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.235 | 1.47 |  | --> | 0.598 | 0 | 0.012 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3349 | -6.3325
065620 | MV/LV Substation AR***620 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.6026 | -6.3868
0014171 | MV/LV Substation TH***4171 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.55 |  | --> | 0.95 | 0 | 0.079 | 0.5 | 0 |  | --> | C21 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.289 | -6.1768
0054243 | MV/LV Substation BL***4243 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =378 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6801 | -6.303
3494014 | MV/LV Substation CA***4014 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8164 | -9.0529
0054120 | MV/LV Substation KI***4120 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E21 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6737 | -6.3164
021173X | MV/LV Substation LI***173X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =534 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.906 | -8.4429
015736 | MV/LV Substation HA***736 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2219 | -6.5955
012579 | MV/LV Substation CL***579 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.283 | 1.99 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C20 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8499 | -6.9804
093213Z | MV/LV Substation FO***213Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C18 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4 | -6.2596
081615Y | MV/LV Substation AB***615Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.058 | 0 | 0 | Constrained, otherwise capacity available =320 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3301 | -6.5538
014675Z | MV/LV Substation AR***675Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1473 | -6.9184
068702 | MV/LV Substation TA***702 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.207 | 14.34 |  | --> | 0.38 | 0 | 0 | 0.353 | 0 |  | --> | C37 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3508 | -6.2513
220377 | MV/LV Substation BA***377 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.36 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.279 | -9.3741
021648Z | MV/LV Substation FA***648Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.004 | 0.36 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9174 | -8.494
053141 | MV/LV Substation GE***141 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =60 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.234 | -7.3209
127538Y | MV/LV Substation TR***538Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C14 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.725 | -7.5835
365858 | MV/LV Substation LO***858 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0 | 0.356 | 0 |  | --> | C14 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2819 | -6.3771
288039X | MV/LV Substation AR***039X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.353 | 1.16 |  | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C19 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.273 | -6.2079
004816 | MV/LV Substation YA***816 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 18.08 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7998 | -6.1712
068453 | MV/LV Substation PH***453 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =257 kVA | --> | 0.95 | 0 | 0.021 | 0.5 | 0 |  | --> | C14 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3567 | -6.2752
1274496 | MV/LV Substation SI***4496 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6719 | -7.835
365309 | MV/LV Substation RA***309 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0.015 | 0.08 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2777 | -6.4651
081445Z | MV/LV Substation TH***445Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.314 | -6.6114
007796X | MV/LV Substation JO***796X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.337 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.2928 | -6.5025
011874Z | MV/LV Substation RA***874Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =136 kW | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6734 | -7.2343
007557Y | MV/LV Substation DO***557Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E13 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2007 | -6.3543
066794Z | MV/LV Substation KN***794Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4502 | -6.2657
1544023 | MV/LV Substation MO***4023 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4642 | -6.5219
052357Y | MV/LV Substation KI***357Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 10.9 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C24 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.6077 | -7.3846
021233Z | MV/LV Substation WI***233Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.005 | 0.359 | 0 |  | --> | C15 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9325 | -8.3796
019162 | MV/LV Substation FE***162 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2833 | -9.8606
365047 | MV/LV Substation WH***047 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.347 | 13.91 |  | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2779 | -6.377
068187X | MV/LV Substation PH***187X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.218 | 20.78 |  | --> | 0.38 | 0 | 0 | 0.354 | 0 |  | --> | C19 ex HEUSTON SQUARE | Heuston Square [T101,T102] | INCHICORE 220KV |  | 53.3432 | -6.2919
365522X | MV/LV Substation HA***522X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0 | 0.367 | 0 |  | --> | C20 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.3258 | -6.3541
031547 | MV/LV Substation KN***547 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9969 | -7.7407
0994147 | MV/LV Substation CR***4147 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =273 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9368 | -7.7501
081110Z | MV/LV Substation PA***110Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =566 kVA | --> | 0.95 | 0 | 0.132 | 0.5 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3303 | -6.3741
067341 | MV/LV Substation WO***341 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 6.81 |  | --> | 0.598 | 0 | 0.034 | 0.5 | 0 |  | --> | C06 ex AHANE | Ahane [T102] | AHANE |  | 52.6672 | -8.5207
0494332 | MV/LV Substation MC***4332 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8642 | -7.7133
154544 | MV/LV Substation DU***544 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =771 kVA | --> | 0.95 | 0 | 0.011 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4156 | -6.365
021474Z | MV/LV Substation BL***474Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =497 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9163 | -8.4716
069554 | MV/LV Substation HA***554 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.382 | 9.28 |  | --> | 0.598 | 0 | 0.008 | 0.5 | 0 |  | --> | C23 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.335 | -6.2425
144641X | MV/LV Substation OA***641X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C11 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.796 | -7.2129
021006 | MV/LV Substation CO***006 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =116 kVA | --> | 0.19 | 0 | 0 | 0.178 | 0 |  | --> | C27 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9185 | -8.4777
050280X | MV/LV Substation TH***280X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.177 | 7.61 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C13 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4283 | -7.93
365005Y | MV/LV Substation NE***005Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2987 | -6.5215
0304137 | MV/LV Substation SI***4137 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9551 | -7.8707
281464Z | MV/LV Substation HE***464Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =337 kVA | --> | 0.598 | 0 | 0.069 | 0 | 0 | Constrained, otherwise capacity available =506 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8245 | -8.3889
074300X | MV/LV Substation MA***300X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9528 | -8.0917
089105X | MV/LV Substation KN***105X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.363 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E19 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1178 | -9.1335
0334092 | MV/LV Substation RA***4092 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3236 | -7.3906
142011 | MV/LV Substation MO***011 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C17 ex ATHENRY |  |  |  | 53.3008 | -8.7433
0374141 | MV/LV Substation AB***4141 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8244 | -8.9776
029390 | MV/LV Substation PA***390 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C15 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.912 | -8.1572
007875Z | MV/LV Substation LI***875Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.196 | 1.4 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2841 | -6.399
062043 | MV/LV Substation CA***043 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 5.69 |  | --> | 0.95 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =899 kW | --> | C19 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0062 | -6.3942
026737Y | MV/LV Substation CL***737Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 8.66 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C14 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.745 | -8.7223
0144348 | MV/LV Substation RI***4348 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.63 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1315 | -6.7362
281227Z | MV/LV Substation BR***227Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0.039 | 0 | 0 | Constrained, otherwise capacity available =154 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8223 | -8.3844
034973 | MV/LV Substation G ***973 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.075 | 0.95 |  | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | C16 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3555 | -7.6996
023544Y | MV/LV Substation PA***544Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E11 ex CASTLELYONS | Castlelyons [T421,T422] | BARRYMORE |  | 52.0758 | -8.2846
048018 | MV/LV Substation GR***018 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 2.03 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9222 | -7.8674
281100Z | MV/LV Substation HE***100Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =138 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C12 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8221 | -8.389
054026Z | MV/LV Substation TH***026Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =527 kVA | --> | 0.598 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0495 | -7.3239
130763 | MV/LV Substation SE***763 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7733 | -7.4934
026961Y | MV/LV Substation CL***961Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.6859 | -8.7583
164797 | MV/LV Substation RA***797 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5011 | -9.3539
281615 | MV/LV Substation CO***615 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.82 | -8.3562
0394213 | MV/LV Substation AS***4213 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2336 | -8.9437
293245 | MV/LV Substation KI***245 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 2.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E18 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7363 | -6.802
046974 | MV/LV Substation OA***974 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.257 | -8.4967
032445Y | MV/LV Substation AS***445Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1638 | -7.0022
0644387 | MV/LV Substation LA***4387 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =557 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | E15 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6323 | -6.2338
281077X | MV/LV Substation HO***077X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.112 | 5.49 |  | --> | 0.19 | 0 | 0 | 0.178 | 0 |  | --> | C19 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.866 | -8.4515
125401 | MV/LV Substation MU***401 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =76 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2649 | -8.2596
260546 | MV/LV Substation KN***546 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.67 |  | --> | 0.048 | 0 | 0.005 | 0.042 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8937 | -9.5487
008483Z | MV/LV Substation PR***483Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =381 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C18 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3925 | -6.9483
033868Y | MV/LV Substation KI***868Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.5142 | -7.5075
006046Y | MV/LV Substation BL***046Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 4.38 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | E13 ex CRANE | Crane [T122] | CRANE |  | 52.4476 | -6.3579
157469 | MV/LV Substation PU***469 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 53.9906 | -7.6542
162139X | MV/LV Substation MC***139X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 7.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8442 | -7.7226
069513 | MV/LV Substation BA***513 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =762 kVA | --> | 0.95 | 0 | 0.01 | 0.5 | 0 |  | --> | C18 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3153 | -6.3455
154208Z | MV/LV Substation DU***208Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =820 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =925 kW | --> | C19 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.394 | -6.386
068467X | MV/LV Substation LO***467X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 12.96 |  | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | C21 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3813 | -6.2408
023540X | MV/LV Substation TE***540X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1426 | -8.3481
039068 | MV/LV Substation CO***068 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.45 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2651 | -9.0677
0174320 | MV/LV Substation NA***4320 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4086 | -9.0309
026516Y | MV/LV Substation IV***516Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.6729 | -8.6814
164429 | MV/LV Substation UN***429 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C17 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5563 | -9.1429
068038 | MV/LV Substation BO***038 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =599 kVA | --> | 0.95 | 0 | 0.136 | 0.5 | 0 |  | --> | C11 ex GLASNEVIN | Glasnevin [T41] | FINGLAS |  | 53.3676 | -6.2688
069188 | MV/LV Substation BA***188 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.598 | 0 | 0.152 | 0.438 | 0 |  | --> | C21 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2879 | -6.2995
0024066 | MV/LV Substation CO***4066 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.041 | 0.04 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2099 | -6.1057
0664125 | MV/LV Substation SE***4125 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =337 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C15 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.46 | -6.2169
006688 | MV/LV Substation TO***688 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 1.29 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex MONFIN | Monfin [T41,T42] | WEXFORD |  | 52.4889 | -6.5948
070875X | MV/LV Substation HI***875X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.146 | 0.76 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C11 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0834 | -9.2098
1604013 | MV/LV Substation 50***4013 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.164 | -7.5631
027919 | MV/LV Substation KI***919 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.042 | 7.79 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | E12 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.6584 | -9.0864
078078X | MV/LV Substation KN***078X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C12 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9673 | -8.7989
281669X | MV/LV Substation BO***669X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.796 | -8.356
207157 | MV/LV Substation BE***157 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.713 | -7.5435
054785X | MV/LV Substation CU***785X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 2.78 |  | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | E16 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.819 | -7.4737
156325X | MV/LV Substation LO***325X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2902 | -6.8789
066899X | MV/LV Substation BU***899X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4792 | -6.3673
063800X | MV/LV Substation TH***800X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8481 | -6.5395
021536Z | MV/LV Substation AR***536Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C24 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9134 | -8.4906
016062Z | MV/LV Substation WO***062Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =237 kVA | --> | 0.38 | 0 | 0.043 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3424 | -6.5529
281116X | MV/LV Substation TO***116X |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 17.47 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | E11 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.888 | -8.6079
034694 | MV/LV Substation AR***694 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.021 | 0.57 |  | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | C16 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3609 | -7.7209
054933X | MV/LV Substation PU***933X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.78 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.8476 | -7.4041
164265 | MV/LV Substation CO***265 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.182 | 0.88 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5648 | -9.1112
281965X | MV/LV Substation CO***965X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 6.78 |  | --> | 0.38 | 0 | 0.013 | 0.361 | 0 |  | --> | C26 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8925 | -8.4023
050862 | MV/LV Substation IN***862 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4052 | -7.9873
015448Z | MV/LV Substation LA***448Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.208 | -6.7226
075232 | MV/LV Substation CO***232 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 0.58 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E17 ex FERNS | Ferns [T421] | CRANE |  | 52.6442 | -6.4577
3654056 | MV/LV Substation AI***4056 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2941 | -6.3636
021214 | MV/LV Substation AL***214 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0.06 | 0.325 | 0 |  | --> | C20 ex FAIRHILL | Fairhill [T42] | KILBARRY |  | 51.9048 | -8.4586
039211X | MV/LV Substation CA***211X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C20 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.3052 | -8.9315
0814359 | MV/LV Substation LE***4359 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C17 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.363 | -6.5001
405271 | MV/LV Substation AS***271 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2256 | -6.9447
377802 | MV/LV Substation IN***802 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9676 | -10.1688
030037 | MV/LV Substation LI***037 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =104 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9585 | -7.8559
047242 | MV/LV Substation ST***242 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 1.04 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C11 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9685 | -8.2986
099484 | MV/LV Substation HE***484 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9312 | -7.7101
064053 | MV/LV Substation TR***053 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.38 | 0 | 0.084 | 0 | 0 | Constrained, otherwise capacity available =310 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6981 | -6.2517
037126Y | MV/LV Substation GA***126Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0.069 | 0 | 0 | Constrained, otherwise capacity available =317 kW | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8515 | -9.0089
281425X | MV/LV Substation MO***425X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C22 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8112 | -8.3909
007065X | MV/LV Substation WI***065X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 16.12 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E12 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3738 | -6.6533
052293Y | MV/LV Substation LY***293Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4982 | -7.3581
160874Y | MV/LV Substation SH***874Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0722 | -7.2352
137167X | MV/LV Substation SL***167X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.355 | 3.74 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.4 | -9.6148
067449Y | MV/LV Substation BR***449Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 13.8 |  | --> | 0.38 | 0 | 0.023 | 0.359 | 0 |  | --> | C13 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6661 | -8.5929
015738Z | MV/LV Substation WA***738Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C11 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2472 | -6.6592
368334X | MV/LV Substation RY***334X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C17 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7627 | -8.7682
0714087 | MV/LV Substation DR***4087 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 5.58 |  | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0959 | -6.0792
0684743 | MV/LV Substation DA***4743 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GLASNEVIN | Glasnevin [T41] | FINGLAS |  | 53.3673 | -6.2676
0814200 | MV/LV Substation GR***4200 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =298 kVA | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.325 | -6.47
281274 | MV/LV Substation BA***274 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.841 | -8.6017
206191X | MV/LV Substation UD***191X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 1.6 |  | --> | 0.19 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E17 ex BELMULLET | Belmullet [T421] | BELLACORICK |  | 54.1194 | -10.1021
099644X | MV/LV Substation ES***644X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.358 | 5.45 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C18 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9657 | -7.7214
1644025 | MV/LV Substation RE***4025 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.6397 | -9.1582
064012Z | MV/LV Substation MA***012Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =541 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C20 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.702 | -6.3707
050259 | MV/LV Substation CO***259 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | C23 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.439 | -7.9344
238653X | MV/LV Substation MC***653X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =626 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E18 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6357 | -9.2389
0824262 | MV/LV Substation CA***4262 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.154 | 2.01 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6631 | -6.6735
253706Z | MV/LV Substation CA***706Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C17 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5068 | -8.8207
068712X | MV/LV Substation HO***712X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 11.14 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3776 | -6.3119
047226X | MV/LV Substation FO***226X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.195 | 1.04 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C15 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9778 | -8.2919
0214309 | MV/LV Substation LO***4309 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0.046 | 0.5 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9271 | -8.4527
054293Z | MV/LV Substation DR***293Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =327 kVA | --> | 0.38 | 0 | 0.009 | 0.363 | 0 |  | --> | C21 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0159 | -7.1377
015958 | MV/LV Substation FI***958 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2811 | -6.7088
010586X | MV/LV Substation KE***586X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.4826 | -7.0739
033190 | MV/LV Substation OW***190 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3965 | -7.3363
014867X | MV/LV Substation TI***867X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0791 | -6.8293
0684649 | MV/LV Substation EA***4649 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =947 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CLONTARF | Clontarf [T42] | FINGLAS |  | 53.3726 | -6.2102
132010 | MV/LV Substation AB***010 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C16 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2016 | -8.5714
066964 | MV/LV Substation PO***964 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4866 | -6.1173
139144Y | MV/LV Substation TO***144Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E21 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.865 | -7.3148
0254306 | MV/LV Substation BA***4306 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.4103 | -8.7875
209278X | MV/LV Substation TR***278X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0918 | -7.6823
2884176 | MV/LV Substation TU***4176 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2472 | -6.1576
051729 | MV/LV Substation MO***729 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.22 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.4 | -7.6769
118018 | MV/LV Substation MA***018 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 2 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C11 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3318 | -8.2186
053904Y | MV/LV Substation ES***904Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 2.39 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2949 | -7.5649
0334242 | MV/LV Substation CA***4242 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3976 | -7.3469
433931 | MV/LV Substation SO***931 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.45 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9331 | -8.5171
021095Y | MV/LV Substation ME***095Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.017 | 0.167 | 0 |  | --> | C18 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9062 | -8.4508
081382Z | MV/LV Substation WE***382Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C18 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3461 | -6.3988
154719 | MV/LV Substation NE***719 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.4264 | -6.4927
064211Z | MV/LV Substation TH***211Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7156 | -6.3717
0034239 | MV/LV Substation SU***4239 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9717 | -6.077
1844101 | MV/LV Substation HE***4101 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.38 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C20 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.0681 | -6.7019
277004 | MV/LV Substation GR***004 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.38 | 0 | 0.07 | 0.297 | 0 |  | --> | C19 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3969 | -6.1679
011592Y | MV/LV Substation SM***592Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.614 | -7.1335
050149X | MV/LV Substation KI***149X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.162 | 7.61 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C12 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4109 | -7.8951
196042X | MV/LV Substation SU***042X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | C18 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5601 | -6.7903
165127Y | MV/LV Substation TH***127Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.5994 | -8.8723
035884X | MV/LV Substation GA***884X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3566 | -7.7971
052586Z | MV/LV Substation TI***586Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =285 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | E14 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4578 | -7.1103
522030 | MV/LV Substation PR***030 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C18 ex MEELICK |  |  |  | 53.0199 | -7.2968
041552X | MV/LV Substation CA***552X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7117 | -8.9942
095084 | MV/LV Substation CL***084 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 0.7 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C20 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.7254 | -9.395
293597Z | MV/LV Substation CA***597Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8032 | -6.7635
1364019 | MV/LV Substation BA***4019 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.5762 | -8.397
590203 | MV/LV Substation RI***203 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex CONG |  |  |  | 53.5358 | -9.2924
015917Y | MV/LV Substation TH***917Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 12.6 |  | --> | 0.38 | 0 | 0.023 | 0.353 | 0 |  | --> | C19 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2331 | -6.6589
093112Z | MV/LV Substation SA***112Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =138 kVA | --> | 0.19 | 0 | 0 | 0.181 | 0 |  | --> | C20 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.399 | -6.2536
151815X | MV/LV Substation CO***815X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0 | 0.185 | 0 |  | --> | C12 ex BRUFF | Bruff [T42,T421] | LIMERICK |  | 52.4781 | -8.4321
0044076 | MV/LV Substation GA***4076 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =950 kW | --> | C25 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7913 | -6.1435
054002 | MV/LV Substation WE***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =217 kVA | --> | 0.598 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =537 kW | --> | C23 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0334 | -7.2949
0934160 | MV/LV Substation WA***4160 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =464 kVA | --> | 0.598 | 0 | 0.046 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4071 | -6.1814
041174Y | MV/LV Substation HO***174Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6708 | -8.9559
082900X | MV/LV Substation CA***900X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 0.64 |  | --> | 0.048 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.779 | -6.7182
025385 | MV/LV Substation MI***385 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.15 | 1.93 |  | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C15 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.34 | -8.8564
068447 | MV/LV Substation BR***447 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.155 | 1.86 |  | --> | 0.598 | 0 | 0.051 | 0.492 | 0 |  | --> | C20 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3661 | -6.2397
120405Y | MV/LV Substation NE***405Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.151 | 3.5 |  | --> | 0.19 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | E13 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.3956 | -6.7597
001089 | MV/LV Substation ST***089 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.11 | 0.86 |  | --> | 0.19 | 0 | 0 | 0.177 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3056 | -6.2005
084873 | MV/LV Substation KI***873 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =475 kVA | --> | 0.598 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1383 | -8.9383
0684495 | MV/LV Substation HA***4495 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 11.14 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3659 | -6.2912
029633X | MV/LV Substation CA***633X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =617 kVA | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9216 | -8.1879
281141 | MV/LV Substation AR***141 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C13 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8696 | -8.4358
365255 | MV/LV Substation NE***255 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2605 | -6.4944
023341 | MV/LV Substation CU***341 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C18 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.1326 | -8.192
042579X | MV/LV Substation KN***579X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C19 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8408 | -9.3221
028033Y | MV/LV Substation CL***033Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 19.7 |  | --> | 0.38 | 0 | 0.011 | 0.361 | 0 |  | --> | C12 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8537 | -8.3082
176005 | MV/LV Substation TH***005 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E11 ex MACROOM | Macroom [T422] | MACROOM |  | 51.8977 | -8.8627
064371Y | MV/LV Substation BA***371Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =114 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6533 | -6.4224
082414X | MV/LV Substation LI***414X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 2.01 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C18 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6662 | -6.7223
365011 | MV/LV Substation SI***011 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0.024 | 0.351 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2948 | -6.3483
021053X | MV/LV Substation FA***053X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0.021 | 0.076 | 0 |  | --> | C12 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9053 | -8.4375
065111 | MV/LV Substation HI***111 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =104 kVA | --> | 0.19 | 0 | 0.071 | 0 | 0 | Constrained, otherwise capacity available =124 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5705 | -6.1129
066751Z | MV/LV Substation CH***751Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5065 | -6.46
182221 | MV/LV Substation CO***221 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.042 | 0 | 0 | Constrained, otherwise capacity available =331 kW | --> | E21 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.7433 | -8.7756
081165Y | MV/LV Substation CR***165Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =320 kW | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3555 | -6.5428
093265Z | MV/LV Substation JA***265Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =604 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4051 | -6.2208
139160Y | MV/LV Substation CA***160Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8753 | -7.3
1674086 | MV/LV Substation LI***4086 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9702 | -8.5283
1544391 | MV/LV Substation KI***4391 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4299 | -6.3916
152006 | MV/LV Substation P/***006 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E33 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.5655 | -8.3393
082985 | MV/LV Substation VE***985 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6314 | -6.5484
082809Y | MV/LV Substation AT***809Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =328 kVA | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C30 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6477 | -6.6558
068910 | MV/LV Substation VE***910 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C11 ex CLONTARF | Clontarf [T42] | FINGLAS |  | 53.3777 | -6.1998
003040 | MV/LV Substation TH***040 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9335 | -6.2335
015833Y | MV/LV Substation CL***833Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =407 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =564 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2925 | -6.6857
015979 | MV/LV Substation BA***979 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.173 | -6.6264
093333Z | MV/LV Substation LI***333Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =485 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C33 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4031 | -6.257
039360 | MV/LV Substation CA***360 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 11.03 |  | --> | 0.38 | 0 | 0.005 | 0.368 | 0 |  | --> | C31 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.278 | -9.0781
365049Y | MV/LV Substation LY***049Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2992 | -6.5367
0114028 | MV/LV Substation BA***4028 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C14 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6082 | -6.9526
001233 | MV/LV Substation PA***233 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.162 | 1.16 |  | --> | 0.38 | 0 | 0.043 | 0.314 | 0 |  | --> | C17 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2964 | -6.1981
0684068 | MV/LV Substation NE***4068 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.188 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3497 | -6.2359
093030 | MV/LV Substation SA***030 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =807 kVA | --> | 0.95 | 0 | 0.02 | 0.5 | 0 |  | --> | C20 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3979 | -6.2487
0604011 | MV/LV Substation BA***4011 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C18 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1199 | -7.2504
068855 | MV/LV Substation MO***855 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.6 |  | --> | 0.598 | 0 | 0.003 | 0.5 | 0 |  | --> | C11 ex KINGSBRIDGE | Kingsbridge [T41,T42] | INCHICORE 220KV |  | 53.3497 | -6.2936
039418X | MV/LV Substation GA***418X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =232 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C17 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2814 | -9.0498
054204X | MV/LV Substation LI***204X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0447 | -7.3099
0054175 | MV/LV Substation PE***4175 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6771 | -6.2927
0684519 | MV/LV Substation ST***4519 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 11.14 |  | --> | 0.95 | 0 | 0.04 | 0.5 | 0 |  | --> | C24 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3691 | -6.2961
001205X | MV/LV Substation JA***205X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 15.18 |  | --> | 0.95 | 0 | 0.006 | 0.5 | 0 |  | --> | C14 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2811 | -6.1945
293021 | MV/LV Substation MO***021 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =899 kVA | --> | 0.95 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =926 kW | --> | E20 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9422 | -6.7116
260004 | MV/LV Substation BA***004 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.033 | 1.67 |  | --> | 0.19 | 0 | 0.014 | 0.156 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8861 | -9.5444
075083 | MV/LV Substation MO***083 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.014 | 4.38 |  | --> | 0.048 | 0 | 0.007 | 0.037 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.5275 | -6.4827
081101Z | MV/LV Substation FF***101Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.043 | 0.333 | 0 |  | --> | C18 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3482 | -6.4258
012440Y | MV/LV Substation ME***440Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 1.99 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C17 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8326 | -6.9481
176061Y | MV/LV Substation SU***061Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E12 ex HARTNETTS CROSS |  |  |  | 51.9051 | -8.9759
365228 | MV/LV Substation RA***228 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.38 | 0 | 0 | 0.346 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2817 | -6.4669
009905Y | MV/LV Substation AR***905Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 0.95 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2607 | -7.1522
160639 | MV/LV Substation TI***639 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C23 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1416 | -7.1594
365849X | MV/LV Substation CO***849X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =614 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2922 | -6.421
051849 | MV/LV Substation GO***849 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.22 |  | --> | 0.048 | 0 | 0.004 | 0.044 | 0 |  | --> | E20 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3119 | -7.5024
3654104 | MV/LV Substation MO***4104 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =895 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2947 | -6.4448
089106X | MV/LV Substation AB***106X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.1 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =575 kW | --> | C14 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1117 | -9.1493
029597Y | MV/LV Substation CH***597Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8296 | -8.0815
081369Z | MV/LV Substation TO***369Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =483 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3652 | -6.3888
050131 | MV/LV Substation HA***131 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =138 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C14 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4254 | -7.9527
355117X | MV/LV Substation FA***117X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 0.06 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C18 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0517 | -8.7126
136106Y | MV/LV Substation MU***106Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C18 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.5504 | -8.0648
067951Y | MV/LV Substation LI***951Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E21 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.741 | -8.782
164901X | MV/LV Substation RO***901X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.88 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C12 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5771 | -9.0692
028022Y | MV/LV Substation CH***022Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =387 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C13 ex COW CROSS |  |  |  | 51.8558 | -8.3218
093194 | MV/LV Substation BE***194 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.82 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3932 | -6.1954
062722X | MV/LV Substation CA***722X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 4.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E16 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 53.9941 | -6.2231
050242Y | MV/LV Substation WE***242Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4056 | -7.9837
099986 | MV/LV Substation B/***986 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.046 | 2.96 |  | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =76 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9863 | -7.7294
067222 | MV/LV Substation FO***222 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.024 | 0.346 | 0 |  | --> | C15 ex BALLINACURRA | Ballinacurra [T41,T42] | LIMERICK |  | 52.646 | -8.6349
144105X | MV/LV Substation CO***105X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C15 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.8661 | -7.1651
099065X | MV/LV Substation FO***065X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.196 | 5.45 |  | --> | 0.38 | 0 | 0.042 | 0 | 0 | Constrained, otherwise capacity available =320 kW | --> | C13 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.975 | -7.7299
164694X | MV/LV Substation CA***694X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C22 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5914 | -9.3785
365335 | MV/LV Substation BR***335 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.095 | 0 | 0.005 | 0.082 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2367 | -6.454
196738 | MV/LV Substation TR***738 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C15 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.565 | -6.8015
026566Y | MV/LV Substation MO***566Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 8.66 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7887 | -8.7936
068619X | MV/LV Substation GR***619X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.47 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.34 | -6.3205
288228 | MV/LV Substation BR***228 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.041 | 0.04 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C15 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2106 | -6.1031
058856 | MV/LV Substation TO***856 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.144 | 0.18 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C16 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.849 | -8.0336
052860 | MV/LV Substation RO***860 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =145 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E14 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4149 | -7.3056
255275X | MV/LV Substation RE***275X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.09 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C17 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6346 | -8.6469
025180Y | MV/LV Substation KI***180Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 6.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.3879 | -8.8581
081074Z | MV/LV Substation FO***074Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =202 kVA | --> | 0.38 | 0 | 0.025 | 0.334 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3494 | -6.4137
014861Z | MV/LV Substation NA***861Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0483 | -6.8357
238035Y | MV/LV Substation RO***035Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6303 | -9.1088
139915X | MV/LV Substation TO***915X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8653 | -7.3229
139348Y | MV/LV Substation DR***348Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7168 | -7.1526
014483Z | MV/LV Substation LA***483Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.075 | 0.63 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C17 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1371 | -6.7397
068253X | MV/LV Substation SO***253X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.319 | 17.78 |  | --> | 0.38 | 0 | 0 | 0.369 | 0 |  | --> | C12 ex RINGSEND | Ringsend [T101,T102] | POOLBEG |  | 53.3425 | -6.2035
068688 | MV/LV Substation SE***688 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.205 | 1.86 |  | --> | 0.38 | 0 | 0.03 | 0.33 | 0 |  | --> | C12 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3636 | -6.2022
093437Z | MV/LV Substation HA***437Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =522 kVA | --> | 0.598 | 0 | 0.019 | 0.5 | 0 |  | --> | C24 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4042 | -6.2839
034154Y | MV/LV Substation LA***154Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.57 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3792 | -7.7306
265213Y | MV/LV Substation MU***213Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.07 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.123 | -7.5792
064994Y | MV/LV Substation SO***994Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6795 | -6.2397
0624116 | MV/LV Substation NE***4116 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.69 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C14 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.9989 | -6.4042
204689 | MV/LV Substation FA***689 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.02 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.083 | -7.4618
009892Y | MV/LV Substation GL***892Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2505 | -7.0894
130255X | MV/LV Substation AR***255X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 2.55 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6665 | -7.6937
067120 | MV/LV Substation WE***120 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C11 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6488 | -8.6448
068689X | MV/LV Substation HI***689X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 17.78 |  | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C22 ex RINGSEND | Ringsend [T101,T102] | POOLBEG |  | 53.3391 | -6.2091
009161 | MV/LV Substation AB***161 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.296 | 8.16 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C13 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.261 | -7.0822
160831X | MV/LV Substation MO***831X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =15 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0938 | -7.1745
365232 | MV/LV Substation RA***232 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0.024 | 0.353 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.278 | -6.4808
031147Y | MV/LV Substation MI***147Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =347 kW | --> | E15 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0836 | -7.6371
047253 | MV/LV Substation I ***253 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 1.04 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =132 kW | --> | C15 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9758 | -8.2955
056995X | MV/LV Substation WA***995X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1011 | -8.0088
068455X | MV/LV Substation HA***455X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3446 | -6.2373
127515X | MV/LV Substation BA***515X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.7302 | -7.7787
032507 | MV/LV Substation GO***507 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =365 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.159 | -6.9893
0394036 | MV/LV Substation AN***4036 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =900 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =936 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2703 | -8.9301
118981 | MV/LV Substation BE***981 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3346 | -8.1399
030303 | MV/LV Substation CA***303 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =117 kVA | --> | 0.19 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9488 | -7.8476
1394222 | MV/LV Substation CO***4222 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8248 | -7.1828
068274X | MV/LV Substation AL***274X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.2 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3413 | -6.2467
005005 | MV/LV Substation CL***005 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C14 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6771 | -6.2799
056323 | MV/LV Substation RA***323 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1142 | -8.0217
433037X | MV/LV Substation HA***037X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.853 | -8.725
118846 | MV/LV Substation FO***846 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3867 | -8.3853
365182Y | MV/LV Substation KI***182Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2681 | -6.379
064063Z | MV/LV Substation DU***063Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =674 kVA | --> | 0.95 | 0 | 0.16 | 0 | 0 | Constrained, otherwise capacity available =786 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.663 | -6.4103
070918X | MV/LV Substation CL***918X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.63 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C14 ex CLOONBANNIN | Cloonbannin [T42] | GLENLARA |  | 52.114 | -9.0589
249091 | MV/LV Substation MI***091 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =123 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.0922 | -8.0062
082302Z | MV/LV Substation CA***302Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 1.82 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C15 ex RANDALSTOWN | Randalstown [T41] | NAVAN |  | 53.6719 | -6.813
056704X | MV/LV Substation PI***704X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1054 | -8.0504
233101 | MV/LV Substation TR***101 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2946 | -9.3934
052071Y | MV/LV Substation RA***071Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5104 | -7.1585
3654242 | MV/LV Substation RA***4242 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2761 | -6.487
051489X | MV/LV Substation SI***489X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 2.22 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | E20 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3222 | -7.53
065638 | MV/LV Substation DE***638 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5731 | -6.1978
011650Y | MV/LV Substation DE***650Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6069 | -6.9441
0504413 | MV/LV Substation IL***4413 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 6.49 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C20 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4276 | -7.8998
293556Z | MV/LV Substation FE***556Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 0.43 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7355 | -6.7737
365900X | MV/LV Substation CH***900X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.046 | 0.324 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2803 | -6.4748
065407Z | MV/LV Substation BA***407Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.02 | 0.359 | 0 |  | --> | C29 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5991 | -6.1834
068226X | MV/LV Substation BE***226X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 7.91 |  | --> | 0.38 | 0 | 0.016 | 0.358 | 0 |  | --> | C29 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3717 | -6.3311
065730 | MV/LV Substation RA***730 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5283 | -6.1525
066295X | MV/LV Substation MO***295X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.003 | 0.36 | 0 |  | --> | C17 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.403 | -6.2014
067916Y | MV/LV Substation TH***916Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C17 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6668 | -8.6155
0544521 | MV/LV Substation CO***4521 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C23 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0354 | -7.2967
255924 | MV/LV Substation GA***924 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.09 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6264 | -8.6005
127510X | MV/LV Substation KI***510X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =603 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6052 | -7.8403
0354075 | MV/LV Substation OG***4075 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.49 |  | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | E11 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.2947 | -8.052
288706 | MV/LV Substation BA***706 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =19 kVA | --> | 0.048 | 0 | 0.01 | 0.036 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2521 | -6.2249
001067X | MV/LV Substation FI***067X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 15.18 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2717 | -6.2042
065087 | MV/LV Substation HA***087 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0.068 | 0.315 | 0 |  | --> | C25 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6056 | -6.1666
153176X | MV/LV Substation KI***176X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | E13 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.739 | -8.5253
258431 | MV/LV Substation MA***431 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.86 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.1728 | -7.8996
001013 | MV/LV Substation ST***013 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.405 | 0.86 |  | --> | 0.598 | 0 | 0.053 | 0.5 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3111 | -6.2011
009240 | MV/LV Substation CO***240 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =141 kVA | --> | 0.19 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C12 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.2923 | -7.2508
3654064 | MV/LV Substation FO***4064 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =385 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C17 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2922 | -6.3753
066511 | MV/LV Substation BE***511 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5376 | -6.2496
154560Z | MV/LV Substation NO***560Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.598 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E14 ex CORDUFF |  |  |  | 53.4199 | -6.3443
405436 | MV/LV Substation C ***436 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2175 | -6.9475
0174340 | MV/LV Substation BA***4340 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5184 | -8.8096
119768X | MV/LV Substation CO***768X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1604 | -8.8153
068361 | MV/LV Substation EA***361 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.312 | 14.34 |  | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C31 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3539 | -6.2302
001254 | MV/LV Substation MO***254 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.236 | 1.16 |  | --> | 0.38 | 0 | 0.006 | 0.353 | 0 |  | --> | C19 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.3083 | -6.2144
249832 | MV/LV Substation AG***832 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 52.0724 | -7.827
055617X | MV/LV Substation KI***617X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.9326 | -7.5606
426007 | MV/LV Substation GO***007 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1659 | -10.4124
0934117 | MV/LV Substation ES***4117 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C24 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.3995 | -6.3009
099084X | MV/LV Substation DO***084X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.383 | 5.45 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C18 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.962 | -7.7126
060715Y | MV/LV Substation TO***715Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.9314 | -7.1015
021201Y | MV/LV Substation BA***201Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 52.0076 | -8.643
021366Z | MV/LV Substation TI***366Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0.015 | 0.175 | 0 |  | --> | C12 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9054 | -8.4298
013984Y | MV/LV Substation GA***984Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.121 | 0.12 | Constrained, otherwise capacity available =557 kVA | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | E62 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9965 | -6.9636
0664050 | MV/LV Substation MA***4050 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =431 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =571 kW | --> | C21 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4448 | -6.1626
243986 | MV/LV Substation CA***986 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E17 ex INCH | Inch [T421,T422] | OUGHTRAGH |  | 52.2321 | -9.9294
027553X | MV/LV Substation PR***553X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 7.79 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C11 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7123 | -9.1129
046164X | MV/LV Substation GR***164X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.158 | 4.13 |  | --> | 0.19 | 0 | 0.017 | 0.172 | 0 |  | --> | C13 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.4302 | -8.4499
238687 | MV/LV Substation BA***687 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =67 kW | --> | E13 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.7563 | -9.2825
0114426 | MV/LV Substation ST***4426 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.8 |  | --> | 0.95 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =913 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6363 | -7.2395
003932 | MV/LV Substation SA***932 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =53 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C11 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9299 | -6.2257
276449 | MV/LV Substation CL***449 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 0.76 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C12 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0359 | -9.4119
237579 | MV/LV Substation DU***579 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C18 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8292 | -6.3988
0324043 | MV/LV Substation KI***4043 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1793 | -7.3312
0714049 | MV/LV Substation BR***4049 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =423 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1517 | -6.0677
066826Z | MV/LV Substation ST***826Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4374 | -6.1806
041410X | MV/LV Substation LO***410X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7517 | -8.9715
014752X | MV/LV Substation K ***752X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1693 | -6.7542
021135 | MV/LV Substation KI***135 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =271 kVA | --> | 0.38 | 0 | 0.017 | 0.35 | 0 |  | --> | C12 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9243 | -8.4608
081170 | MV/LV Substation ME***170 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3317 | -6.3938
012490 | MV/LV Substation TI***490 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.7986 | -6.8993
0394011 | MV/LV Substation CE***4011 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =550 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2691 | -8.9286
002139 | MV/LV Substation PI***139 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.51 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1876 | -6.106
037302Y | MV/LV Substation FX***302Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =950 kW | --> | C19 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8755 | -8.9601
426846 | MV/LV Substation GO***846 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.14 | -10.2609
081235Z | MV/LV Substation EL***235Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3266 | -6.3942
137387 | MV/LV Substation BA***387 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.4036 | -9.8783
366393X | MV/LV Substation SL***393X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.197 | 0.45 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2647 | -9.6055
003009 | MV/LV Substation HU***009 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0065 | -6.0851
165650 | MV/LV Substation CA***650 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C12 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5836 | -8.9619
071055 | MV/LV Substation CO***055 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1502 | -6.1141
180539 | MV/LV Substation CA***539 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.138 | 3.27 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7504 | -6.9567
154127Z | MV/LV Substation CO***127Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C11 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4128 | -6.3672
061068 | MV/LV Substation GL***068 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 2.04 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C12 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1145 | -7.0091
028415 | MV/LV Substation BA***415 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C13 ex COW CROSS |  |  |  | 51.8602 | -8.3254
0824465 | MV/LV Substation DU***4465 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =353 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6445 | -6.6478
160915X | MV/LV Substation BA***915X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.05 | 0.149 | 0 |  | --> | C21 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0178 | -7.1165
118611X | MV/LV Substation HI***611X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E17 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3185 | -8.2416
127627X | MV/LV Substation PA***627X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.006 | 5.89 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C13 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5202 | -7.8842
281787X | MV/LV Substation PO***787X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =205 kVA | --> | 0.38 | 0 | 0.021 | 0.34 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8879 | -8.5796
1164005 | MV/LV Substation SL***4005 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.059 | 8.1 |  | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | E16 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.7917 | -9.5368
003532X | MV/LV Substation LA***532X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 53.0057 | -6.2983
137338X | MV/LV Substation TH***338X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C19 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.3924 | -9.8424
237143X | MV/LV Substation DR***143X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C12 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8979 | -6.387
405241 | MV/LV Substation IR***241 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 3.03 |  | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E12 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2045 | -6.9843
062611Y | MV/LV Substation OA***611Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.69 |  | --> | 0.598 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =556 kW | --> | C11 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.9993 | -6.3937
276283 | MV/LV Substation CA***283 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.094 | 0.76 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C18 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0398 | -9.4948
016244Z | MV/LV Substation GR***244Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.598 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =531 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.2989 | -6.4729
067498X | MV/LV Substation PA***498X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C16 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.6929 | -8.6237
119185 | MV/LV Substation CU***185 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1936 | -8.9045
059071 | MV/LV Substation MA***071 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =482 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C15 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9905 | -7.3581
365160X | MV/LV Substation P+***160X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0.008 | 0.37 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3218 | -6.4085
0824086 | MV/LV Substation LA***4086 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =144 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6364 | -6.6622
125893X | MV/LV Substation BA***893X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2574 | -8.2564
066120Z | MV/LV Substation WY***120Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =8 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5284 | -6.3127
065319Z | MV/LV Substation CO***319Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0.008 | 0.086 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5904 | -6.1868
156032 | MV/LV Substation AR***032 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.299 | 2.47 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E21 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2588 | -6.961
017022 | MV/LV Substation CR***022 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.007 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5245 | -8.7153
042916X | MV/LV Substation SP***916X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =615 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C13 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8521 | -9.2948
039664X | MV/LV Substation BL***664X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =496 kVA | --> | 0.598 | 0 | 0.065 | 0 | 0 | Constrained, otherwise capacity available =532 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.263 | -8.934
204444 | MV/LV Substation LE***444 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.0542 | -7.3115
067272X | MV/LV Substation JO***272X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.38 | 0 | 0.027 | 0.324 | 0 |  | --> | C19 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6644 | -8.6176
377006Y | MV/LV Substation GL***006Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0581 | -9.9351
117787X | MV/LV Substation CL***787X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.22 | -8.2771
164889 | MV/LV Substation WE***889 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.593 | -9.0749
007065 | MV/LV Substation CO***065 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =283 kVA | --> | 0.38 | 0 | 0.047 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3353 | -6.4676
0394275 | MV/LV Substation AP***4275 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0 | 0.365 | 0 |  | --> | C23 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2866 | -9.031
111026 | MV/LV Substation CE***026 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C16 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6767 | -9.4509
288074X | MV/LV Substation CO***074X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.341 | 1.16 |  | --> | 0.38 | 0 | 0.037 | 0.344 | 0 |  | --> | C17 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2771 | -6.215
009306Y | MV/LV Substation GR***306Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C12 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2429 | -7.1124
288895 | MV/LV Substation BU***895 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.367 | 1.16 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2767 | -6.2056
288628 | MV/LV Substation BA***628 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.011 | 0.037 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2537 | -6.2295
068292X | MV/LV Substation MA***292X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =905 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3515 | -6.254
031303 | MV/LV Substation SH***303 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0479 | -7.59
031745 | MV/LV Substation MO***745 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E16 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.1315 | -7.4695
046150 | MV/LV Substation BA***150 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 4.13 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C13 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.4219 | -8.4605
026692X | MV/LV Substation CA***692X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.6536 | -8.5951
039082 | MV/LV Substation SA***082 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =280 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C17 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2844 | -9.0405
365400X | MV/LV Substation DE***400X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =256 kVA | --> | 0.38 | 0 | 0.017 | 0.347 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3233 | -6.4255
007992X | MV/LV Substation RA***992X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.4 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2702 | -6.4788
0634057 | MV/LV Substation MU***4057 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8419 | -6.4769
059582Y | MV/LV Substation OL***582Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9667 | -7.3422
068516X | MV/LV Substation PE***516X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CAMDEN ROW | Camden Row [T41] | FRANCIS STREET |  | 53.3392 | -6.2667
209197 | MV/LV Substation CH***197 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.095 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0358 | -7.6447
0094333 | MV/LV Substation FO***4333 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2313 | -7.1362
2534193 | MV/LV Substation TH***4193 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.222 | 10.7 |  | --> | 0.38 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =331 kW | --> | C22 ex CLOON | Cloon [T42,T421] | CLOON |  | 53.5123 | -8.8522
0814063 | MV/LV Substation BA***4063 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.323 | -6.5934
109105 | MV/LV Substation CA***105 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 0.38 |  | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | C22 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.6909 | -8.9247
067154Z | MV/LV Substation HI***154Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =503 kVA | --> | 0.598 | 0 | 0.039 | 0 | 0 | Constrained, otherwise capacity available =552 kW | --> | C17 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6653 | -8.6327
293788Z | MV/LV Substation RU***788Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7924 | -6.7811
162035X | MV/LV Substation MI***035X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8073 | -7.5338
366325X | MV/LV Substation BR***325X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 1.47 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3249 | -9.8377
0014031 | MV/LV Substation BA***4031 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 15.18 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2711 | -6.2035
0814087 | MV/LV Substation RO***4087 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =232 kVA | --> | 0.38 | 0 | 0.094 | 0.287 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3636 | -6.4522
365848X | MV/LV Substation PO***848X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =188 kVA | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2451 | -6.5495
018952 | MV/LV Substation SI***952 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.013 | 3.75 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C18 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4128 | -9.5126
014278Z | MV/LV Substation RE***278Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1334 | -6.8427
182529 | MV/LV Substation TO***529 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =13 kW | --> | C11 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.8966 | -8.5402
037109Y | MV/LV Substation PL***109Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8249 | -8.9757
0064285 | MV/LV Substation GR***4285 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.38 |  | --> | 0.598 | 0 | 0.027 | 0.5 | 0 |  | --> | E13 ex CRANE | Crane [T122] | CRANE |  | 52.5072 | -6.5495
001069X | MV/LV Substation BL***069X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.392 | 15.18 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2718 | -6.2035
365081 | MV/LV Substation KI***081 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.139 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2786 | -6.3749
064086Z | MV/LV Substation ST***086Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =947 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =943 kW | --> | C20 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7164 | -6.3484
433101X | MV/LV Substation KI***101X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8808 | -8.4496
1604449 | MV/LV Substation RA***4449 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C14 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0406 | -7.2747
020304 | MV/LV Substation SP***304 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C18 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0671 | -9.6472
0504051 | MV/LV Substation BA***4051 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4565 | -7.9748
0684006 | MV/LV Substation CO***4006 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 14.34 |  | --> | 0.598 | 0 | 0 | 0.481 | 0 |  | --> | C23 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3485 | -6.239
065358Z | MV/LV Substation BR***358Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =344 kW | --> | C18 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5243 | -6.1053
048901 | MV/LV Substation WO***901 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.8813 | -7.8994
2934568 | MV/LV Substation CO***4568 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E13 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.748 | -6.5009
1524098 | MV/LV Substation CO***4098 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6085 | -8.2777
021992X | MV/LV Substation OS***992X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =626 kVA | --> | 0.598 | 0 | 0.2 | 0 | 0 | Constrained, otherwise capacity available =450 kW | --> | C22 ex KILBARRY |  |  |  | 51.914 | -8.4924
001021X | MV/LV Substation LA***021X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =694 kVA | --> | 0.95 | 0 | 0.05 | 0.5 | 0 |  | --> | C19 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3028 | -6.2425
053581Y | MV/LV Substation CA***581Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.017 | 0.035 | 0 |  | --> | E20 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2986 | -7.2808
003467Y | MV/LV Substation VA***467Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.416 | 11.58 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =569 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0123 | -6.1077
067754Y | MV/LV Substation DE***754Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C13 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6201 | -8.6527
067053 | MV/LV Substation BA***053 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 13.8 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6274 | -8.576
180124X | MV/LV Substation CR***124X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =53 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | C17 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.715 | -7.0203
093230 | MV/LV Substation SH***230 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.38 | 0 | 0.041 | 0.314 | 0 |  | --> | C11 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3877 | -6.2374
1574069 | MV/LV Substation BA***4069 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.36 | 1.55 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.058 | -7.7933
209881X | MV/LV Substation AR***881X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0713 | -7.6801
026975X | MV/LV Substation DE***975X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 8.66 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C20 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7514 | -8.829
2164028 | MV/LV Substation R ***4028 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C26 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7983 | -8.2935
0174322 | MV/LV Substation TA***4322 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 1.98 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5263 | -8.7133
062085 | MV/LV Substation CL***085 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.488 | 5.69 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =575 kW | --> | C20 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0058 | -6.4032
082939 | MV/LV Substation CL***939 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.021 | 0.64 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7875 | -6.7637
281701X | MV/LV Substation WI***701X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =461 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =575 kW | --> | C20 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.881 | -8.5076
154066Z | MV/LV Substation CA***066Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =110 kVA | --> | 0.19 | 0 | 0.022 | 0.161 | 0 |  | --> | C41 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4016 | -6.4254
0214219 | MV/LV Substation BA***4219 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =399 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9295 | -8.5958
068947X | MV/LV Substation CA***947X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C43 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3499 | -6.2327
005885X | MV/LV Substation PR***885X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C15 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6744 | -6.2903
032941X | MV/LV Substation BA***941X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2205 | -7.3748
005104Y | MV/LV Substation CO***104Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 17.8 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E21 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6583 | -6.3355
001643 | MV/LV Substation CO***643 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.041 | 0.04 | Constrained, otherwise capacity available =106 kVA | --> | 0.19 | 0 | 0.075 | 0.121 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2364 | -6.1123
046056 | MV/LV Substation HI***056 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 5.78 |  | --> | 0.38 | 0 | 0.05 | 0.328 | 0 |  | --> | C11 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2604 | -8.4685
132473Y | MV/LV Substation EA***473Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =519 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C17 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2042 | -8.5446
154574Z | MV/LV Substation LA***574Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3986 | -6.4322
018117Z | MV/LV Substation AS***117Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.112 | 3.75 |  | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =148 kW | --> | C12 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4475 | -9.502
015059 | MV/LV Substation AB***059 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =253 kVA | --> | 0.38 | 0 | 0.057 | 0 | 0 | Constrained, otherwise capacity available =317 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2919 | -6.6777
277074 | MV/LV Substation BU***074 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.22 | 12.96 |  | --> | 0.38 | 0 | 0 | 0.355 | 0 |  | --> | C23 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3852 | -6.2133
377198 | MV/LV Substation CR***198 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.1253 | -9.8964
127939X | MV/LV Substation SR***939X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.6014 | -7.9775
041339Y | MV/LV Substation CA***339Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E18 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6871 | -8.9798
266359 | MV/LV Substation RE***359 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.278 | -7.3974
162036X | MV/LV Substation MA***036X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 0.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8755 | -7.5851
0344240 | MV/LV Substation LI***4240 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.88 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C11 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.356 | -7.7074
015996Y | MV/LV Substation KE***996Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.379 | 12.6 |  | --> | 0.38 | 0 | 0.005 | 0.373 | 0 |  | --> | C20 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2352 | -6.6527
365134 | MV/LV Substation MI***134 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =483 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2804 | -6.4522
062986Y | MV/LV Substation GL***986Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0524 | -6.4289
4174069 | MV/LV Substation RO***4069 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0667 | -8.152
019367 | MV/LV Substation BA***367 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.015 | 1.54 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2452 | -9.7298
031144 | MV/LV Substation KI***144 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =432 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =564 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0927 | -7.6348
253657 | MV/LV Substation TO***657 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.607 | -8.5589
176117Y | MV/LV Substation FA***117Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 18.78 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | E11 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | HARTNETTS CROSS |  | 51.9099 | -8.9663
018198Z | MV/LV Substation SK***198Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 3.75 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C13 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4484 | -9.4414
041612 | MV/LV Substation CL***612 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7243 | -8.9789
033210Y | MV/LV Substation CO***210Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex PORTLAW | Portlaw [T41,T42] | BUTLERSTOWN |  | 52.2745 | -7.2956
365989X | MV/LV Substation ST***989X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2798 | -6.4683
066197 | MV/LV Substation ED***197 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.29 | 5.82 |  | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C19 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3887 | -6.1819
288351X | MV/LV Substation ST***351X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 15.18 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2773 | -6.2043
0554218 | MV/LV Substation AL***4218 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C13 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9571 | -7.801
132131Y | MV/LV Substation MO***131Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | E28 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2097 | -8.5169
334034 | MV/LV Substation RO***034 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.003 | 0.366 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.386 | -6.1589
014187X | MV/LV Substation CH***187X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2512 | -6.8422
064645 | MV/LV Substation PA***645 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.698 | -6.3074
252886 | MV/LV Substation BO***886 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.32 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C24 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.5214 | -10.1184
019014 | MV/LV Substation WE***014 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.332 | 2.18 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2736 | -9.7143
253678Y | MV/LV Substation CH***678Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | E21 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6405 | -8.6801
081601Z | MV/LV Substation PH***601Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.378 | 7.91 |  | --> | 0.598 | 0 | 0.028 | 0.5 | 0 |  | --> | C29 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3726 | -6.3407
001825 | MV/LV Substation TH***825 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =293 kVA | --> | 0.38 | 0 | 0.028 | 0.344 | 0 |  | --> | C19 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3077 | -6.2418
082974 | MV/LV Substation WI***974 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 0.64 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7387 | -6.7183
365964X | MV/LV Substation CI***964X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =740 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2859 | -6.4506
281681Z | MV/LV Substation GA***681Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =285 kVA | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8697 | -8.3971
041506 | MV/LV Substation PO***506 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6866 | -9.0864
142475X | MV/LV Substation AT***475X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E23 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.3085 | -8.653
144029 | MV/LV Substation GR***029 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.452 | 2.78 |  | --> | 0.598 | 0 | 0.042 | 0 | 0 | Constrained, otherwise capacity available =543 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7866 | -7.3314
192008 | MV/LV Substation EU***008 |  | 10 kV | _ | LV | 50 kVA :Building Structure | 0.05 | --> | 0.05 | 0.032 | 1.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0651 | -8.2859
017034Y | MV/LV Substation CA***034Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E12 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4602 | -8.995
031876 | MV/LV Substation SC***876 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2059 | -7.4021
066224Z | MV/LV Substation KI***224Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4397 | -6.2246
093138Z | MV/LV Substation ST***138Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =489 kVA | --> | 0.598 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =562 kW | --> | C17 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4002 | -6.3412
066875X | MV/LV Substation CO***875X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5267 | -6.2078
060660Y | MV/LV Substation SC***660Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C16 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1848 | -7.2272
039832X | MV/LV Substation CR***832X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.147 | 11.03 |  | --> | 0.19 | 0 | 0.031 | 0.16 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2527 | -9.1547
253044Z | MV/LV Substation BA***044Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6086 | -8.5604
066320Z | MV/LV Substation BR***320Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =460 kVA | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3845 | -6.1642
005094 | MV/LV Substation AU***094 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =239 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =548 kW | --> | C15 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6766 | -6.2925
074173 | MV/LV Substation LA***173 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C16 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.8198 | -8.1098
150272X | MV/LV Substation ME***272X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8658 | -8.0433
014911 | MV/LV Substation BA***911 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 0.63 |  | --> | 0.095 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =72 kW | --> | C16 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.123 | -6.8298
004030 | MV/LV Substation BE***030 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.105 | 18.08 |  | --> | 0.19 | 0 | 0.004 | 0.174 | 0 |  | --> | C19 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8077 | -6.1398
009583X | MV/LV Substation NO***583X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.207 | 0.95 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =347 kW | --> | C18 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2556 | -7.1396
039732X | MV/LV Substation GO***732X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C13 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2847 | -9.0477
039407X | MV/LV Substation TE***407X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =791 kVA | --> | 0.95 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =917 kW | --> | C13 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2857 | -9.0445
180854X | MV/LV Substation HE***854X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C26 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7224 | -6.854
365531X | MV/LV Substation BU***531X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.021 | 0.343 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3101 | -6.4061
365012Y | MV/LV Substation RA***012Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C29 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.291 | -6.4811
293420Z | MV/LV Substation TY***420Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.8886 | -6.6155
066192Y | MV/LV Substation BU***192Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =444 kVA | --> | 0.598 | 0 | 0.078 | 0 | 0 | Constrained, otherwise capacity available =515 kW | --> | E20 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.517 | -6.411
093169Z | MV/LV Substation TU***169Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0 | 0.367 | 0 |  | --> | C13 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.418 | -6.2862
093190 | MV/LV Substation CA***190 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.38 | 0 | 0.015 | 0.34 | 0 |  | --> | C12 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3867 | -6.3125
293196X | MV/LV Substation AR***196X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E13 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.755 | -6.5291
154599Z | MV/LV Substation BA***599Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =519 kVA | --> | 0.598 | 0 | 0.054 | 0.5 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3921 | -6.444
0654380 | MV/LV Substation GO***4380 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =629 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5268 | -6.0955
007399 | MV/LV Substation CR***399 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.143 | 0.14 | Constrained, otherwise capacity available =328 kVA | --> | 0.38 | 0 | 0.069 | 0 | 0 | Constrained, otherwise capacity available =319 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3533 | -6.4561
066617 | MV/LV Substation EL***617 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5368 | -6.2706
099162X | MV/LV Substation FR***162X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9548 | -7.8501
1614099 | MV/LV Substation AI***4099 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex SPIDDAL |  |  |  | 53.2469 | -9.3834
064632X | MV/LV Substation LA***632X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6579 | -6.4218
045010X | MV/LV Substation CL***010X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.032 | 2.45 |  | --> | 0.095 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C20 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9973 | -8.5245
067068Y | MV/LV Substation CH***068Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.19 | 0 | 0.093 | 0.106 | 0 |  | --> | C20 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6246 | -8.6511
139256 | MV/LV Substation GA***256 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E21 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8402 | -7.3701
049402Z | MV/LV Substation FA***402Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.31 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7723 | -8.1076
039893 | MV/LV Substation TU***893 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =536 kVA | --> | 0.598 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =541 kW | --> | C14 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2838 | -9.0372
288323X | MV/LV Substation BA***323X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.01 | 0.176 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2564 | -6.1896
366513 | MV/LV Substation OS***513 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.47 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3265 | -9.8392
288230 | MV/LV Substation CO***230 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2751 | -6.2128
0734119 | MV/LV Substation BA***4119 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C16 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.4202 | -7.6544
017451 | MV/LV Substation KI***451 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4934 | -8.7911
0684009 | MV/LV Substation SA***4009 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.02 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3464 | -6.242
060020 | MV/LV Substation NE***020 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C16 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1801 | -7.2382
068870 | MV/LV Substation DU***870 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.14 |  | --> | 0.598 | 0 | 0.004 | 0.5 | 0 |  | --> | C11 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3594 | -6.3022
001267 | MV/LV Substation GR***267 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.313 | 13.42 |  | --> | 0.38 | 0 | 0.041 | 0.338 | 0 |  | --> | C20 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2642 | -6.1432
125827 | MV/LV Substation KI***827 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C20 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2429 | -8.2782
039652 | MV/LV Substation CA***652 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C20 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.3024 | -8.9255
001068X | MV/LV Substation BL***068X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 15.18 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CENTRAL PARK | Central Park [T101,T102] | CARRICKMINES |  | 53.2717 | -6.2035
001209 | MV/LV Substation DA***209 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.03 | 4.01 |  | --> | 0.095 | 0 | 0.029 | 0.063 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2715 | -6.1119
068378X | MV/LV Substation RE***378X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =781 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3766 | -6.2423
366447 | MV/LV Substation GA***447 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 1.47 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3602 | -9.6235
081055X | MV/LV Substation KY***055X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =252 kVA | --> | 0.38 | 0 | 0 | 0.359 | 0 |  | --> | C17 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3364 | -6.3484
015886Y | MV/LV Substation SU***886Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C14 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2149 | -6.6647
032124 | MV/LV Substation GA***124 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C21 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1738 | -7.3485
055998 | MV/LV Substation BA***998 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9442 | -7.5916
062785Y | MV/LV Substation MU***785Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.32 | 3.12 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C12 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9844 | -6.4
065367Z | MV/LV Substation HO***367Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5592 | -6.2598
108588 | MV/LV Substation AS***588 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.178 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.4968 | -8.1734
011044 | MV/LV Substation WI***044 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.004 | 5.05 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =150 kW | --> | C13 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.655 | -7.2402
503768 | MV/LV Substation MU***768 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9731 | -7.5845
064945X | MV/LV Substation IN***945X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =268 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C19 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7054 | -6.3603
081242X | MV/LV Substation KN***242X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C12 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3672 | -6.3745
005987X | MV/LV Substation CL***987X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6829 | -6.27
366246X | MV/LV Substation CA***246X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 1.47 |  | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3248 | -9.8396
0564135 | MV/LV Substation CL***4135 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1011 | -7.9811
132206Y | MV/LV Substation BA***206Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =557 kVA | --> | 0.598 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =568 kW | --> | C16 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.1941 | -8.5562
009343Y | MV/LV Substation SE***343Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =374 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C21 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2429 | -7.1324
052639Y | MV/LV Substation SO***639Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.6093 | -7.0635
160821Y | MV/LV Substation LA***821Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1616 | -7.5631
0114039 | MV/LV Substation DU***4039 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6334 | -7.1483
116344Y | MV/LV Substation KN***344Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 7.32 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C12 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7683 | -9.5197
253270Y | MV/LV Substation CA***270Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C17 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5077 | -8.8357
031082 | MV/LV Substation SI***082 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0894 | -7.6387
165925X | MV/LV Substation SA***925X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 0.88 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C12 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5679 | -8.9997
009469Y | MV/LV Substation BA***469Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 0.53 | Constrained, otherwise capacity available =843 kVA | --> | 0.95 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =919 kW | --> | C22 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2599 | -7.1112
182235 | MV/LV Substation WH***235 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.949 | -8.3751
046063 | MV/LV Substation E ***063 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =402 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.271 | -8.472
139101X | MV/LV Substation KI***101X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.148 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C19 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8433 | -7.2077
001196X | MV/LV Substation HA***196X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.476 | 4.37 |  | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C19 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2949 | -6.1405
062643Y | MV/LV Substation OM***643Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.168 | 4.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E18 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0878 | -6.2625
050941Y | MV/LV Substation SO***941Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.15 | 7.61 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4272 | -7.9206
2764052 | MV/LV Substation IR***4052 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0038 | -9.4574
111508Z | MV/LV Substation SL***508Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C12 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6843 | -9.4345
109020 | MV/LV Substation RI***020 |  | 10 kV | _ | LV | 50 kVA :Building Structure | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =12 kVA | --> | 0.048 | 0 | 0 | 0.042 | 0 |  | --> | C16 ex SHANNON | Shannon [T41,T42] | DRUMLINE |  | 52.6979 | -8.9063
052044 | MV/LV Substation LY***044 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.195 | 10.9 |  | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C12 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5219 | -7.3391
127537Y | MV/LV Substation TE***537Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C18 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6857 | -7.8305
281565Y | MV/LV Substation PR***565Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.382 | 4.3 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C17 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.834 | -8.3319
007453X | MV/LV Substation MO***453X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C20 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3157 | -6.4834
081199X | MV/LV Substation CH***199X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =261 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C13 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3457 | -6.3752
209058X | MV/LV Substation PE***058X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C21 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1756 | -7.7861
111615Y | MV/LV Substation SE***615Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =540 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6817 | -9.4569
064829X | MV/LV Substation BR***829X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0.063 | 0 | 0 | Constrained, otherwise capacity available =309 kW | --> | C20 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7249 | -6.3455
176001Y | MV/LV Substation ST***001Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.051 | 18.78 |  | --> | 0.095 | 0 | 0.005 | 0.084 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9422 | -9.1583
142039X | MV/LV Substation CL***039X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =125 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C17 ex ATHENRY |  |  |  | 53.3109 | -8.7346
099056X | MV/LV Substation ER***056X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.109 | 2.96 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9847 | -7.7231
045114X | MV/LV Substation OD***114X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.187 | 2.45 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C18 ex GURTEEN | Gurteen [T41] | TONROE |  | 53.9886 | -8.4879
265159Y | MV/LV Substation LA***159Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.07 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1178 | -7.4833
067023Z | MV/LV Substation DR***023Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 13.8 |  | --> | 0.048 | 0 | 0.011 | 0.039 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.627 | -8.5724
160047 | MV/LV Substation CO***047 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C15 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1577 | -7.1871
426456 | MV/LV Substation BA***456 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E15 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1657 | -10.407
0234199 | MV/LV Substation CU***4199 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1934 | -8.3217
196706 | MV/LV Substation BU***706 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5607 | -6.8003
0234039 | MV/LV Substation AC***4039 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.149 | -8.3292
019625 | MV/LV Substation KY***625 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.047 | 0.05 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C12 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2724 | -9.6358
250505 | MV/LV Substation BA***505 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C27 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1585 | -8.3
154326 | MV/LV Substation AS***326 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.38 | 0 | 0.056 | 0 | 0 | Constrained, otherwise capacity available =308 kW | --> | C20 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.4023 | -6.4059
073001 | MV/LV Substation CH***001 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.38 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =315 kW | --> | C15 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.3958 | -7.724
281375X | MV/LV Substation CO***375X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.05 | 4.3 |  | --> | 0.095 | 0 | 0.01 | 0.08 | 0 |  | --> | C19 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8561 | -8.3359
006656Y | MV/LV Substation NA***656Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.115 | 3.12 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C17 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5028 | -6.576
120736Y | MV/LV Substation FA***736Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.2819 | -7.2039
031010 | MV/LV Substation RI***010 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.048 | 0 | 0 | Constrained, otherwise capacity available =148 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0477 | -7.5918
253325X | MV/LV Substation LI***325X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =275 kVA | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C17 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5234 | -8.8589
067807Y | MV/LV Substation CU***807Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0.004 | 0.184 | 0 |  | --> | C14 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.631 | -8.66
256971 | MV/LV Substation HA***971 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.28 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7497 | -8.4785
009676 | MV/LV Substation FI***676 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C12 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.2904 | -7.2518
120453Y | MV/LV Substation HA***453Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.324 | 3.5 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4013 | -6.8552
154454Z | MV/LV Substation D.***454Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.4156 | -6.4787
1204266 | MV/LV Substation CA***4266 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 3.5 |  | --> | 0.095 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =54 kW | --> | E12 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4422 | -6.9502
078128X | MV/LV Substation PU***128X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9236 | -8.8391
162599 | MV/LV Substation CO***599 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.133 | 0.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8031 | -7.5855
0154154 | MV/LV Substation OL***4154 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 12.6 |  | --> | 0.38 | 0 | 0.016 | 0.355 | 0 |  | --> | C14 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2343 | -6.6682
377065 | MV/LV Substation GL***065 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E16 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.7593 | -10.0918
152601X | MV/LV Substation MU***601X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6972 | -8.4096
151064X | MV/LV Substation BA***064X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3753 | -8.3525
093066 | MV/LV Substation PL***066 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0.005 | 0.349 | 0 |  | --> | C20 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3974 | -6.3133
059727X | MV/LV Substation CA***727X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E11 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.022 | -7.2899
1964009 | MV/LV Substation EP***4009 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.6235 | -6.8587
060281X | MV/LV Substation SK***281X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.948 | -7.0121
015658Z | MV/LV Substation NA***658Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2473 | -6.6381
030923 | MV/LV Substation MI***923 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9455 | -7.8586
028496 | MV/LV Substation ED***496 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 19.7 |  | --> | 0.19 | 0 | 0.01 | 0.18 | 0 |  | --> | C12 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8542 | -8.2967
042711X | MV/LV Substation TU***711X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8836 | -9.2137
035089Y | MV/LV Substation RO***089Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 0.49 |  | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3103 | -7.8908
022620X | MV/LV Substation BA***620X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1662 | -8.7411
066251Z | MV/LV Substation CA***251Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4716 | -6.2385
046841 | MV/LV Substation ST***841 |  | 10 kV | _ | LV | 50 kVA :Building Structure | 0.05 | --> | 0.05 | 0.028 | 4.13 |  | --> | 0.048 | 0 | 0.022 | 0.028 | 0 |  | --> | C18 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.4023 | -8.5655
120888X | MV/LV Substation CL***888X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3463 | -7.0474
059245Y | MV/LV Substation DR***245Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E17 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0342 | -7.3695
281865X | MV/LV Substation TH***865X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8009 | -8.2914
0644366 | MV/LV Substation SM***4366 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6755 | -6.2939
136703Y | MV/LV Substation AS***703Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C17 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6221 | -8.1989
065391Z | MV/LV Substation KI***391Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E14 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5503 | -6.4482
2814332 | MV/LV Substation SL***4332 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C21 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.7727 | -8.4374
0684289 | MV/LV Substation RA***4289 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.47 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3419 | -6.2838
041015 | MV/LV Substation BA***015 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E12 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7226 | -8.9905
066879Z | MV/LV Substation FO***879Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4432 | -6.2593
039582X | MV/LV Substation RO***582X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 3.45 |  | --> | 0.38 | 0 | 0.01 | 0.362 | 0 |  | --> | C21 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2677 | -9.0748
035445X | MV/LV Substation MO***445X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 0.49 |  | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.337 | -7.8027
058288Y | MV/LV Substation NE***288Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8602 | -8.2073
139418Y | MV/LV Substation AR***418Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.922 | -7.3426
116056 | MV/LV Substation QU***056 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 7.32 |  | --> | 0.095 | 0 | 0.013 | 0.08 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.798 | -9.5477
043158 | MV/LV Substation KI***158 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C20 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.87 | -8.8537
1204240 | MV/LV Substation MC***4240 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =25 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3003 | -7.2288
054929Y | MV/LV Substation KN***929Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 53.0502 | -7.4497
132236Y | MV/LV Substation BL***236Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E30 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2314 | -8.7322
059981 | MV/LV Substation CA***981 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E11 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0312 | -7.2741
154324 | MV/LV Substation AS***324 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =262 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =333 kW | --> | C20 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.4001 | -6.4029
281123X | MV/LV Substation BO***123X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.223 | 4.67 |  | --> | 0.38 | 0 | 0.082 | 0.294 | 0 |  | --> | C20 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8922 | -8.4596
417807 | MV/LV Substation AG***807 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0644 | -8.0893
116947X | MV/LV Substation SU***947X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.174 | 7.32 |  | --> | 0.38 | 0 | 0 | 0.348 | 0 |  | --> | C13 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7982 | -9.5244
003753X | MV/LV Substation WO***753X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.19 | 11.58 |  | --> | 0.38 | 0 | 0.212 | 0 | 0 | Constrained, otherwise capacity available =193 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0039 | -6.1079
084883 | MV/LV Substation DU***883 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1391 | -8.9301
0414133 | MV/LV Substation LU***4133 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E21 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7389 | -9.0139
1524163 | MV/LV Substation GL***4163 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6343 | -8.3951
066257Z | MV/LV Substation AP***257Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =406 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =567 kW | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4698 | -6.2302
081588X | MV/LV Substation WI***588X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.077 | 0.305 | 0 |  | --> | C13 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3554 | -6.4267
019119 | MV/LV Substation ST***119 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =265 kVA | --> | 0.38 | 0 | 0.071 | 0 | 0 | Constrained, otherwise capacity available =309 kW | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2687 | -9.6961
417136 | MV/LV Substation EI***136 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0852 | -8.1688
0684007 | MV/LV Substation MA***4007 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3497 | -6.2573
048178X | MV/LV Substation DR***178X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 2.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.861 | -7.9164
081605Y | MV/LV Substation KI***605Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3647 | -6.5604
281271Z | MV/LV Substation GR***271Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.36 | 4.3 |  | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C19 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.866 | -8.3311
0474020 | MV/LV Substation LA***4020 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.085 | 1.04 |  | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9804 | -8.2804
011296Z | MV/LV Substation CL***296Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =301 kVA | --> | 0.38 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =342 kW | --> | C19 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6391 | -7.2527
017738Y | MV/LV Substation BA***738Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4825 | -9.032
1184127 | MV/LV Substation ST***4127 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3365 | -8.1946
0464167 | MV/LV Substation BA***4167 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.48 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3062 | -8.5322
293918Z | MV/LV Substation GR***918Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 2.83 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E18 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7119 | -6.8462
0274173 | MV/LV Substation GL***4173 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.79 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7926 | -9.0562
039067 | MV/LV Substation TA***067 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.06 | 3.45 |  | --> | 0.19 | 0 | 0.035 | 0.144 | 0 |  | --> | C21 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2687 | -9.0714
025384 | MV/LV Substation NE***384 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 2.96 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E14 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3445 | -8.7666
1174177 | MV/LV Substation OA***4177 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2089 | -8.5113
039489X | MV/LV Substation BA***489X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3.45 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2594 | -9.0777
3654115 | MV/LV Substation CU***4115 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0.078 | 0.316 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3252 | -6.4169
058117Y | MV/LV Substation BA***117Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 53.0235 | -8.2221
007245 | MV/LV Substation SL***245 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =12 kVA | --> | 0.048 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =8 kW | --> | C11 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3395 | -6.4783
0714094 | MV/LV Substation MA***4094 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.58 |  | --> | 0.598 | 0 | 0.012 | 0.5 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0919 | -6.1179
293379Z | MV/LV Substation KI***379Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 2.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7167 | -6.8971
009724Y | MV/LV Substation NA***724Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =147 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C15 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.3144 | -7.1793
293463Z | MV/LV Substation GA***463Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 2.83 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E13 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6757 | -6.8431
029552X | MV/LV Substation FA***552X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =8 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C32 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8401 | -8.1383
252572 | MV/LV Substation ST***572 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.008 | 1.32 |  | --> | 0.048 | 0 | 0 | 0.041 | 0 |  | --> | C24 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.507 | -9.9371
015991 | MV/LV Substation DI***991 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C19 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2621 | -6.7055
047057X | MV/LV Substation BO***057X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9799 | -8.2975
093609Z | MV/LV Substation SA***609Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C17 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4063 | -6.2603
001173X | MV/LV Substation IR***173X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.37 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2966 | -6.1398
0814365 | MV/LV Substation PA***4365 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =534 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | E21 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3319 | -6.4107
196091 | MV/LV Substation MU***091 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.6332 | -6.8942
029665 | MV/LV Substation PU***665 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9389 | -8.2764
039046 | MV/LV Substation DA***046 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.297 | 11.03 |  | --> | 0.38 | 0 | 0.043 | 0.334 | 0 |  | --> | C19 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2606 | -9.0816
070470 | MV/LV Substation CU***470 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 2.63 |  | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C14 ex CLOONBANNIN | Cloonbannin [T42] | GLENLARA |  | 52.114 | -9.1228
001012 | MV/LV Substation BO***012 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.362 | 0.86 |  | --> | 0.598 | 0 | 0.073 | 0.5 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3032 | -6.1992
010238 | MV/LV Substation ST***238 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.4878 | -6.9295
010023 | MV/LV Substation DA***023 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5263 | -7.1324
192571 | MV/LV Substation ST***571 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.126 | 1.56 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0214 | -8.3198
244773X | MV/LV Substation MI***773X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E11 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1441 | -9.7123
029566Y | MV/LV Substation AB***566Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =385 kVA | --> | 0.38 | 0 | 0.04 | 0.348 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9139 | -8.1877
068004 | MV/LV Substation PA***004 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.205 | 4.6 |  | --> | 0.598 | 0 | 0.009 | 0.5 | 0 |  | --> | C18 ex KINGSBRIDGE | Kingsbridge [T41,T42] | INCHICORE 220KV |  | 53.3477 | -6.2924
046019 | MV/LV Substation YE***019 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.064 | 5.48 |  | --> | 0.095 | 0 | 0 | 0.09 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2814 | -8.4499
082579X | MV/LV Substation KI***579X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.192 | 0.64 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.7038 | -6.6865
038011 | MV/LV Substation GO***011 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =55 kVA | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =157 kW | --> | C16 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0641 | -8.8223
144356X | MV/LV Substation CA***356X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C16 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.8036 | -7.2151
032173Y | MV/LV Substation PI***173Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1774 | -7.1411
288139 | MV/LV Substation CL***139 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.055 | 0.321 | 0 |  | --> | C11 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2765 | -6.2346
365449X | MV/LV Substation HA***449X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =276 kVA | --> | 0.38 | 0 | 0.023 | 0.346 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3116 | -6.404
281714Z | MV/LV Substation MA***714Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =365 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C18 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8706 | -8.4287
158253X | MV/LV Substation IN***253X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | C20 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.8777 | -9.1778
055717 | MV/LV Substation SH***717 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =139 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E22 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9823 | -7.9336
052369Z | MV/LV Substation WO***369Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.5059 | -7.4521
151524X | MV/LV Substation TI***524X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.4024 | -8.2966
111766Z | MV/LV Substation HE***766Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C11 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.681 | -9.4219
253573Y | MV/LV Substation CO***573Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6714 | -8.5703
0594006 | MV/LV Substation GO***4006 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9442 | -7.4285
073805 | MV/LV Substation CA***805 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =29 kW | --> | C15 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.4282 | -7.7787
016169Z | MV/LV Substation GR***169Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =700 kVA | --> | 0.95 | 0 | 0.066 | 0 | 0 | Constrained, otherwise capacity available =859 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2988 | -6.4784
017449Z | MV/LV Substation DE***449Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.4511 | -9.0662
049301Z | MV/LV Substation WE***301Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.213 | 0.21 | Constrained, otherwise capacity available =391 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E11 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7149 | -7.8119
054611Y | MV/LV Substation FO***611Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0433 | -7.2833
081277Z | MV/LV Substation N ***277Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3339 | -6.5576
022796X | MV/LV Substation BR***796X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.319 | 4.55 |  | --> | 0.38 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =355 kW | --> | C21 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1539 | -8.6305
026715Y | MV/LV Substation MI***715Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.357 | 8.66 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C20 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7445 | -8.7987
2384151 | MV/LV Substation FR***4151 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6288 | -9.2091
265796 | MV/LV Substation SW***796 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.066 | 0.07 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E17 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1905 | -7.7028
056924X | MV/LV Substation SH***924X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0855 | -8.1016
0694010 | MV/LV Substation EL***4010 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =604 kVA | --> | 0.598 | 0 | 0.064 | 0.5 | 0 |  | --> | C13 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2927 | -6.2757
151468X | MV/LV Substation CL***468X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =147 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3702 | -8.3408
151091X | MV/LV Substation ST***091X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C16 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3615 | -8.4734
0034216 | MV/LV Substation BR***4216 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.174 | 11.58 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.8913 | -6.0564
253096X | MV/LV Substation MO***096X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.4883 | -8.5815
069334 | MV/LV Substation LA***334 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.33 | 2.93 |  | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C20 ex DODDER ROAD | Dodder Road [T42] | MILLTOWN (DR) |  | 53.2992 | -6.2683
119577X | MV/LV Substation KN***577X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.2765 | -8.8704
281048 | MV/LV Substation CL***048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =248 kVA | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C19 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8904 | -8.4169
154307Y | MV/LV Substation SA***307Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.069 | 0.128 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4226 | -6.4826
026089 | MV/LV Substation BA***089 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =156 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7092 | -8.5216
009267X | MV/LV Substation MU***267X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.162 | 8.16 |  | --> | 0.19 | 0 | 0.048 | 0 | 0 | Constrained, otherwise capacity available =149 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2848 | -7.1145
137042 | MV/LV Substation CA***042 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 3.74 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3542 | -9.6302
051551 | MV/LV Substation LO***551 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.22 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E17 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3826 | -7.4912
142976X | MV/LV Substation CL***976X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =371 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C17 ex ATHENRY |  |  |  | 53.3099 | -8.7375
281317 | MV/LV Substation CA***317 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =194 kVA | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.897 | -8.5506
254450 | MV/LV Substation LO***450 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6762 | -8.5808
0214253 | MV/LV Substation LE***4253 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.192 | 6.78 |  | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C41 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9043 | -8.3899
026627Y | MV/LV Substation MA***627Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.447 | 8.66 |  | --> | 0.598 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | C11 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7443 | -8.7374
063144X | MV/LV Substation CH***144X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C18 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.9153 | -6.4867
022743 | MV/LV Substation CU***743 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 4.55 |  | --> | 0.095 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =59 kW | --> | C14 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1794 | -8.6323
0094087 | MV/LV Substation KI***4087 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =301 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C30 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2472 | -7.128
067875Y | MV/LV Substation AS***875Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C11 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6533 | -8.6488
156863Y | MV/LV Substation VO***863Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3339 | -7.0935
052001 | MV/LV Substation DO***001 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.9 |  | --> | 0.95 | 0 | 0.011 | 0.5 | 0 |  | --> | C12 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5239 | -7.3442
251126X | MV/LV Substation GO***126X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =315 kVA | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C30 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3983 | -8.9902
025733 | MV/LV Substation BA***733 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 6.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.4051 | -8.7939
244144 | MV/LV Substation KN***144 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1417 | -9.7198
046715 | MV/LV Substation RO***715 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 5.48 |  | --> | 0.19 | 0 | 0.014 | 0.174 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3102 | -8.5499
162146X | MV/LV Substation BR***146X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8219 | -7.6012
054901 | MV/LV Substation BA***901 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.8781 | -7.4598
035822X | MV/LV Substation MO***822X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 6.17 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3755 | -7.8376
137334 | MV/LV Substation CL***334 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C12 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.4584 | -9.727
066308Z | MV/LV Substation TH***308Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.19 | 0 | 0.068 | 0 | 0 | Constrained, otherwise capacity available =127 kW | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4217 | -6.1307
156390Y | MV/LV Substation KI***390Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.267 | -7.0539
154527Z | MV/LV Substation CH***527Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0.032 | 0.341 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4325 | -6.3758
019405 | MV/LV Substation CU***405 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C14 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2847 | -9.699
068605 | MV/LV Substation WA***605 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =270 kVA | --> | 0.38 | 0 | 0.066 | 0.313 | 0 |  | --> | C17 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.379 | -6.2524
0044211 | MV/LV Substation HA***4211 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.057 | 18.08 |  | --> | 0.095 | 0 | 0 | 0.089 | 0 |  | --> | C13 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8114 | -6.1902
237957 | MV/LV Substation DR***957 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C12 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.912 | -6.4047
059204Y | MV/LV Substation LE***204Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9643 | -7.4506
066653Z | MV/LV Substation KI***653Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =983 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =948 kW | --> | E15 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5114 | -6.4017
0814131 | MV/LV Substation PH***4131 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.91 |  | --> | 0.598 | 0 | 0.008 | 0.5 | 0 |  | --> | C29 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3722 | -6.3391
025098X | MV/LV Substation LY***098X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 1.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3589 | -8.9978
0654007 | MV/LV Substation HY***4007 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5763 | -6.2823
1364195 | MV/LV Substation RO***4195 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6474 | -8.1717
001003 | MV/LV Substation SH***003 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =269 kVA | --> | 0.38 | 0 | 0.043 | 0.33 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2355 | -6.1261
064772Y | MV/LV Substation WO***772Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.731 | -6.4738
037105Y | MV/LV Substation KI***105Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 13.05 |  | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C19 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8277 | -8.9346
081005Z | MV/LV Substation FI***005Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =244 kVA | --> | 0.38 | 0 | 0.021 | 0.343 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3392 | -6.4509
288338X | MV/LV Substation TH***338X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =391 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2508 | -6.1833
139415Y | MV/LV Substation BO***415Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7662 | -7.1325
144464 | MV/LV Substation GR***464 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.78 |  | --> | 0.048 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7499 | -7.392
074239X | MV/LV Substation CA***239X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =568 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9418 | -8.0999
028032Y | MV/LV Substation CL***032Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 19.7 |  | --> | 0.38 | 0 | 0.035 | 0.341 | 0 |  | --> | C12 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8551 | -8.3056
281673 | MV/LV Substation CU***673 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C24 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8477 | -8.4311
084344X | MV/LV Substation CL***344X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =356 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C18 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.2271 | -8.8809
152719X | MV/LV Substation BO***719X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6698 | -8.4038
281049Z | MV/LV Substation BL***049Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C21 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8801 | -8.4235
050235 | MV/LV Substation DE***235 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.223 | 6.49 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =355 kW | --> | C18 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4321 | -7.9078
007452 | MV/LV Substation CU***452 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.019 | 16.12 |  | --> | 0.095 | 0 | 0.008 | 0.077 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3931 | -6.3888
0134110 | MV/LV Substation TH***4110 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C21 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9742 | -7.0703
165019 | MV/LV Substation FE***019 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0.039 | 0 | 0 | Constrained, otherwise capacity available =154 kW | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6274 | -8.9071
254261 | MV/LV Substation TH***261 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5146 | -8.8657
024811X | MV/LV Substation TO***811X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.361 | 2.14 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C18 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2323 | -8.6767
066340X | MV/LV Substation PO***340X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =157 kW | --> | C15 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4121 | -6.1267
365597X | MV/LV Substation CA***597X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.012 | 0.172 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2829 | -6.3273
0694028 | MV/LV Substation LI***4028 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.91 |  | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C12 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3094 | -6.2822
014820Z | MV/LV Substation WH***820Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =761 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =917 kW | --> | C20 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1788 | -6.7981
156876X | MV/LV Substation DE***876X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3575 | -7.0239
081665 | MV/LV Substation WE***665 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =109 kVA | --> | 0.19 | 0 | 0 | 0.177 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.374 | -6.44
064675 | MV/LV Substation TO***675 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7289 | -6.4459
122919 | MV/LV Substation SH***919 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 4.18 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9096 | -6.809
4294147 | MV/LV Substation BA***4147 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CHURCHTOWN | Churchtown [T422] | RATHKEALE |  | 52.4127 | -9.1528
249039Z | MV/LV Substation DR***039Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C20 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1364 | -7.8685
070489X | MV/LV Substation MI***489X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 2.24 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | E11 ex CLOONBANNIN | Cloonbannin [T421] | GLENLARA |  | 52.0592 | -9.0547
071160 | MV/LV Substation BE***160 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0.033 | 0.344 | 0 |  | --> | C17 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1449 | -6.0699
165010 | MV/LV Substation TI***010 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C13 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6068 | -8.7338
015003Y | MV/LV Substation WE***003Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E20 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1685 | -6.5408
014512Z | MV/LV Substation HI***512Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.195 | 0.63 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C17 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1349 | -6.7413
059598 | MV/LV Substation C/***598 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 53.9867 | -7.1462
064381Y | MV/LV Substation BO***381Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =107 kVA | --> | 0.19 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =143 kW | --> | C18 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7197 | -6.3823
0074177 | MV/LV Substation TA***4177 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 16.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3208 | -6.6506
0014038 | MV/LV Substation E ***4038 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2526 | -6.1692
019080 | MV/LV Substation BA***080 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.181 | 2.18 |  | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C19 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2725 | -9.7109
093002 | MV/LV Substation FI***002 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.598 | 0 | 0.022 | 0.5 | 0 |  | --> | C20 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3907 | -6.3129
066799X | MV/LV Substation NE***799X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4493 | -6.327
099601X | MV/LV Substation LI***601X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9329 | -7.694
070832X | MV/LV Substation TH***832X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.184 | 0.76 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C11 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0863 | -9.2155
288183X | MV/LV Substation BE***183X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =535 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2764 | -6.2207
035036X | MV/LV Substation CU***036X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 0.49 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.2996 | -8.0825
495802 | MV/LV Substation KE***802 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.974 | -10.0907
081459Z | MV/LV Substation BA***459Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3233 | -6.6101
334013 | MV/LV Substation CA***013 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.19 | 0 | 0.09 | 0.103 | 0 |  | --> | C20 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3771 | -6.0555
093263Z | MV/LV Substation FI***263Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0 | 0.367 | 0 |  | --> | C22 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.391 | -6.3055
069265 | MV/LV Substation SE***265 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.379 | 9.28 |  | --> | 0.598 | 0 | 0.04 | 0.5 | 0 |  | --> | C15 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3345 | -6.2175
184323X | MV/LV Substation CR***323X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1738 | -6.7867
281064Z | MV/LV Substation CL***064Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 4.67 |  | --> | 0.38 | 0 | 0.002 | 0.366 | 0 |  | --> | C18 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8862 | -8.4195
021815 | MV/LV Substation MO***815 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C15 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8998 | -8.5326
160297Y | MV/LV Substation KI***297Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.1295 | -7.0338
089055 | MV/LV Substation SH***055 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.384 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E17 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1143 | -9.1424
151768X | MV/LV Substation SK***768X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex BRUFF | Bruff [T42,T421] | LIMERICK |  | 52.5516 | -8.5592
281377X | MV/LV Substation RA***377X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.8391 | -8.3673
144581 | MV/LV Substation MO***581 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 2.78 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7354 | -7.3899
015085 | MV/LV Substation SA***085 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C14 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2551 | -6.6657
065324Z | MV/LV Substation RO***324Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.565 | -6.2198
0784053 | MV/LV Substation GL***4053 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C12 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9671 | -8.7995
255611 | MV/LV Substation TH***611 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =524 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6363 | -8.4414
1824156 | MV/LV Substation TE***4156 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.8017 | -8.7543
1104099 | MV/LV Substation SU***4099 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.364 | 0.76 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | E11 ex KILGARVAN | Kilgarvan [T421] | KNOCKEARAGH |  | 51.9053 | -9.44
068816X | MV/LV Substation PE***816X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.2 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3435 | -6.2481
130242X | MV/LV Substation TI***242X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.326 | 2.55 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6998 | -7.6157
050071 | MV/LV Substation IO***071 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C16 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4279 | -7.9553
035442 | MV/LV Substation OU***442 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 6.17 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C24 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.4254 | -7.8809
095891X | MV/LV Substation CL***891X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 1.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C25 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.6739 | -9.6516
1604282 | MV/LV Substation BA***4282 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1254 | -7.0964
001219 | MV/LV Substation CA***219 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.233 | 1.23 |  | --> | 0.598 | 0 | 0.057 | 0.5 | 0 |  | --> | C23 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.277 | -6.1038
156606Y | MV/LV Substation MU***606Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3019 | -6.913
081527Z | MV/LV Substation GR***527Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0 | 0.363 | 0 |  | --> | C20 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3406 | -6.4318
281116Y | MV/LV Substation SC***116Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C22 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8868 | -8.5442
006703X | MV/LV Substation ES***703X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.337 | 4.38 |  | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | E11 ex CRANE | Crane [T122] | CRANE |  | 52.5214 | -6.561
150548 | MV/LV Substation KI***548 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.117 | 3.96 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | E18 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7982 | -7.6846
081365Z | MV/LV Substation SA***365Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C15 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3627 | -6.5677
0134011 | MV/LV Substation CA***4011 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 0.12 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0.007 | 0.179 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.997 | -6.9908
034274Y | MV/LV Substation TU***274Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 5.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.5005 | -7.5943
068703X | MV/LV Substation HI***703X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3502 | -6.2379
4054053 | MV/LV Substation CA***4053 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.1298 | -7.1919
058119Y | MV/LV Substation SH***119Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.7949 | -8.293
005002 | MV/LV Substation TA***002 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.03 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | C17 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6664 | -6.3064
066789Z | MV/LV Substation FO***789Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4418 | -6.2578
149296X | MV/LV Substation AR***296X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6921 | -8.012
066423Z | MV/LV Substation MU***423Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5251 | -6.2873
058328 | MV/LV Substation LI***328 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C25 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8615 | -8.1579
036858X | MV/LV Substation CA***858X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =193 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E18 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5771 | -8.1658
067943 | MV/LV Substation GL***943 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.7175 | -8.8124
081068Z | MV/LV Substation AS***068Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =114 kVA | --> | 0.19 | 0 | 0.037 | 0.151 | 0 |  | --> | C20 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3462 | -6.4342
026585 | MV/LV Substation CO***585 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C13 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.6479 | -8.6626
0294296 | MV/LV Substation EL***4296 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =496 kVA | --> | 0.598 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =562 kW | --> | C12 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9138 | -8.2482
120079Y | MV/LV Substation AB***079Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2649 | -6.8479
047946 | MV/LV Substation NC***946 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 54.0568 | -8.2452
034702 | MV/LV Substation CL***702 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 5.88 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3633 | -7.7069
137915 | MV/LV Substation CL***915 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 2 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C12 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.4623 | -9.7237
025093X | MV/LV Substation CO***093X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.014 | 6.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E28 ex MILFORD (MWR) | Milford (mwr) [T422] | CHARLEVILLE |  | 52.4052 | -8.825
069510 | MV/LV Substation BL***510 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.177 | 3 |  | --> | 0.38 | 0 | 0.008 | 0.342 | 0 |  | --> | C34 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3312 | -6.3401
089624 | MV/LV Substation ID***624 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 3.56 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E22 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2848 | -8.9519
365474 | MV/LV Substation OL***474 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0.058 | 0.324 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2711 | -6.345
039981X | MV/LV Substation RE***981X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.18 | 3.45 |  | --> | 0.19 | 0 | 0.011 | 0.179 | 0 |  | --> | C11 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.262 | -9.0738
022652X | MV/LV Substation CA***652X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.491 | 4.55 |  | --> | 0.598 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =535 kW | --> | C21 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1516 | -8.634
0664347 | MV/LV Substation RI***4347 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =573 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4889 | -6.2981
125761 | MV/LV Substation KI***761 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C15 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2721 | -8.3461
068297 | MV/LV Substation TO***297 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 6.65 |  | --> | 0.19 | 0 | 0 | 0.158 | 0 |  | --> | C12 ex EAST WALL ROAD | East Wall Road [T41,T42] | MCDERMOTT |  | 53.3523 | -6.2199
120315Y | MV/LV Substation JO***315Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 3.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4069 | -6.8435
009588X | MV/LV Substation PA***588X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.262 | -7.0216
365038 | MV/LV Substation WH***038 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2796 | -6.3747
042893X | MV/LV Substation OL***893X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =490 kVA | --> | 0.598 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =567 kW | --> | E16 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8477 | -9.2835
031972X | MV/LV Substation CU***972X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9669 | -7.7156
011067 | MV/LV Substation LO***067 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.139 | 5.05 |  | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C13 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6635 | -7.2442
248133X | MV/LV Substation MU***133X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.436 | -6.6172
251056 | MV/LV Substation PA***056 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =381 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C18 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.3018 | -8.9939
065927 | MV/LV Substation GR***927 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6093 | -6.2225
037509 | MV/LV Substation WE***509 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0.048 | 0 | 0 | Constrained, otherwise capacity available =333 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8302 | -8.9766
125044Y | MV/LV Substation MC***044Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2636 | -8.2809
052638Y | MV/LV Substation SO***638Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C17 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.611 | -7.0723
0504326 | MV/LV Substation ES***4326 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4294 | -7.9021
066201 | MV/LV Substation BU***201 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.031 | 0.344 | 0 |  | --> | C13 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3931 | -6.1209
1164281 | MV/LV Substation WP***4281 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.32 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8091 | -9.5454
120224Y | MV/LV Substation JO***224Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 3.5 |  | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.412 | -6.8356
066731Z | MV/LV Substation TO***731Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C18 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.442 | -6.1569
127347 | MV/LV Substation BA***347 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C18 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6809 | -7.8284
238685X | MV/LV Substation GR***685X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6262 | -9.2237
007147 | MV/LV Substation CL***147 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 16.12 |  | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3384 | -6.5654
068370 | MV/LV Substation RE***370 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =303 kVA | --> | 0.598 | 0 | 0.028 | 0.5 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.333 | -6.2889
281746Z | MV/LV Substation SU***746Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8851 | -8.6078
099197 | MV/LV Substation LE***197 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9306 | -7.7005
281384Z | MV/LV Substation RE***384Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.49 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8679 | -8.4793
017158Y | MV/LV Substation IN***158Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 1.58 |  | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C17 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.5675 | -9.2759
014430X | MV/LV Substation AV***430X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 0.63 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C17 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1259 | -6.7523
433230X | MV/LV Substation BD***230X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =602 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C15 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8961 | -8.5677
029540 | MV/LV Substation KI***540 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8539 | -8.0305
1544084 | MV/LV Substation GA***4084 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3974 | -6.3645
021057 | MV/LV Substation ST***057 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =298 kVA | --> | 0.598 | 0 | 0.019 | 0.5 | 0 |  | --> | C11 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.905 | -8.478
066621Z | MV/LV Substation RN***621Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =604 kVA | --> | 0.598 | 0 | 0.04 | 0.5 | 0 |  | --> | C20 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4444 | -6.2196
025115Y | MV/LV Substation NU***115Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C11 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4061 | -8.5699
281014 | MV/LV Substation SA***014 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C20 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.88 | -8.4842
433203X | MV/LV Substation BE***203X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9027 | -8.5899
046073X | MV/LV Substation TH***073X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.183 | 5.48 |  | --> | 0.19 | 0 | 0.005 | 0.184 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3091 | -8.554
063542X | MV/LV Substation PO***542X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8185 | -6.4692
111027Z | MV/LV Substation BI***027Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.368 | 3.64 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C18 ex CASTLETOWNBERE | Castletownbere [T42] | BALLYLICKY |  | 51.6478 | -9.9061
281319 | MV/LV Substation RO***319 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.01 | 0.084 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8916 | -8.551
127102 | MV/LV Substation AR***102 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5656 | -7.926
1544314 | MV/LV Substation FC***4314 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C12 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3843 | -6.3964
059002X | MV/LV Substation KI***002X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.066 | 0.07 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1022 | -7.4544
062612Y | MV/LV Substation GR***612Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.424 | 5.69 |  | --> | 0.598 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =546 kW | --> | C11 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.996 | -6.3952
099526X | MV/LV Substation LK***526X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =522 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C18 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9488 | -7.7305
067090Z | MV/LV Substation CO***090Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 13.8 |  | --> | 0.38 | 0 | 0.036 | 0.338 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.595 | -8.4695
066085Y | MV/LV Substation AR***085Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =299 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4651 | -6.2392
281022Y | MV/LV Substation DY***022Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.043 | 7.88 |  | --> | 0.19 | 0 | 0.012 | 0.158 | 0 |  | --> | C19 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8976 | -8.484
2884174 | MV/LV Substation TU***4174 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2446 | -6.1547
060355 | MV/LV Substation CL***355 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1754 | -7.2124
0584022 | MV/LV Substation CL***4022 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9274 | -8.183
024654X | MV/LV Substation CH***654X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.116 | 2.14 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2165 | -8.5875
154178Z | MV/LV Substation WE***178Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.39 | -6.3894
281132 | MV/LV Substation BE***132 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.88 |  | --> | 0.95 | 0 | 0.025 | 0.5 | 0 |  | --> | C23 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8979 | -8.4681
165788 | MV/LV Substation CL***788 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C14 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6072 | -8.9029
067151Z | MV/LV Substation SI***151Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =468 kVA | --> | 0.598 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =559 kW | --> | C16 ex CORBALLY | Corbally [T41,T42] | ARDNACRUSHA |  | 52.6674 | -8.6199
154247Z | MV/LV Substation MT***247Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =142 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3874 | -6.419
093547Z | MV/LV Substation LA***547Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =479 kVA | --> | 0.598 | 0 | 0.033 | 0.5 | 0 |  | --> | C19 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.3929 | -6.1702
281100X | MV/LV Substation MC***100X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 5.49 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8671 | -8.4781
082939X | MV/LV Substation DE***939X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6565 | -6.5825
068437X | MV/LV Substation CL***437X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C11 ex CLONTARF | Clontarf [T42] | FINGLAS |  | 53.3728 | -6.2146
012528Y | MV/LV Substation CA***528Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.361 | 1.99 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C14 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8384 | -6.9283
032839 | MV/LV Substation CR***839 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | E11 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.23 | -6.975
029728Y | MV/LV Substation PI***728Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex CARRIGTWOHILL |  |  |  | 51.9082 | -8.2804
015348 | MV/LV Substation KI***348 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.221 | -6.6301
125024 | MV/LV Substation KI***024 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C11 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.27 | -8.2757
053557Y | MV/LV Substation PU***557Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.037 | 3.28 |  | --> | 0.095 | 0 | 0.004 | 0.083 | 0 |  | --> | C23 ex SRAH | Srah [T43] | THORNSBERRY |  | 53.2838 | -7.4841
052066Z | MV/LV Substation NC***066Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5141 | -7.3553
0134061 | MV/LV Substation FO***4061 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E62 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0518 | -6.8902
084299X | MV/LV Substation BA***299X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C18 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.2351 | -8.8239
002125 | MV/LV Substation OL***125 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.242 | 4.51 |  | --> | 0.38 | 0 | 0.056 | 0.316 | 0 |  | --> | C16 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1904 | -6.1188
281764X | MV/LV Substation PA***764X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =284 kVA | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C14 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8715 | -8.4939
0684394 | MV/LV Substation MA***4394 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =794 kVA | --> | 0.95 | 0 | 0.003 | 0.5 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3362 | -6.2851
161150 | MV/LV Substation AR***150 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C13 ex SPIDDAL |  |  |  | 53.2484 | -9.2826
069114 | MV/LV Substation MO***114 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.235 | 4.47 |  | --> | 0.38 | 0 | 0.038 | 0.329 | 0 |  | --> | C14 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3068 | -6.3233
066593Z | MV/LV Substation HO***593Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =188 kVA | --> | 0.19 | 0 | 0.005 | 0.185 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4445 | -6.2062
007949Y | MV/LV Substation PA***949Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.143 | 0.14 | Constrained, otherwise capacity available =369 kVA | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C16 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3495 | -6.4929
108248X | MV/LV Substation WA***248X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5094 | -8.2413
119502 | MV/LV Substation SC***502 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 4.16 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | C20 ex NEWMARKET (SR) | Newmarket (sr) [T41,T42] | GLENLARA |  | 52.2197 | -8.9972
0664083 | MV/LV Substation CA***4083 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =336 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C14 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4292 | -6.2363
003563 | MV/LV Substation KE***563 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KILMARTIN | Kilmartin [T41] | ARKLOW |  | 53.0582 | -6.1366
011154Z | MV/LV Substation KI***154Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C16 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.655 | -7.2486
355013 | MV/LV Substation TO***013 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.06 | 0.06 | Constrained, otherwise capacity available =471 kVA | --> | 0.598 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =550 kW | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0537 | -8.7382
031095Y | MV/LV Substation WE***095Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C19 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0888 | -7.6227
1424350 | MV/LV Substation UI***4350 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex ATHENRY |  |  |  | 53.2921 | -8.7475
009962 | MV/LV Substation BU***962 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 13.6 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2406 | -7.1752
0414166 | MV/LV Substation HI***4166 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | E12 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7225 | -8.9928
0954235 | MV/LV Substation DO***4235 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C20 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.7353 | -9.4983
036736 | MV/LV Substation CO***736 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4776 | -8.1372
002972 | MV/LV Substation GI***972 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 2.36 |  | --> | 0.38 | 0 | 0.016 | 0.357 | 0 |  | --> | C19 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1918 | -6.1132
007076 | MV/LV Substation BA***076 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =324 kW | --> | C19 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3304 | -6.4518
0584350 | MV/LV Substation BA***4350 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.8075 | -8.0924
069674 | MV/LV Substation PR***674 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0.043 | 0.324 | 0 |  | --> | C12 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2752 | -6.2992
039063 | MV/LV Substation RA***063 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.154 | 11.03 |  | --> | 0.38 | 0 | 0.032 | 0.321 | 0 |  | --> | C14 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2738 | -9.0754
117324Y | MV/LV Substation CO***324Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.315 | 0.32 | Constrained, otherwise capacity available =578 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C18 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0864 | -8.5192
281439Y | MV/LV Substation BA***439Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =19 kVA | --> | 0.048 | 0 | 0.03 | 0.021 | 0 |  | --> | C11 ex BALLINCOLLIG | Ballincollig [T41,T42] | KILBARRY |  | 51.8365 | -8.5385
180946X | MV/LV Substation LL***946X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.171 | 3.27 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.739 | -6.9023
156676 | MV/LV Substation AN***676 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 2.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3079 | -6.8627
150083X | MV/LV Substation MA***083X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.96 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E18 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7588 | -7.7238
0214407 | MV/LV Substation AN***4407 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9018 | -8.3288
031021 | MV/LV Substation WH***021 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.11 | -7.5969
019414 | MV/LV Substation CL***414 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.345 | 2.18 |  | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | C16 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2818 | -9.7286
052710X | MV/LV Substation BA***710X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5183 | -7.3242
064123 | MV/LV Substation LE***123 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =319 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C18 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7109 | -6.3435
056277Y | MV/LV Substation MA***277Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.316 | 0.89 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C17 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0919 | -7.9031
071035 | MV/LV Substation TR***035 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =111 kVA | --> | 0.38 | 0 | 0.072 | 0.285 | 0 |  | --> | C17 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1492 | -6.0657
007532X | MV/LV Substation BA***532X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 1.4 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2432 | -6.49
0204090 | MV/LV Substation FO***4090 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C18 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.071 | -9.5879
2484127 | MV/LV Substation PR***4127 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 0.33 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E33 ex TRIM | Trim [T421] | NAVAN |  | 53.4823 | -6.7403
004316Y | MV/LV Substation MA***316Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 0.45 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8806 | -6.3323
204207 | MV/LV Substation PU***207 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2176 | -7.4065
001049X | MV/LV Substation CO***049X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.345 | 4.01 |  | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2758 | -6.0951
012524 | MV/LV Substation BE***524 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.817 | -6.877
035444X | MV/LV Substation OR***444X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.197 | 0.49 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3409 | -7.8105
005233X | MV/LV Substation BA***233X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6326 | -6.2575
004046 | MV/LV Substation QU***046 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =220 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C25 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.796 | -6.1611
266173X | MV/LV Substation GL***173X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2621 | -7.3155
061071 | MV/LV Substation MA***071 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.116 | 2.04 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C14 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1271 | -6.9028
156888X | MV/LV Substation T/***888X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 2.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.2393 | -7.0239
058472X | MV/LV Substation BA***472X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 0.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C15 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.9452 | -8.0477
136759Y | MV/LV Substation GL***759Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6518 | -8.3953
281989Y | MV/LV Substation CU***989Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 5.49 |  | --> | 0.38 | 0 | 0.024 | 0.348 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8666 | -8.4713
068572X | MV/LV Substation DI***572X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.86 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.365 | -6.2476
082210Z | MV/LV Substation TA***210Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6038 | -6.6225
1384118 | MV/LV Substation CO***4118 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.52 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex SHERCOCK | Shercock [T41,T42] | MEATH HILL |  | 54.0236 | -6.9279
081130Z | MV/LV Substation CA***130Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C18 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3743 | -6.3636
068729 | MV/LV Substation SA***729 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.598 | 0 | 0.028 | 0.5 | 0 |  | --> | C16 ex DRUMCONDRA | Drumcondra [T41,T42] | MCDERMOTT |  | 53.3638 | -6.2619
060053Y | MV/LV Substation CO***053Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 2.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E14 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0196 | -7.0543
028993X | MV/LV Substation JO***993X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.475 | 6.78 |  | --> | 0.598 | 0 | 0.03 | 0.5 | 0 |  | --> | C39 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9049 | -8.3524
013055 | MV/LV Substation GR***055 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9942 | -6.9872
054434X | MV/LV Substation UP***434X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 53.0194 | -7.4563
022343 | MV/LV Substation DR***343 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =55 kVA | --> | 0.095 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =66 kW | --> | C15 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1031 | -8.6889
265841 | MV/LV Substation PU***841 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.56 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0048 | -7.5187
036032Y | MV/LV Substation RO***032Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4804 | -8.1512
154431Z | MV/LV Substation AR***431Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0 | 0.185 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4034 | -6.4099
233076X | MV/LV Substation GO***076X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C21 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.1899 | -9.4215
139714Y | MV/LV Substation DR***714Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C17 ex VIRGINIA | Virginia [T41,T42] | MEATH HILL |  | 53.8378 | -7.078
082753Y | MV/LV Substation KE***753Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6257 | -6.5279
050834Y | MV/LV Substation CO***834Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C23 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4474 | -7.9334
050991Y | MV/LV Substation AT***991Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =993 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =949 kW | --> | C17 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4237 | -7.9358
180857X | MV/LV Substation KE***857X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.448 | 3.27 |  | --> | 0.598 | 0 | 0.049 | 0 | 0 | Constrained, otherwise capacity available =537 kW | --> | C12 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7388 | -6.8988
251033 | MV/LV Substation TW***033 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex PARKMORE | Parkmore [T41,T42] | GALWAY 110KV |  | 53.3051 | -9.0021
156214 | MV/LV Substation CL***214 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =9 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2071 | -6.8432
0394188 | MV/LV Substation GL***4188 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 11.03 |  | --> | 0.38 | 0 | 0.006 | 0.359 | 0 |  | --> | C18 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2662 | -9.1189
021467Z | MV/LV Substation BO***467Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.922 | -8.4839
015442X | MV/LV Substation BL***442X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | E20 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1706 | -6.5335
069577 | MV/LV Substation MA***577 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.072 | 9.99 |  | --> | 0.38 | 0 | 0.019 | 0.319 | 0 |  | --> | C12 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3266 | -6.2801
050488Y | MV/LV Substation MO***488Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C21 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4214 | -7.9904
161077Y | MV/LV Substation MO***077Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 6.53 |  | --> | 0.048 | 0 | 0.03 | 0.023 | 0 |  | --> | C16 ex OUGHTERARD | Oughterard [T41,T42] | SCREEB |  | 53.3599 | -9.1749
031742X | MV/LV Substation CO***742X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =482 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C12 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0897 | -7.618
054469Y | MV/LV Substation DE***469Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C12 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 53.0077 | -7.4403
1104033 | MV/LV Substation GO***4033 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 0.76 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex KILGARVAN | Kilgarvan [T421] | KNOCKEARAGH |  | 51.9037 | -9.4535
365610 | MV/LV Substation RE***610 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =248 kVA | --> | 0.38 | 0 | 0.025 | 0.34 | 0 |  | --> | C19 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2988 | -6.3638
1184097 | MV/LV Substation ST***4097 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E11 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.471 | -8.2723
0644302 | MV/LV Substation ST***4302 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7109 | -6.5378
058151 | MV/LV Substation PU***151 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C26 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9302 | -8.2392
075548Y | MV/LV Substation CL***548Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E22 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6966 | -6.6451
068185X | MV/LV Substation WE***185X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C44 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3445 | -6.2691
012152 | MV/LV Substation CL***152 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =300 kVA | --> | 0.38 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =341 kW | --> | C19 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8346 | -6.9181
120006 | MV/LV Substation CH***006 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =154 kW | --> | E18 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3419 | -7.0524
154633 | MV/LV Substation GL***633 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0.053 | 0.316 | 0 |  | --> | C11 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4002 | -6.4164
0324209 | MV/LV Substation ST***4209 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =549 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C23 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1705 | -7.145
066106Z | MV/LV Substation WO***106Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =153 kW | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5078 | -6.4719
051445X | MV/LV Substation KI***445X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 2.22 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3468 | -7.6134
065094 | MV/LV Substation SE***094 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0.076 | 0 | 0 | Constrained, otherwise capacity available =305 kW | --> | C16 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.578 | -6.1203
034077 | MV/LV Substation TU***077 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 5.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.4542 | -7.6504
047931 | MV/LV Substation TA***931 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9091 | -8.3009
052392Y | MV/LV Substation LO***392Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C18 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.681 | -7.163
004511X | MV/LV Substation AR***511X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 18.08 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C18 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8596 | -6.0748
0814094 | MV/LV Substation HA***4094 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =594 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3303 | -6.3888
047204 | MV/LV Substation HO***204 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.04 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9968 | -8.2735
154681 | MV/LV Substation CA***681 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =137 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.385 | -6.4134
011036 | MV/LV Substation GO***036 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.359 | 5.05 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C11 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.656 | -7.2427
068536X | MV/LV Substation CA***536X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 11.14 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3768 | -6.3159
154362 | MV/LV Substation LO***362 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =144 kW | --> | C18 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.387 | -6.4079
081021X | MV/LV Substation AL***021X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C17 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.334 | -6.3447
1674173 | MV/LV Substation BL***4173 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =580 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9367 | -8.5471
035004 | MV/LV Substation CA***004 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.236 | 6.17 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3759 | -7.9224
009154Y | MV/LV Substation IE***154Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2463 | -7.1576
238014 | MV/LV Substation ID***014 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E12 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6158 | -9.2184
0154364 | MV/LV Substation BL***4364 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1724 | -6.5282
069421 | MV/LV Substation PA***421 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.178 | 0.91 |  | --> | 0.38 | 0 | 0.053 | 0.309 | 0 |  | --> | C22 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3009 | -6.3189
0014224 | MV/LV Substation AR***4224 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2569 | -6.1476
007212Z | MV/LV Substation PI***212Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C14 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3361 | -6.4582
039200 | MV/LV Substation CO***200 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C31 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2804 | -9.0724
1654120 | MV/LV Substation CO***4120 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C11 ex TIMOLEAGUE | Timoleague [T41] | BANDON |  | 51.6321 | -8.7266
015745X | MV/LV Substation LI***745X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =340 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1278 | -6.6147
012891X | MV/LV Substation KI***891X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 2.83 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.708 | -6.9821
0934031 | MV/LV Substation HE***4031 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =461 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4038 | -6.2353
144032Y | MV/LV Substation MU***032Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C11 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.7618 | -7.2002
022893X | MV/LV Substation WE***893X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C21 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1376 | -8.6504
0524746 | MV/LV Substation SS***4746 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 10.9 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5448 | -7.3482
120497Y | MV/LV Substation TO***497Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3582 | -7.2171
014848Z | MV/LV Substation DU***848Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C20 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1698 | -6.9087
0074523 | MV/LV Substation BA***4523 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2004 | -6.3749
160011 | MV/LV Substation RA***011 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =108 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C15 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1551 | -7.183
018114Z | MV/LV Substation TI***114Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.75 |  | --> | 0.048 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5708 | -9.3713
021461Z | MV/LV Substation KE***461Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0 | 0.04 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.939 | -8.4278
039188X | MV/LV Substation FU***188X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C13 ex SPIDDAL |  |  |  | 53.2508 | -9.225
144731X | MV/LV Substation GO***731X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C15 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.8258 | -7.1364
176157Y | MV/LV Substation HO***157Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.194 | 18.78 |  | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | E11 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | HARTNETTS CROSS |  | 51.9061 | -8.968
165874 | MV/LV Substation MT***874 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6295 | -8.8763
1514240 | MV/LV Substation RA***4240 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E09 ex BRUFF |  |  |  | 52.5365 | -8.5207
036123Y | MV/LV Substation RO***123Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | E16 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4786 | -8.1501
252026 | MV/LV Substation CL***026 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 1.32 |  | --> | 0.38 | 0 | 0.008 | 0.364 | 0 |  | --> | C29 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4874 | -9.9842
005828X | MV/LV Substation CA***828X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7111 | -6.5101
067233 | MV/LV Substation AN***233 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C11 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.654 | -8.6576
288119X | MV/LV Substation TI***119X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2679 | -6.2454
063416X | MV/LV Substation AR***416X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C15 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.8765 | -6.5685
1274422 | MV/LV Substation DU***4422 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C17 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6783 | -7.8117
026579X | MV/LV Substation FA***579X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 8.66 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C17 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7705 | -8.6551
138129X | MV/LV Substation WH***129X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.098 | 1.52 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C18 ex SHERCOCK | Shercock [T41,T42] | MEATH HILL |  | 54.0129 | -6.8873
288802 | MV/LV Substation QU***802 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.03 | 0.04 |  | --> | 0.031 | 0 | 0 | 0.031 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2219 | -6.1425
001210X | MV/LV Substation PO***210X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C12 ex POTTERY ROAD |  |  |  | 53.2734 | -6.1517
1084101 | MV/LV Substation RO***4101 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5619 | -8.206
238509 | MV/LV Substation HO***509 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.661 | -9.1176
165031 | MV/LV Substation CO***031 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =317 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C15 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6186 | -8.8947
214534 | MV/LV Substation CL***534 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C14 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.799 | -8.9746
281436X | MV/LV Substation PO***436X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C24 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8226 | -8.4713
017127 | MV/LV Substation HA***127 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5267 | -8.9371
064634 | MV/LV Substation GO***634 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =52 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E15 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6366 | -6.2171
038014 | MV/LV Substation GE***014 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =159 kW | --> | C16 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0632 | -8.8157
038023 | MV/LV Substation GO***023 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E15 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0731 | -8.8165
1564433 | MV/LV Substation AL***4433 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2455 | -6.9686
046071 | MV/LV Substation ME***071 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.212 | 5.78 |  | --> | 0.38 | 0 | 0.038 | 0.325 | 0 |  | --> | C13 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2684 | -8.489
153667 | MV/LV Substation ST***667 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =142 kVA | --> | 0.19 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =159 kW | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.705 | -8.5062
503550 | MV/LV Substation WO***550 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.252 | 1.69 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C16 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 54.9967 | -7.5059
132243 | MV/LV Substation DO***243 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | E30 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2267 | -8.7308
011123 | MV/LV Substation OR***123 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =475 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | C14 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6488 | -7.2518
005081Y | MV/LV Substation GL***081Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 17.8 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6345 | -6.234
068509X | MV/LV Substation CA***509X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3451 | -6.2408
015547Z | MV/LV Substation WO***547Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1779 | -6.5302
012165 | MV/LV Substation TU***165 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =117 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C23 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8322 | -6.9111
0074429 | MV/LV Substation RO***4429 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 16.12 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3019 | -6.7424
0814161 | MV/LV Substation ST***4161 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0.095 | 0.291 | 0 |  | --> | E20 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3421 | -6.4657
248987 | MV/LV Substation PA***987 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3342 | -6.6925
001035 | MV/LV Substation SH***035 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =242 kVA | --> | 0.38 | 0 | 0.046 | 0.324 | 0 |  | --> | C11 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2429 | -6.1223
074334X | MV/LV Substation CA***334X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9413 | -8.1033
162348 | MV/LV Substation TR***348 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 0.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8036 | -7.5411
006581Y | MV/LV Substation BA***581Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.12 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C17 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5026 | -6.568
050072 | MV/LV Substation RE***072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 7.61 |  | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =344 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.424 | -7.9163
365295X | MV/LV Substation SY***295X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C17 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.3043 | -6.3661
109535 | MV/LV Substation SK***535 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.381 | 0.38 | Constrained, otherwise capacity available =862 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7098 | -8.8791
041350 | MV/LV Substation DR***350 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E17 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7249 | -8.9631
1424068 | MV/LV Substation ME***4068 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.4203 | -8.5514
066455X | MV/LV Substation RA***455X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E18 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5048 | -6.4545
013939Y | MV/LV Substation KC***939Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0994 | -7.0103
0144043 | MV/LV Substation OL***4043 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1685 | -6.9486
071211 | MV/LV Substation KI***211 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.116 | 5.58 |  | --> | 0.19 | 0 | 0.009 | 0.172 | 0 |  | --> | C14 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1079 | -6.0664
074418 | MV/LV Substation WO***418 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9425 | -8.1131
237082X | MV/LV Substation DR***082X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.9007 | -6.4224
196221X | MV/LV Substation OA***221X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =576 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =591 kW | --> | C15 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5655 | -6.7932
066820Z | MV/LV Substation AI***820Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =578 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4481 | -6.2211
054122 | MV/LV Substation EL***122 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =16 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0451 | -7.314
039097X | MV/LV Substation BA***097X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0.029 | 0.5 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2511 | -9.1532
001283 | MV/LV Substation SP***283 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.212 | 1.16 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2762 | -6.1574
0374204 | MV/LV Substation CR***4204 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 13.05 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C21 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.9365 | -8.8971
368447X | MV/LV Substation CN***447X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.6847 | -8.7476
281043 | MV/LV Substation GE***043 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C20 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8784 | -8.4873
0014076 | MV/LV Substation HA***4076 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.075 | 0.319 | 0 |  | --> | C19 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3055 | -6.2437
006099 | MV/LV Substation GI***099 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.33 | 1.29 |  | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C24 ex MONFIN | Monfin [T41,T42] | WEXFORD |  | 52.4961 | -6.5523
039538X | MV/LV Substation FL***538X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =608 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2895 | -9.0204
281833Z | MV/LV Substation CA***833Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =297 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | C22 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8018 | -8.4026
149307X | MV/LV Substation BI***307X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6766 | -8.0421
068660X | MV/LV Substation BR***660X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.86 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3645 | -6.2456
093549Z | MV/LV Substation EA***549Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.598 | 0 | 0.1 | 0.487 | 0 |  | --> | C25 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4183 | -6.3138
062712Y | MV/LV Substation FR***712Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.33 |  | --> | 0.95 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =941 kW | --> | C21 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.004 | -6.4012
074324X | MV/LV Substation CE***324X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =590 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =593 kW | --> | C13 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9448 | -8.0927
1224131 | MV/LV Substation RO***4131 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 4.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8461 | -6.7195
0344207 | MV/LV Substation CN***4207 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.417 | 0.57 |  | --> | 0.598 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =547 kW | --> | C16 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3537 | -7.7224
366077 | MV/LV Substation VO***077 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 0.45 |  | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1256 | -9.672
1624074 | MV/LV Substation DR***4074 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.8695 | -7.7487
033943X | MV/LV Substation CO***943X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | C12 ex PORTLAW | Portlaw [T41,T42] | BUTLERSTOWN |  | 52.2826 | -7.3114
082083Z | MV/LV Substation SK***083Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5827 | -6.5604
136888Y | MV/LV Substation CE***888Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =378 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =563 kW | --> | C12 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6315 | -8.1805
009814Y | MV/LV Substation SW***814Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C12 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2438 | -7.1225
117209Y | MV/LV Substation CL***209Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.0786 | -8.3816
064207 | MV/LV Substation GE***207 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =155 kW | --> | C11 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7203 | -6.3593
130993 | MV/LV Substation BR***993 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.156 | 2.55 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.7016 | -7.611
047834 | MV/LV Substation TA***834 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.196 | 1.04 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9959 | -8.2796
495416X | MV/LV Substation BU***416X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9703 | -9.986
065329Z | MV/LV Substation GE***329Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =913 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =938 kW | --> | C16 ex BALBRIGGAN | Balbriggan [T42] | GLASMORE |  | 53.6107 | -6.1824
281382Z | MV/LV Substation RE***382Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.49 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8685 | -8.4801
184273X | MV/LV Substation LI***273X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 3.38 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C21 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1377 | -6.7761
011346X | MV/LV Substation NA***346X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.8 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6433 | -7.21
590104 | MV/LV Substation LI***104 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5406 | -9.2679
0894243 | MV/LV Substation RA***4243 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.56 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E20 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2164 | -9.0805
064112 | MV/LV Substation HI***112 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C16 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7138 | -6.3701
012457X | MV/LV Substation CL***457X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.99 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C19 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8081 | -6.9687
288909 | MV/LV Substation NE***909 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.02 | 0.031 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2646 | -6.3056
365875 | MV/LV Substation TY***875 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0.005 | 0.173 | 0 |  | --> | C20 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2975 | -6.3474
0424175 | MV/LV Substation CO***4175 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =602 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =591 kW | --> | C19 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8404 | -9.3183
014084Z | MV/LV Substation BA***084Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =154 kW | --> | C11 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1672 | -6.8152
042068 | MV/LV Substation CA***068 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.51 |  | --> | 0.598 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | C19 ex TURLOUGH ROAD | Turlough Road [T43] | CASTLEBAR |  | 53.8615 | -9.2956
082198Y | MV/LV Substation DU***198Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7147 | -6.6557
154057Z | MV/LV Substation KI***057Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C13 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3789 | -6.3922
012915X | MV/LV Substation ES***915X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =328 kVA | --> | 0.38 | 0 | 0.047 | 0 | 0 | Constrained, otherwise capacity available =335 kW | --> | C19 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8392 | -6.92
062022Z | MV/LV Substation FI***022Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 3.12 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C18 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9875 | -6.3796
075280 | MV/LV Substation CL***280 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 17.8 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.555 | -6.2569
067489X | MV/LV Substation MA***489X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =421 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =561 kW | --> | E21 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.7419 | -8.7716
099392X | MV/LV Substation CH***392X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 5.45 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9612 | -7.7579
0524803 | MV/LV Substation PE***4803 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C23 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.526 | -7.3063
0024008 | MV/LV Substation SU***4008 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.388 | 2.36 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C19 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1937 | -6.1107
233116 | MV/LV Substation ST***116 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =157 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C23 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2349 | -9.4623
064904X | MV/LV Substation MA***904X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =278 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.709 | -6.3767
248359X | MV/LV Substation CA***359X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.4251 | -6.6611
365975X | MV/LV Substation MA***975X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2707 | -6.3689
067861Y | MV/LV Substation GR***861Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.8 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6597 | -8.5753
355003X | MV/LV Substation AL***003X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.06 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex TUBBERCURRY | Tubbercurry [T41,T42] | TONROE |  | 54.0449 | -8.7603
026938Y | MV/LV Substation CU***938Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.8039 | -8.6299
017009 | MV/LV Substation CH***009 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.095 | 1.98 |  | --> | 0.19 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =156 kW | --> | E18 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5207 | -8.9431
054496Y | MV/LV Substation MO***496Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 52.9945 | -7.2143
093164 | MV/LV Substation GL***164 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.254 | 5.82 |  | --> | 0.38 | 0 | 0.018 | 0.346 | 0 |  | --> | C19 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.3899 | -6.1897
041909X | MV/LV Substation AL***909X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =21 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.6687 | -8.9528
014822 | MV/LV Substation LO***822 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C11 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1654 | -6.9321
109280 | MV/LV Substation GL***280 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | E17 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7613 | -8.8864
156034 | MV/LV Substation KI***034 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =344 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2419 | -6.9696
062073Y | MV/LV Substation SU***073Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.69 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C23 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0081 | -6.4049
150575 | MV/LV Substation RE***575 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8576 | -8.1223
0664103 | MV/LV Substation AR***4103 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0.105 | 0 | 0 | Constrained, otherwise capacity available =297 kW | --> | E21 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5099 | -6.3865
281212Z | MV/LV Substation MO***212Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.264 | 5.49 |  | --> | 0.38 | 0 | 0 | 0.361 | 0 |  | --> | C23 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8511 | -8.4805
008600Z | MV/LV Substation RA***600Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.1865 | -6.8624
0494336 | MV/LV Substation FI***4336 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.7475 | -7.903
099076 | MV/LV Substation CO***076 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.23 | 5.45 |  | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9572 | -7.7532
0334104 | MV/LV Substation CU***4104 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | C11 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3177 | -7.3632
082521Y | MV/LV Substation BU***521Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.612 | -6.5056
0644171 | MV/LV Substation AN***4171 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =486 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6961 | -6.2488
042107 | MV/LV Substation CO***107 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.251 | 1.51 |  | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C19 ex TURLOUGH ROAD | Turlough Road [T43] | CASTLEBAR |  | 53.8534 | -9.2996
0434013 | MV/LV Substation MU***4013 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.8925 | -9.1242
035234X | MV/LV Substation NE***234X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 0.49 |  | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =33 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.2733 | -7.8123
029953X | MV/LV Substation WA***953X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C19 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9287 | -8.1953
252279 | MV/LV Substation MA***279 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.389 | 2.76 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C13 ex RECESS | Recess [T41] | SCREEB |  | 53.4667 | -9.7241
365174 | MV/LV Substation CU***174 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2748 | -6.3761
0934314 | MV/LV Substation TB***4314 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C13 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3821 | -6.291
214863 | MV/LV Substation HI***863 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7424 | -9.1722
053721Y | MV/LV Substation CI***721Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.39 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =593 kW | --> | C11 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2688 | -7.4994
196258 | MV/LV Substation RA***258 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.34 |  | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5637 | -6.9556
062214X | MV/LV Substation RO***214X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 4.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E16 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0086 | -6.2931
064574Y | MV/LV Substation SL***574Y |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =180 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7033 | -6.5398
069813 | MV/LV Substation CO***813 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.47 |  | --> | 0.95 | 0 | 0.013 | 0.5 | 0 |  | --> | C11 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.3051 | -6.3028
089623 | MV/LV Substation EA***623 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.153 | 3.56 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E22 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2854 | -8.9555
0684330 | MV/LV Substation TH***4330 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =620 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GLASNEVIN | Glasnevin [T41] | FINGLAS |  | 53.3678 | -6.2701
0424182 | MV/LV Substation GO***4182 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8396 | -9.2673
055867 | MV/LV Substation PA***867 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9479 | -7.8021
038619X | MV/LV Substation GO***619X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0474 | -8.8377
108003 | MV/LV Substation DO***003 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.57 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =947 kW | --> | C16 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.497 | -8.2017
082687 | MV/LV Substation BA***687 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5998 | -6.6868
0814315 | MV/LV Substation TH***4315 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =846 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3379 | -6.4707
005600X | MV/LV Substation RA***600X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 3.03 |  | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C18 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6696 | -6.2946
031028 | MV/LV Substation CO***028 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =334 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0909 | -7.6354
037631 | MV/LV Substation KI***631 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 13.05 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C19 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8626 | -8.9203
0214276 | MV/LV Substation CL***4276 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E21 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.9284 | -8.6135
056279Y | MV/LV Substation FA***279Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.171 | 0.89 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E20 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0834 | -7.9278
0074071 | MV/LV Substation BU***4071 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2664 | -6.3927
075161 | MV/LV Substation BA***161 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 1.13 |  | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6184 | -6.6653
0034277 | MV/LV Substation TA***4277 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C23 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9234 | -6.1168
1584069 | MV/LV Substation AB***4069 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C21 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9319 | -9.3447
065343Z | MV/LV Substation CH***343Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =300 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C16 ex BALBRIGGAN | Balbriggan [T42] | GLASMORE |  | 53.6105 | -6.1856
0814322 | MV/LV Substation AD***4322 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0 | 0.365 | 0 |  | --> | E17 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3408 | -6.4749
324879 | MV/LV Substation AT***879 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C20 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.5688 | -8.261
0294268 | MV/LV Substation AV***4268 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C19 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9329 | -8.1854
062851X | MV/LV Substation MA***851X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 0.72 |  | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C11 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0021 | -6.3708
0194103 | MV/LV Substation CR***4103 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2681 | -9.6947
082795X | MV/LV Substation FE***795X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.27 | 2.01 |  | --> | 0.38 | 0 | 0.057 | 0 | 0 | Constrained, otherwise capacity available =320 kW | --> | C17 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6636 | -6.6875
156219Y | MV/LV Substation CA***219Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2081 | -6.8432
149406 | MV/LV Substation LA***406 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =108 kVA | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6182 | -8.0875
345553 | MV/LV Substation FR***553 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.598 | 0 | 0.163 | 0.346 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3068 | -8.1752
055053Y | MV/LV Substation RO***053Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C14 ex ROSCREA |  |  |  | 52.9502 | -7.7951
0844072 | MV/LV Substation KI***4072 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C14 ex KILCOLGAN |  |  |  | 53.2116 | -8.8701
0684221 | MV/LV Substation DO***4221 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3331 | -6.2929
074905 | MV/LV Substation LO***905 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.049 | -7.8512
377436X | MV/LV Substation EM***436X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =106 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0554 | -9.9422
071929 | MV/LV Substation ED***929 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =337 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1228 | -6.0777
161810 | MV/LV Substation AR***810 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C13 ex SPIDDAL |  |  |  | 53.2485 | -9.2834
050191X | MV/LV Substation B ***191X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.61 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.3169 | -7.9699
1204385 | MV/LV Substation SO***4385 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C14 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.3498 | -6.8699
1544200 | MV/LV Substation LA***4200 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =789 kVA | --> | 0.95 | 0 | 0.042 | 0 | 0 | Constrained, otherwise capacity available =890 kW | --> | C11 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4139 | -6.3656
063126X | MV/LV Substation TA***126X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C15 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.9203 | -6.5486
011678X | MV/LV Substation BO***678X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C16 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6562 | -7.2484
066346X | MV/LV Substation ES***346X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =257 kVA | --> | 0.38 | 0 | 0.046 | 0.326 | 0 |  | --> | C18 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4529 | -6.1835
081281 | MV/LV Substation ST***281 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3494 | -6.3585
066673Z | MV/LV Substation NO***673Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C12 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4584 | -6.2099
281759Z | MV/LV Substation FU***759Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.372 | 4.3 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C17 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8267 | -8.3153
049496 | MV/LV Substation DR***496 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.016 | 0.21 |  | --> | 0.095 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =69 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.819 | -7.7676
002773 | MV/LV Substation RI***773 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.209 | 2.36 |  | --> | 0.38 | 0 | 0.035 | 0.327 | 0 |  | --> | C16 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1887 | -6.1324
011289 | MV/LV Substation RA***289 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6872 | -7.2395
067524X | MV/LV Substation RO***524X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C17 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.7031 | -8.6009
064932Y | MV/LV Substation IN***932Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.088 | 0 | 0 | Constrained, otherwise capacity available =298 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6861 | -6.2487
033502X | MV/LV Substation KI***502X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =298 kVA | --> | 0.38 | 0 | 0 | 0.059 | 0 | Constrained, otherwise capacity available =366 kW | --> | C23 ex CREGG ROAD | Cregg Road [T41,T42] | BALLYDINE |  | 52.354 | -7.3127
0154006 | MV/LV Substation SC***4006 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2513 | -6.5814
154489Z | MV/LV Substation WI***489Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =289 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3804 | -6.3993
064703Y | MV/LV Substation CA***703Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =193 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C16 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7098 | -6.3734
165887 | MV/LV Substation SH***887 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C11 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6472 | -8.8782
156738Y | MV/LV Substation KI***738Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =52 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2028 | -6.84
0394220 | MV/LV Substation GA***4220 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2798 | -8.9471
288096X | MV/LV Substation OR***096X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.014 | 0.172 | 0 |  | --> | C19 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2636 | -6.204
1584066 | MV/LV Substation GA***4066 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9687 | -9.2733
165927X | MV/LV Substation GE***927X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.6572 | -8.9733
039606X | MV/LV Substation LE***606X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.156 | 11.03 |  | --> | 0.19 | 0 | 0.013 | 0.174 | 0 |  | --> | C17 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2682 | -9.1169
026514Y | MV/LV Substation SU***514Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7026 | -8.5012
151271 | MV/LV Substation JA***271 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.334 | -8.5772
062306Y | MV/LV Substation MA***306Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.154 | 0.72 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 53.9987 | -6.3818
117385Y | MV/LV Substation KE***385Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.0571 | -8.4245
011016 | MV/LV Substation AU***016 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6772 | -7.2694
184016 | MV/LV Substation MO***016 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.358 | 3.38 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C13 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.122 | -6.7431
0564246 | MV/LV Substation BI***4246 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.389 | 0.89 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E18 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1058 | -7.9087
023746Y | MV/LV Substation AN***746Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.147 | -8.399
250618 | MV/LV Substation EY***618 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 0.3 |  | --> | 0.095 | 0 | 0.042 | 0 | 0 | Constrained, otherwise capacity available =60 kW | --> | C17 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.2008 | -8.1348
127804Y | MV/LV Substation LI***804Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.256 | 5.89 |  | --> | 0.38 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =316 kW | --> | C17 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5095 | -7.89
063368X | MV/LV Substation BI***368X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8475 | -6.6563
0214015 | MV/LV Substation OR***4015 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =221 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9053 | -8.5011
154093Z | MV/LV Substation WE***093Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =718 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3901 | -6.3859
255397 | MV/LV Substation EA***397 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6398 | -8.3023
0314180 | MV/LV Substation MO***4180 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =343 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C11 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0962 | -7.6069
293004 | MV/LV Substation TH***004 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 0.43 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7978 | -6.7417
0594241 | MV/LV Substation TU***4241 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 2.57 |  | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | C13 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 53.9921 | -7.1642
010205 | MV/LV Substation KN***205 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.5222 | -6.9024
0814218 | MV/LV Substation SP***4218 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =315 kVA | --> | 0.38 | 0 | 0.01 | 0.361 | 0 |  | --> | C14 ex INCHICORE NORTH | Inchicore North [T41] | INCHICORE 220KV |  | 53.348 | -6.3401
018076 | MV/LV Substation TA***076 |  | 20 kV | _ | LV | 50 kVA :Building Structure | 0.05 | --> | 0.05 | 0 | 3.75 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5883 | -9.3648
016231Z | MV/LV Substation GR***231Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =585 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2986 | -6.477
0254330 | MV/LV Substation GA***4330 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.4055 | -8.6639
266376 | MV/LV Substation CO***376 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E18 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.244 | -7.2658
151683X | MV/LV Substation BA***683X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3784 | -8.3426
011027 | MV/LV Substation AU***027 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.028 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =24 kW | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6765 | -7.2689
015876Y | MV/LV Substation IR***876Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2342 | -6.5806
109548 | MV/LV Substation SM***548 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.371 | 0.38 |  | --> | 0.38 | 0 | 0.04 | 0.346 | 0 |  | --> | C20 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7165 | -8.8702
0664349 | MV/LV Substation CR***4349 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =591 kVA | --> | 0.598 | 0 | 0.152 | 0 | 0 | Constrained, otherwise capacity available =480 kW | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4694 | -6.2484
0334165 | MV/LV Substation BA***4165 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C23 ex CREGG ROAD | Cregg Road [T41,T42] | BALLYDINE |  | 52.3715 | -7.3512
015847Z | MV/LV Substation TU***847Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2904 | -6.6131
0144207 | MV/LV Substation RA***4207 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C20 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.17 | -6.8481
062117 | MV/LV Substation SE***117 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.138 | 3.12 |  | --> | 0.19 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C12 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9937 | -6.3886
025424 | MV/LV Substation NE***424 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 2.96 |  | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | E14 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3469 | -8.7693
276894 | MV/LV Substation MO***894 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C20 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.1005 | -9.4718
042618X | MV/LV Substation RO***618X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.157 | 1.93 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C16 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8662 | -9.2988
071882 | MV/LV Substation CH***882 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.024 | 0.354 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1293 | -6.0659
012116 | MV/LV Substation NA***116 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =245 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C22 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8356 | -6.9274
066523Z | MV/LV Substation GL***523Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5227 | -6.1668
153251 | MV/LV Substation GR***251 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E17 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8113 | -8.4327
015175Y | MV/LV Substation FO***175Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.223 | -6.615
052744Y | MV/LV Substation CA***744Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =23 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E20 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.3903 | -7.3753
007550Z | MV/LV Substation BA***550Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 16.12 |  | --> | 0.095 | 0 | 0.05 | 0.056 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3955 | -6.4022
0584451 | MV/LV Substation MA***4451 |  | 20 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.033 | 0.18 |  | --> | 0.031 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C18 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.8204 | -8.0615
046169 | MV/LV Substation HO***169 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 4.13 |  | --> | 0.095 | 0 | 0.003 | 0.091 | 0 |  | --> | C13 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.4166 | -8.4837
068605X | MV/LV Substation MA***605X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =982 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3533 | -6.259
164347X | MV/LV Substation LE***347X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.128 | 0.88 |  | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C22 ex ROSS CARBERY | Ross Carbery [T41,T42] | DUNMANWAY |  | 51.5829 | -9.1356
062272X | MV/LV Substation WO***272X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.327 | 5.69 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C11 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.9934 | -6.393
050505Y | MV/LV Substation IN***505Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.61 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4218 | -7.9318
054066 | MV/LV Substation CO***066 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.167 | 2.78 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E16 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.8417 | -7.4
156496X | MV/LV Substation CO***496X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C20 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2392 | -6.944
366501 | MV/LV Substation CL***501 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.47 |  | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | C15 ex SCREEB | Screeb [T41] | SCREEB |  | 53.3233 | -9.8178
018261 | MV/LV Substation MO***261 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.042 | 3.75 |  | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | C14 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.5 | -9.3723
039390X | MV/LV Substation GA***390X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 11.03 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C18 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2652 | -9.1269
154293Z | MV/LV Substation ST***293Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3796 | -6.395
034365Y | MV/LV Substation MI***365Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.064 | 0.57 |  | --> | 0.19 | 0 | 0.18 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E23 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.4521 | -7.7693
154289Y | MV/LV Substation AL***289Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.4271 | -6.5164
220581X | MV/LV Substation MI***581X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.082 | 2.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.191 | -9.2367
0174397 | MV/LV Substation KC***4397 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.251 | 1.05 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =558 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3755 | -9.0517
120260Y | MV/LV Substation WO***260Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3561 | -7.1967
0674235 | MV/LV Substation PA***4235 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E13 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7626 | -8.4791
035417X | MV/LV Substation BA***417X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 6.17 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3628 | -7.9694
0154348 | MV/LV Substation RA***4348 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2129 | -6.672
156913X | MV/LV Substation CR***913X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.47 |  | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C12 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2705 | -6.9378
0684215 | MV/LV Substation RA***4215 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.227 | 11.14 |  | --> | 0.38 | 0 | 0.225 | 0.189 | 0 |  | --> | C12 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3778 | -6.3203
015417Z | MV/LV Substation AS***417Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2399 | -6.5859
157300X | MV/LV Substation CA***300X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 1.55 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 53.9876 | -7.6667
093098 | MV/LV Substation JA***098 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C16 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3827 | -6.2942
180075Y | MV/LV Substation KE***075Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.158 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C25 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7273 | -6.8743
111433 | MV/LV Substation EA***433 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.204 | 0.94 |  | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =315 kW | --> | E15 ex CASTLETOWNBERE | Castletownbere [T421] | BALLYLICKY |  | 51.653 | -9.9084
003492 | MV/LV Substation BA***492 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =63 kW | --> | C11 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9034 | -6.2578
293853Y | MV/LV Substation SP***853Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9312 | -6.7112
031916 | MV/LV Substation KI***916 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.1008 | -7.5714
011117 | MV/LV Substation VE***117 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.272 | 5.05 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6556 | -7.2332
180472 | MV/LV Substation BE***472 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C23 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7001 | -6.9096
160468Y | MV/LV Substation MI***468Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C16 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.148 | -7.185
237709 | MV/LV Substation BE***709 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.9017 | -6.3919
003106Y | MV/LV Substation MA***106Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.15 | 11.58 |  | --> | 0.19 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | C20 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9797 | -6.0504
0214216 | MV/LV Substation HO***4216 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 4.67 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.9009 | -8.459
067124Z | MV/LV Substation GO***124Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C17 ex GILLOGUE | Gillogue [T41,T42] | ARDNACRUSHA |  | 52.6984 | -8.5987
204362 | MV/LV Substation CA***362 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E13 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2786 | -7.444
048297X | MV/LV Substation GL***297X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9691 | -7.9019
252888X | MV/LV Substation CA***888X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 1.32 |  | --> | 0.38 | 0 | 0 | 0.367 | 0 |  | --> | C27 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4889 | -10.0198
053891Y | MV/LV Substation CL***891Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =408 kVA | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C23 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2663 | -7.4681
007631Z | MV/LV Substation CO***631Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2495 | -6.5063
417774 | MV/LV Substation RY***774 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 8.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0887 | -8.1116
093237X | MV/LV Substation JO***237X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =149 kVA | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | C17 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.413 | -6.3216
0894197 | MV/LV Substation AL***4197 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.1 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =593 kW | --> | C14 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1136 | -9.1581
064036Z | MV/LV Substation SA***036Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6533 | -6.2458
052952Z | MV/LV Substation CA***952Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | E14 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4158 | -7.3092
127702X | MV/LV Substation O/***702X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6657 | -7.8261
008143 | MV/LV Substation CO***143 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4204 | -6.8638
110204X | MV/LV Substation WO***204X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.301 | 0.76 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E19 ex KENMARE | Kenmare [T421] | KNOCKEARAGH |  | 51.8201 | -9.8765
064312 | MV/LV Substation DR***312 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C18 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7201 | -6.3847
138724 | MV/LV Substation CA***724 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 2.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C26 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9333 | -6.986
130091X | MV/LV Substation RA***091X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.118 | 2.55 |  | --> | 0.19 | 0 | 0.055 | 0 | 0 | Constrained, otherwise capacity available =138 kW | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6558 | -7.5215
005258 | MV/LV Substation CL***258 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6857 | -6.2656
067121X | MV/LV Substation ES***121X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =587 kVA | --> | 0.598 | 0 | 0.056 | 0.5 | 0 |  | --> | C22 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6512 | -8.5869
0654248 | MV/LV Substation TA***4248 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6079 | -6.2093
235241 | MV/LV Substation FA***241 |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E18 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8934 | -8.7596
0934217 | MV/LV Substation BU***4217 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =849 kVA | --> | 0.95 | 0 | 0.02 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4058 | -6.1812
120282Y | MV/LV Substation LU***282Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2774 | -6.9411
350483 | MV/LV Substation TU***483 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 1.57 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4687 | -8.3297
0144258 | MV/LV Substation RE***4258 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =950 kW | --> | C13 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1549 | -6.9158
044852 | MV/LV Substation KA***852 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.369 | 0.43 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9831 | -9.1135
238184 | MV/LV Substation DE***184 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6586 | -9.2694
062849 | MV/LV Substation MO***849 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 1.03 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9252 | -6.3802
056751X | MV/LV Substation LI***751X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E20 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0143 | -8.0326
281667Z | MV/LV Substation LY***667Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.88 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8978 | -8.4817
182241 | MV/LV Substation JO***241 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C12 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.9101 | -8.5312
009700 | MV/LV Substation BA***700 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.95 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2352 | -7.1926
081582Z | MV/LV Substation FO***582Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C16 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3709 | -6.4397
043297 | MV/LV Substation RA***297 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9474 | -8.9466
069486 | MV/LV Substation KI***486 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.339 | 0.91 |  | --> | 0.598 | 0 | 0.074 | 0.5 | 0 |  | --> | C18 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3124 | -6.3006
004086Y | MV/LV Substation BR***086Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.256 | 0.45 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C15 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8808 | -6.3306
015978 | MV/LV Substation LE***978 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.059 | 12.6 |  | --> | 0.095 | 0 | 0 | 0.089 | 0 |  | --> | C18 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2368 | -6.673
160007 | MV/LV Substation PA***007 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C15 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1137 | -7.3287
005066 | MV/LV Substation GL***066 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 17.8 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6662 | -6.219
024555 | MV/LV Substation IM***555 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2809 | -8.6869
065262Z | MV/LV Substation PA***262Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6034 | -6.1896
054647X | MV/LV Substation BA***647X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =53 kVA | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C16 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.8728 | -7.3081
049117Z | MV/LV Substation MA***117Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.476 | 2.8 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | C17 ex GLEBE | Glebe [T41,T42] | RICHMOND |  | 53.7213 | -7.8023
095020 | MV/LV Substation GL***020 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.152 | 0.7 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =337 kW | --> | C14 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6365 | -9.4908
116357 | MV/LV Substation DE***357 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 7.32 |  | --> | 0.095 | 0 | 0.024 | 0.07 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8061 | -9.522
033624 | MV/LV Substation WI***624 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =23 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C18 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.4608 | -7.3986
031009 | MV/LV Substation CA***009 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9431 | -7.8022
206501 | MV/LV Substation GE***501 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.151 | 2.76 |  | --> | 0.19 | 0 | 0.005 | 0.18 | 0 |  | --> | E12 ex BANGOR ERRIS | Bangor Erris [T421] | BELLACORICK |  | 54.1143 | -9.9006
095739X | MV/LV Substation FE***739X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 0.7 |  | --> | 0.19 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C15 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6316 | -9.4798
495511X | MV/LV Substation MU***511X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9057 | -9.7861
253906Y | MV/LV Substation CL***906Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E17 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4522 | -9.0942
069202 | MV/LV Substation AN***202 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =946 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex DONNYBROOK | Donnybrook [T41,T42] | MILLTOWN (DR) |  | 53.3278 | -6.2307
0264071 | MV/LV Substation KN***4071 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | C21 ex KINSALE |  |  |  | 51.7344 | -8.4481
365415X | MV/LV Substation PI***415X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.19 | 0 | 0.012 | 0.166 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3137 | -6.4062
003005 | MV/LV Substation RA***005 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.13 | 11.58 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9916 | -6.0799
365893 | MV/LV Substation BI***893 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =211 kVA | --> | 0.38 | 0 | 0.034 | 0.328 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2996 | -6.356
214667 | MV/LV Substation FE***667 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7704 | -9.1001
066254 | MV/LV Substation GR***254 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =293 kVA | --> | 0.38 | 0 | 0.029 | 0.344 | 0 |  | --> | C12 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3978 | -6.1409
039399 | MV/LV Substation BA***399 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.011 | 0.038 | 0 |  | --> | C28 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.3038 | -9.0334
026827Y | MV/LV Substation WO***827Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.172 | 8.66 |  | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C13 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7326 | -8.7583
068404X | MV/LV Substation GL***404X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3464 | -6.2498
3654149 | MV/LV Substation TH***4149 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C26 ex CITYWEST | Citywest [T101,T102] | INCHICORE 220KV |  | 53.2892 | -6.4183
1094003 | MV/LV Substation FI***4003 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.381 | 0.38 | Constrained, otherwise capacity available =433 kVA | --> | 0.598 | 0 | 0.037 | 0.5 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7094 | -8.8681
238397 | MV/LV Substation GO***397 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6137 | -9.4151
017981X | MV/LV Substation CR***981X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.057 | 1.98 |  | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5211 | -8.7131
0094337 | MV/LV Substation ST***4337 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.53 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C21 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2548 | -7.1182
156851Y | MV/LV Substation DE***851Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =530 kVA | --> | 0.598 | 0 | 0.049 | 0 | 0 | Constrained, otherwise capacity available =548 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3825 | -7.0196
001168 | MV/LV Substation HI***168 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 1.23 |  | --> | 0.38 | 0 | 0.045 | 0.329 | 0 |  | --> | C23 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2754 | -6.1128
064771X | MV/LV Substation AS***771X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C20 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.6935 | -6.3906
0214310 | MV/LV Substation AR***4310 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C21 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9197 | -8.4496
069288 | MV/LV Substation BU***288 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =488 kVA | --> | 0.598 | 0 | 0.046 | 0.5 | 0 |  | --> | C18 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2917 | -6.2961
041788 | MV/LV Substation BR***788 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7849 | -9.1553
0684646 | MV/LV Substation TR***4646 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 7.2 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C28 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3398 | -6.2407
011218 | MV/LV Substation MA***218 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6441 | -7.2445
068918 | MV/LV Substation TH***918 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =532 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3772 | -6.2674
118031 | MV/LV Substation CH***031 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.154 | 2 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C11 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3303 | -8.2118
365769X | MV/LV Substation TU***769X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C11 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2914 | -6.4268
066022Z | MV/LV Substation DU***022Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C19 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4625 | -6.2306
116734X | MV/LV Substation FU***734X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 7.32 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C11 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8014 | -9.5376
026229Z | MV/LV Substation BA***229Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 8.66 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C17 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7687 | -8.6598
164564 | MV/LV Substation LA***564 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5728 | -9.2439
281963Y | MV/LV Substation FI***963Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | C15 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8168 | -8.4912
2514151 | MV/LV Substation GO***4151 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C28 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3458 | -8.9476
164987X | MV/LV Substation BU***987X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5851 | -9.2677
055402 | MV/LV Substation TI***402 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9574 | -7.8398
006166Y | MV/LV Substation DA***166Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 4.38 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.45 | -6.3466
0234091 | MV/LV Substation FE***4091 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C15 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1401 | -8.2775
003486Y | MV/LV Substation RI***486Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.377 | 18.08 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C18 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8881 | -6.1438
049563 | MV/LV Substation PU***563 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.213 | 0.21 | Constrained, otherwise capacity available =438 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | E21 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.79 | -7.8724
007585Z | MV/LV Substation LA***585Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2117 | -6.3786
1184108 | MV/LV Substation KI***4108 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3288 | -8.1883
220757X | MV/LV Substation BE***757X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 7.61 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E12 ex BELLACORICK | Bellacorick [T122] | BELLACORICK |  | 54.1203 | -9.5763
066890 | MV/LV Substation KI***890 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5181 | -6.1828
3654129 | MV/LV Substation CO***4129 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =560 kVA | --> | 0.598 | 0 | 0.206 | 0.436 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3175 | -6.4169
069633 | MV/LV Substation SW***633 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.28 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3291 | -6.2285
2814197 | MV/LV Substation BR***4197 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 17.47 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E12 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8874 | -8.7052
0094267 | MV/LV Substation KN***4267 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =528 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2392 | -7.095
138479 | MV/LV Substation BE***479 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.061 | 2.18 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C26 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9175 | -6.9589
030716 | MV/LV Substation PO***716 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =51 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9614 | -7.8671
2884195 | MV/LV Substation TB***4195 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2233 | -6.123
052543X | MV/LV Substation KI***543X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5143 | -7.1419
111132 | MV/LV Substation KE***132 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.001 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.7505 | -9.3697
062212Y | MV/LV Substation BR***212Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.129 | 0.72 |  | --> | 0.19 | 0 | 0.071 | 0 | 0 | Constrained, otherwise capacity available =128 kW | --> | C15 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0002 | -6.3714
118710X | MV/LV Substation CA***710X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3625 | -8.3212
004701 | MV/LV Substation BA***701 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C23 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7511 | -6.2151
036071 | MV/LV Substation VO***071 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =361 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.478 | -8.1565
1394309 | MV/LV Substation AC***4309 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.9107 | -7.2207
150832 | MV/LV Substation DU***832 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 3.96 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8117 | -7.7751
153109X | MV/LV Substation AR***109X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7509 | -8.5075
0644375 | MV/LV Substation LI***4375 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =523 kVA | --> | 0.598 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =573 kW | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7364 | -6.3406
005126 | MV/LV Substation TA***126 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.335 | 17.8 |  | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6689 | -6.213
068875 | MV/LV Substation CU***875 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.2 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3423 | -6.249
081260X | MV/LV Substation HE***260X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3641 | -6.4098
0934302 | MV/LV Substation FI***4302 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C17 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.4004 | -6.2983
059142X | MV/LV Substation AG***142X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C11 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9596 | -7.3381
068322 | MV/LV Substation QU***322 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.466 | 3.38 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3358 | -6.2544
011925X | MV/LV Substation DR***925X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C11 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6449 | -7.2904
209048X | MV/LV Substation UM***048X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =12 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | C21 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.1665 | -7.8004
0694053 | MV/LV Substation KN***4053 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.91 |  | --> | 0.598 | 0 | 0.034 | 0.5 | 0 |  | --> | C13 ex CRUMLIN | Crumlin [T41,T42] | INCHICORE 220KV |  | 53.3294 | -6.3191
001358 | MV/LV Substation ST***358 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.178 | 4.37 |  | --> | 0.38 | 0 | 0.055 | 0.308 | 0 |  | --> | C14 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2929 | -6.1417
009694X | MV/LV Substation ST***694X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =215 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C12 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2389 | -7.1123
082463X | MV/LV Substation BR***463X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =13 kVA | --> | 0.048 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =22 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6446 | -6.555
049721Y | MV/LV Substation TH***721Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 0.21 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8182 | -7.7684
009748Y | MV/LV Substation FE***748Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.325 | 8.16 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C13 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2646 | -7.1055
288217X | MV/LV Substation BA***217X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =538 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C19 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2728 | -6.255
007422 | MV/LV Substation CA***422 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.263 | 16.12 |  | --> | 0.38 | 0 | 0 | 0.361 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.384 | -6.4494
031033 | MV/LV Substation CA***033 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =203 kVA | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0888 | -7.634
164902X | MV/LV Substation DE***902X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5329 | -9.3122
015522Z | MV/LV Substation KI***522Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C19 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2852 | -6.759
066481 | MV/LV Substation WA***481 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4288 | -6.2275
064806 | MV/LV Substation BE***806 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7501 | -6.4385
127951Y | MV/LV Substation CL***951Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6734 | -7.6942
2884072 | MV/LV Substation GR***4072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.38 | 0 | 0 | 0.35 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2513 | -6.1555
068835 | MV/LV Substation CO***835 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.32 | 7.61 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex SHERIFF STREET | Sheriff Street [T41,T42] | FRANCIS STREET |  | 53.3518 | -6.2479
064550Y | MV/LV Substation GR***550Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =235 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7152 | -6.5313
164574 | MV/LV Substation BE***574 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C22 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5794 | -9.2851
010157X | MV/LV Substation KN***157X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.6204 | -6.8518
022790X | MV/LV Substation TH***790X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.35 | 4.55 |  | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C14 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1481 | -8.6426
081263Z | MV/LV Substation ST***263Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3194 | -6.6069
026393 | MV/LV Substation ME***393 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C17 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7359 | -8.5546
0034261 | MV/LV Substation HE***4261 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9499 | -6.0307
069730 | MV/LV Substation O ***730 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 9.28 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C06 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3326 | -6.2325
0094263 | MV/LV Substation MO***4263 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2059 | -7.0785
062730Y | MV/LV Substation GR***730Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.474 | 3.47 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | E16 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.033 | -6.1332
368918 | MV/LV Substation ER***918 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7566 | -8.776
0124034 | MV/LV Substation IR***4034 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8468 | -6.9257
204274 | MV/LV Substation CA***274 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =613 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | E15 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1272 | -7.4399
055933 | MV/LV Substation MT***933 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9605 | -7.8453
180990X | MV/LV Substation CH***990X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.292 | 3.27 |  | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =342 kW | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7337 | -6.8783
161496 | MV/LV Substation CO***496 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex SPIDDAL |  |  |  | 53.2465 | -9.37
266010X | MV/LV Substation FA***010X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2833 | -7.2233
254498 | MV/LV Substation TI***498 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 10.7 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C22 ex CLOON | Cloon [T42,T421] | CLOON |  | 53.5094 | -8.8518
2494122 | MV/LV Substation CO***4122 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 52.0279 | -7.844
0684226 | MV/LV Substation HI***4226 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.61 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex SHERIFF STREET | Sheriff Street [T41,T42] | FRANCIS STREET |  | 53.3484 | -6.2465
031473Y | MV/LV Substation DE***473Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.1111 | -7.5948
0684539 | MV/LV Substation TH***4539 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.47 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3412 | -6.2887
003517Y | MV/LV Substation AV***517Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9235 | -6.2443
052006 | MV/LV Substation HA***006 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.118 | 10.9 |  | --> | 0.19 | 0 | 0.005 | 0.175 | 0 |  | --> | C19 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5287 | -7.3413
032097Y | MV/LV Substation CH***097Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex KILMACTHOMAS | Kilmacthomas [T421,T422] | DUNGARVAN |  | 52.2246 | -7.3394
184103X | MV/LV Substation CR***103X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1603 | -6.8127
127478X | MV/LV Substation CL***478X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =4 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | C12 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.666 | -7.8051
0624320 | MV/LV Substation PO***4320 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 3.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E16 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0261 | -6.1313
053214 | MV/LV Substation KI***214 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.009 | 0.04 | 0 |  | --> | C21 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2147 | -7.4547
0294401 | MV/LV Substation BA***4401 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C12 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9174 | -8.2421
162956 | MV/LV Substation GR***956 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 7.25 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C12 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8579 | -7.6758
1604421 | MV/LV Substation HE***4421 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =950 kW | --> | C23 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1394 | -7.1492
149316 | MV/LV Substation KI***316 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C14 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6569 | -8.1183
293797Z | MV/LV Substation HU***797Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9059 | -6.6078
0684328 | MV/LV Substation HO***4328 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3452 | -6.2343
069712 | MV/LV Substation BA***712 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.28 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3304 | -6.2276
0474088 | MV/LV Substation AG***4088 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9619 | -8.3054
2354116 | MV/LV Substation CO***4116 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =618 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | E11 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8453 | -8.7903
001012X | MV/LV Substation GL***012X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.19 | 4.01 |  | --> | 0.19 | 0 | 0.004 | 0.186 | 0 |  | --> | C19 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.267 | -6.1372
014078X | MV/LV Substation MO***078X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1824 | -6.8192
365297 | MV/LV Substation FA***297 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2575 | -6.5275
153902 | MV/LV Substation LI***902 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E14 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8312 | -8.2375
244792X | MV/LV Substation CH***792X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.108 | -9.7787
0844007 | MV/LV Substation BO***4007 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.1386 | -8.9265
081602Z | MV/LV Substation DM***602Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =566 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3463 | -6.4082
050071Y | MV/LV Substation BN***071Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.61 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.3471 | -7.9296
066025Y | MV/LV Substation OR***025Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =245 kVA | --> | 0.38 | 0 | 0.054 | 0 | 0 | Constrained, otherwise capacity available =318 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.462 | -6.2464
002970 | MV/LV Substation BU***970 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0.189 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1787 | -6.171
253616X | MV/LV Substation BR***616X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C18 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4731 | -9.0982
066024Y | MV/LV Substation MA***024Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =265 kVA | --> | 0.38 | 0 | 0.043 | 0 | 0 | Constrained, otherwise capacity available =329 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4616 | -6.2439
012121 | MV/LV Substation RE***121 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.113 | 1.99 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =339 kW | --> | C17 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8283 | -6.9343
253860Z | MV/LV Substation MU***860Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.6005 | -8.7686
116640X | MV/LV Substation SA***640X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.192 | 7.32 |  | --> | 0.38 | 0 | 0.009 | 0.344 | 0 |  | --> | C13 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.7968 | -9.5215
029801X | MV/LV Substation GR***801X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.916 | -8.0556
004492Y | MV/LV Substation GA***492Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 18.08 |  | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8017 | -6.1665
235210 | MV/LV Substation ST***210 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8456 | -8.7715
244838X | MV/LV Substation ST***838X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | E11 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1423 | -9.7131
025669Y | MV/LV Substation HO***669Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 2.96 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E12 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3564 | -8.6762
037329 | MV/LV Substation BA***329 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8686 | -8.9737
035807X | MV/LV Substation CL***807X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 6.17 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3771 | -7.9139
281968X | MV/LV Substation DR***968X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.88 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.895 | -8.4737
001184 | MV/LV Substation I.***184 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =481 kVA | --> | 0.598 | 0 | 0.032 | 0.5 | 0 |  | --> | C12 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2948 | -6.2324
2534353 | MV/LV Substation OP***4353 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C18 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4708 | -9.1015
120599X | MV/LV Substation CL***599X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3577 | -7.2284
433516X | MV/LV Substation SC***516X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9182 | -8.7761
003577Y | MV/LV Substation IV***577Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =324 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9374 | -6.2284
151465X | MV/LV Substation BA***465X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C25 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.4458 | -8.4178
049456Y | MV/LV Substation BA***456Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.5915 | -7.6068
180752X | MV/LV Substation GI***752X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.7529 | -6.8841
156313 | MV/LV Substation KI***313 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2341 | -6.9626
130243X | MV/LV Substation ED***243X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.472 | 2.55 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | E16 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6985 | -7.6183
136124Y | MV/LV Substation LE***124Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C18 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.5469 | -8.0546
118528 | MV/LV Substation BA***528 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.4717 | -8.4988
019327X | MV/LV Substation FE***327X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.328 | 1.54 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =556 kW | --> | C11 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2637 | -9.7013
071822 | MV/LV Substation CO***822 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 5.58 |  | --> | 0.38 | 0 | 0.013 | 0.355 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.103 | -6.0676
156986Y | MV/LV Substation GO***986Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 2.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E17 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.2395 | -6.9981
019994 | MV/LV Substation BA***994 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.162 | 2.18 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C21 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.269 | -9.7209
149364 | MV/LV Substation SE***364 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6285 | -8.1189
0144287 | MV/LV Substation IR***4287 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 0.63 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1182 | -6.6908
039889 | MV/LV Substation ID***889 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0.025 | 0.5 | 0 |  | --> | C32 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2904 | -9.0746
2104207 | MV/LV Substation MA***4207 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C19 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9385 | -6.7739
033293 | MV/LV Substation AS***293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.006 | 0.059 | 0 | Constrained, otherwise capacity available =360 kW | --> | C25 ex CREGG ROAD | Cregg Road [T41,T42] | BALLYDINE |  | 52.3481 | -7.4094
039192 | MV/LV Substation FA***192 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.242 | 11.03 |  | --> | 0.38 | 0 | 0.025 | 0.339 | 0 |  | --> | C31 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.285 | -9.0706
095018 | MV/LV Substation BU***018 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.29 | 0.7 |  | --> | 0.598 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =544 kW | --> | C15 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6386 | -9.4831
192429 | MV/LV Substation TE***429 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 1.56 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C15 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.1152 | -8.2867
067292Y | MV/LV Substation CH***292Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 13.8 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C21 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6597 | -8.5899
081517Z | MV/LV Substation DA***517Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =485 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.333 | -6.3745
082657X | MV/LV Substation BA***657X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E16 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6277 | -6.6927
108055 | MV/LV Substation AS***055 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.023 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5025 | -8.1779
0814318 | MV/LV Substation HA***4318 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =529 kVA | --> | 0.598 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C12 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3643 | -6.5275
293064Z | MV/LV Substation RA***064Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.83 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6592 | -6.7906
0994142 | MV/LV Substation MU***4142 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 2.96 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9847 | -7.7189
007548X | MV/LV Substation RI***548X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 1.4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.1894 | -6.5169
024657X | MV/LV Substation CA***657X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.291 | -8.7029
068056 | MV/LV Substation CA***056 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.122 | 11.14 |  | --> | 0.598 | 0 | 0.063 | 0.479 | 0 |  | --> | C11 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3613 | -6.2931
233439 | MV/LV Substation TO***439 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C23 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2904 | -9.427
028446 | MV/LV Substation CA***446 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C13 ex COW CROSS |  |  |  | 51.8711 | -8.321
032798 | MV/LV Substation CL***798 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1704 | -7.07
099513 | MV/LV Substation DO***513 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9427 | -7.8342
058008 | MV/LV Substation GO***008 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C11 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.8673 | -8.2079
009966 | MV/LV Substation RE***966 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 8.16 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2784 | -7.0789
1564062 | MV/LV Substation JM***4062 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =274 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2227 | -6.9212
016115Z | MV/LV Substation BR***115Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3174 | -6.4932
034038 | MV/LV Substation EA***038 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.444 | 0.95 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =573 kW | --> | C16 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3534 | -7.7012
014319X | MV/LV Substation DU***319X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.12 |  | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.117 | -6.9722
0814061 | MV/LV Substation ST***4061 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2977 | -6.5817
029197Y | MV/LV Substation RE***197Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =550 kW | --> | C17 ex CARRIGTWOHILL |  |  |  | 51.8903 | -8.2582
007261X | MV/LV Substation BA***261X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2049 | -6.5341
116889X | MV/LV Substation HO***889X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 8.1 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.8037 | -9.9505
156610Y | MV/LV Substation FE***610Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E16 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.2575 | -6.9011
288209X | MV/LV Substation DU***209X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.488 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2884 | -6.2432
350827 | MV/LV Substation MU***827 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4589 | -8.2594
288220X | MV/LV Substation TA***220X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 19.52 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C17 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2886 | -6.2453
039883 | MV/LV Substation WE***883 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.472 | 11.03 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C34 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2766 | -9.0772
0294402 | MV/LV Substation AR***4402 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.8975 | -8.0502
066283 | MV/LV Substation WI***283 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.058 | 0 | 0 | Constrained, otherwise capacity available =322 kW | --> | C19 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4598 | -6.2305
018402Z | MV/LV Substation DU***402Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.75 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C13 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4562 | -9.4942
0814142 | MV/LV Substation SH***4142 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =240 kVA | --> | 0.38 | 0 | 0.292 | 0.141 | 0 |  | --> | E20 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3471 | -6.471
252472X | MV/LV Substation PO***472X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 1.32 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C24 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.5571 | -10.1821
120105Y | MV/LV Substation ED***105Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.2593 | -7.087
108851 | MV/LV Substation ES***851 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 1.57 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.4921 | -8.1546
022076 | MV/LV Substation TH***076 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 4.55 |  | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C14 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1432 | -8.6514
119099Y | MV/LV Substation CH***099Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =142 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C15 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1663 | -8.8269
046131X | MV/LV Substation MC***131X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.179 | 5.48 |  | --> | 0.19 | 0 | 0 | 0.187 | 0 |  | --> | C11 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2766 | -8.4691
1564245 | MV/LV Substation DE***4245 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3831 | -7.0238
047930 | MV/LV Substation CU***930 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.087 | 1.04 |  | --> | 0.095 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =64 kW | --> | C17 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.9987 | -8.1931
015459 | MV/LV Substation YE***459 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 12.6 |  | --> | 0.048 | 0 | 0.01 | 0.04 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2254 | -6.7359
056363Y | MV/LV Substation BR***363Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0848 | -7.7788
150065X | MV/LV Substation DR***065X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.15 | 3.96 |  | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | E18 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7917 | -7.6847
118526 | MV/LV Substation MO***526 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =70 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.4691 | -8.4947
0714126 | MV/LV Substation RO***4126 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.58 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0892 | -6.1163
003687X | MV/LV Substation RE***687X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 18.08 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C18 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8896 | -6.1441
034275 | MV/LV Substation WO***275 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 0.57 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.5232 | -7.7552
039277 | MV/LV Substation MO***277 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =531 kVA | --> | 0.598 | 0 | 0.013 | 0.5 | 0 |  | --> | C20 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2875 | -9.0143
293211X | MV/LV Substation SH***211X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7435 | -6.5332
288107 | MV/LV Substation HI***107 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =374 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C14 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2817 | -6.2576
130094X | MV/LV Substation BA***094X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 2.55 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.7043 | -7.6708
0684181 | MV/LV Substation HA***4181 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3443 | -6.232
068430 | MV/LV Substation CO***430 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.272 | 0.98 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3361 | -6.2584
081351Z | MV/LV Substation NE***351Z |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C12 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3688 | -6.4874
014621X | MV/LV Substation RA***621X |  | 20 kV | _ | LV | 50 kVA :Building Structure | 0.05 | --> | 0.05 | 0.05 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1149 | -6.6547
119276Y | MV/LV Substation DE***276Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.16 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C22 ex NEWMARKET (SR) | Newmarket (sr) [T41,T42] | GLENLARA |  | 52.1818 | -8.9424
260280 | MV/LV Substation MU***280 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.67 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E14 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8296 | -9.6132
059109X | MV/LV Substation CR***109X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C16 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.98 | -7.3569
109049 | MV/LV Substation PU***049 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | E16 ex DRUMLINE | Drumline [T421,T422] | DRUMLINE |  | 52.7103 | -8.8661
041307 | MV/LV Substation IN***307 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =581 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | E21 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7398 | -9.0061
196359X | MV/LV Substation TR***359X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.387 | 1.34 |  | --> | 0.38 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5098 | -6.8707
265974X | MV/LV Substation KI***974X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.066 | 0.07 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E17 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.0879 | -7.6278
039935X | MV/LV Substation BR***935X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.152 | 11.03 |  | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | C35 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2791 | -9.0678
093055Z | MV/LV Substation CE***055Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =454 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C17 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.4023 | -6.3008
064005Z | MV/LV Substation MO***005Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C13 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7208 | -6.2614
082502Y | MV/LV Substation BR***502Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6299 | -6.5557
1524084 | MV/LV Substation RY***4084 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.095 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =64 kW | --> | C17 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6076 | -8.3722
340237X | MV/LV Substation GW***237X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C16 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.9562 | -8.3594
365856 | MV/LV Substation LI***856 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =319 kVA | --> | 0.38 | 0 | 0.005 | 0.365 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3273 | -6.4158
007957 | MV/LV Substation PM***957 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 0.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3498 | -6.4568
281765Z | MV/LV Substation PE***765Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.347 | 5.49 |  | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C23 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8512 | -8.4825
060265X | MV/LV Substation RA***265X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0418 | -7.1747
0254363 | MV/LV Substation BA***4363 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.4926 | -8.6769
0674431 | MV/LV Substation PA***4431 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C20 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6468 | -8.6519
109122 | MV/LV Substation SM***122 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.244 | 0.38 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7194 | -8.8764
001813 | MV/LV Substation CA***813 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 0.86 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3053 | -6.2234
001046 | MV/LV Substation PA***046 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.013 | 0.171 | 0 |  | --> | C13 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.257 | -6.1187
260410X | MV/LV Substation MO***410X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.67 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E14 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8418 | -9.5807
2534603 | MV/LV Substation HO***4603 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4889 | -9.1027
012695X | MV/LV Substation CH***695X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.247 | 2.83 |  | --> | 0.38 | 0 | 0.061 | 0 | 0 | Constrained, otherwise capacity available =313 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7008 | -6.9585
037102Y | MV/LV Substation MU***102Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =368 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C18 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8621 | -8.985
0414002 | MV/LV Substation CO***4002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | E13 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.725 | -9.0015
017890X | MV/LV Substation GR***890X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 1.98 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4598 | -8.7671
074243X | MV/LV Substation CA***243X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =766 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =924 kW | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9424 | -8.1043
039096 | MV/LV Substation CO***096 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C22 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2828 | -9.0312
064913Y | MV/LV Substation SI***913Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.38 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =330 kW | --> | C18 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7084 | -6.3505
025818Y | MV/LV Substation ST***818Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4434 | -8.4931
039620 | MV/LV Substation OR***620 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.38 | 0 | 0.08 | 0 | 0 | Constrained, otherwise capacity available =290 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2674 | -8.9302
0064273 | MV/LV Substation LI***4273 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 3.12 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5071 | -6.5807
293847Z | MV/LV Substation IN***847Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 0.43 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.7969 | -6.7489
047014 | MV/LV Substation NE***014 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 1.04 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C18 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.845 | -8.1928
005036 | MV/LV Substation FO***036 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 17.8 |  | --> | 0.38 | 0 | 0.013 | 0.365 | 0 |  | --> | E21 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6755 | -6.3094
095513X | MV/LV Substation MO***513X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.1 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C23 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.6716 | -9.6552
109458 | MV/LV Substation BA***458 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 0.38 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C20 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7147 | -8.8801
021099 | MV/LV Substation CO***099 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =279 kVA | --> | 0.38 | 0 | 0.022 | 0.347 | 0 |  | --> | C14 ex FAIRHILL | Fairhill [T42] | KILBARRY |  | 51.8991 | -8.4977
136572X | MV/LV Substation CA***572X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =622 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C20 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.6905 | -8.1789
066389Z | MV/LV Substation RO***389Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =527 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =584 kW | --> | C16 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4435 | -6.133
022895X | MV/LV Substation BA***895X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 4.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1728 | -8.6675
238579X | MV/LV Substation FO***579X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.658 | -9.1558
064482X | MV/LV Substation BA***482X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =246 kVA | --> | 0.38 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | E17 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6682 | -6.2749
031101 | MV/LV Substation FA***101 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9504 | -7.7282
014963 | MV/LV Substation OR***963 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =52 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1443 | -6.8358
154554Z | MV/LV Substation BL***554Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.381 | -6.5725
253809Z | MV/LV Substation CL***809Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E16 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.5583 | -8.648
052374Z | MV/LV Substation BE***374Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5124 | -7.3374
250516 | MV/LV Substation CA***516 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.26 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E13 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1274 | -8.2282
051480X | MV/LV Substation AB***480X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.149 | 2.22 |  | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | E12 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3445 | -7.5884
093392X | MV/LV Substation HI***392X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =556 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C31 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.4018 | -6.2217
082072Z | MV/LV Substation GO***072Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7004 | -6.6436
010190X | MV/LV Substation OL***190X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.519 | -7.1963
253790 | MV/LV Substation CL***790 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.4756 | -8.52
014975 | MV/LV Substation MO***975 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.11 | -6.6798
037401 | MV/LV Substation BA***401 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C19 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.867 | -8.9765
007148X | MV/LV Substation CL***148X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.148 | 16.12 |  | --> | 0.19 | 0 | 0.008 | 0.177 | 0 |  | --> | E14 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3346 | -6.4927
132465X | MV/LV Substation CA***465X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E30 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2476 | -8.6642
0534271 | MV/LV Substation TH***4271 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.472 | 2.39 |  | --> | 0.598 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =554 kW | --> | C12 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2916 | -7.5002
0664124 | MV/LV Substation BE***4124 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =183 kVA | --> | 0.38 | 0 | 0.091 | 0 | 0 | Constrained, otherwise capacity available =282 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.49 | -6.162
154657Z | MV/LV Substation PA***657Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4337 | -6.4718
006407 | MV/LV Substation SA***407 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.29 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex MONFIN | Monfin [T41,T42] | WEXFORD |  | 52.4788 | -6.5557
0094327 | MV/LV Substation ES***4327 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 8.16 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2876 | -7.0613
495690X | MV/LV Substation DO***690X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.5 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 54.0097 | -10.0276
038006 | MV/LV Substation CO***006 |  | 20 kV | _ | LV | 50 kVA :Building Structure | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =25 kW | --> | E13 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0923 | -8.838
156911X | MV/LV Substation KI***911X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2292 | -7.128
249423 | MV/LV Substation CA***423 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C25 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1413 | -7.7153
061827 | MV/LV Substation TU***827 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C19 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.0427 | -6.8703
108730 | MV/LV Substation BA***730 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.57 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =943 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5549 | -8.1415
365833X | MV/LV Substation KI***833X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =107 kVA | --> | 0.19 | 0 | 0.008 | 0.171 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3182 | -6.417
156233Z | MV/LV Substation KI***233Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2402 | -6.9611
365027X | MV/LV Substation BA***027X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.598 | 0 | 0.039 | 0.5 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3242 | -6.4111
020181 | MV/LV Substation AR***181 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C11 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0669 | -9.4986
1274143 | MV/LV Substation MO***4143 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5031 | -7.81
048789 | MV/LV Substation MO***789 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.8596 | -7.9158
074546X | MV/LV Substation RE***546X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =600 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C17 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.942 | -8.1094
265202Y | MV/LV Substation CL***202Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.199 | 2.56 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C17 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0777 | -7.5971
009320Y | MV/LV Substation TE***320Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 13.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2397 | -7.1765
021731Z | MV/LV Substation HA***731Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0.115 | 0.498 | 0 |  | --> | C36 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8946 | -8.333
066990 | MV/LV Substation CO***990 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4699 | -6.1317
0214284 | MV/LV Substation DU***4284 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =583 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9251 | -8.4862
064846Y | MV/LV Substation SE***846Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C13 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7155 | -6.2573
156286Y | MV/LV Substation BE***286Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =171 kVA | --> | 0.19 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C19 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2337 | -6.973
019057X | MV/LV Substation BA***057X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.047 | 0.05 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2698 | -9.6864
118535 | MV/LV Substation GR***535 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.4709 | -8.512
077202X | MV/LV Substation TH***202X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | E16 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5578 | -8.7904
015947X | MV/LV Substation HA***947X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =158 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2412 | -6.586
007691Y | MV/LV Substation WH***691Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.23 | 0.9 |  | --> | 0.38 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =319 kW | --> | C19 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3243 | -6.5007
249208 | MV/LV Substation BA***208 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C22 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1819 | -7.9884
345612 | MV/LV Substation GL***612 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2839 | -7.9834
0124280 | MV/LV Substation MB***4280 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.83 |  | --> | 0.598 | 0 | 0.526 | 0 | 0 | Constrained, otherwise capacity available =209 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6945 | -6.9463
365260Y | MV/LV Substation LO***260Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 13.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2869 | -6.3762
037996 | MV/LV Substation CL***996 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =580 kVA | --> | 0.598 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C18 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.86 | -8.9842
075883X | MV/LV Substation RO***883X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 17.8 |  | --> | 0.19 | 0 | 0.011 | 0.179 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6038 | -6.214
069697 | MV/LV Substation RA***697 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =569 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex DONNYBROOK | Donnybrook [T41,T42] | MILLTOWN (DR) |  | 53.3249 | -6.2119
119008 | MV/LV Substation NE***008 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C16 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1818 | -8.9117
0214002 | MV/LV Substation CL***4002 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 6.78 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C36 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8913 | -8.3384
154129Z | MV/LV Substation RI***129Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =116 kVA | --> | 0.19 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =151 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3748 | -6.4016
160670X | MV/LV Substation KI***670X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex PORTARLINGTON | Portarlington [T43] | BLAKE |  | 53.1457 | -7.1314
365530X | MV/LV Substation PE***530X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3207 | -6.4721
0654024 | MV/LV Substation MI***4024 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C13 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.607 | -6.1958
007923Y | MV/LV Substation AI***923Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3222 | -6.4486
066634 | MV/LV Substation BE***634 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.4938 | -6.1515
001701 | MV/LV Substation CR***701 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.003 | 0.177 | 0 |  | --> | C11 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2454 | -6.124
050494Y | MV/LV Substation CL***494Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.3666 | -8.0265
006051Y | MV/LV Substation RI***051Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.333 | 3.12 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5024 | -6.5828
024619X | MV/LV Substation LI***619X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2131 | -8.6
059063Y | MV/LV Substation BA***063Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9293 | -7.4074
022508X | MV/LV Substation ST***508X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.258 | 4.55 |  | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =344 kW | --> | C11 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.136 | -8.6387
156021Z | MV/LV Substation DR***021Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 2.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2774 | -7.1301
062335 | MV/LV Substation BU***335 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.188 | 3.47 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E18 ex BUSH | Bush [T421,T422] | DUNDALK |  | 53.9985 | -6.1965
017154X | MV/LV Substation AB***154X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.332 | 1.98 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | E18 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5244 | -8.9315
0934048 | MV/LV Substation BA***4048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =345 kVA | --> | 0.38 | 0 | 0.002 | 0.371 | 0 |  | --> | C21 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.405 | -6.2811
154126Z | MV/LV Substation HO***126Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.19 | 0 | 0.045 | 0.144 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4349 | -6.3817
142855X | MV/LV Substation KI***855X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E23 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.3096 | -8.5993
156236X | MV/LV Substation AN***236X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1639 | -6.9311
0934307 | MV/LV Substation HU***4307 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C25 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4023 | -6.3451
1194188 | MV/LV Substation CA***4188 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 4.16 |  | --> | 0.38 | 0 | 0 | 0.221 | 0 | Constrained, otherwise capacity available =380 kW | --> | C22 ex NEWMARKET (SR) | Newmarket (sr) [T41,T42] | GLENLARA |  | 52.2134 | -9.0016
003478 | MV/LV Substation BA***478 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 11.58 |  | --> | 0.095 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0046 | -6.1125
2484178 | MV/LV Substation MI***4178 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0.145 | 0 | 0 | Constrained, otherwise capacity available =260 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3973 | -6.6579
2064051 | MV/LV Substation KI***4051 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.6 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex BELMULLET | Belmullet [T421] | BELLACORICK |  | 54.1799 | -10.0691
001392 | MV/LV Substation KI***392 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =101 kVA | --> | 0.19 | 0 | 0.02 | 0.161 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2544 | -6.1243
238900X | MV/LV Substation NU***900X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E11 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6249 | -9.2088
064993Y | MV/LV Substation GR***993Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7573 | -6.5533
081205Z | MV/LV Substation BA***205Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =567 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3246 | -6.4141
324971 | MV/LV Substation FO***971 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =116 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C20 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.5211 | -8.2716
065440Z | MV/LV Substation PA***440Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5328 | -6.097
007063 | MV/LV Substation TH***063 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =204 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C14 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3312 | -6.4589
156539Y | MV/LV Substation LI***539Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2108 | -6.9092
1564432 | MV/LV Substation CA***4432 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2332 | -6.8563
044737 | MV/LV Substation NE***737 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.079 | 2.33 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 53.9841 | -9.121
037083X | MV/LV Substation LO***083X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C11 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.9488 | -9.0687
0814290 | MV/LV Substation FO***4290 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C17 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3613 | -6.503
005506 | MV/LV Substation DU***506 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6698 | -6.2174
281984X | MV/LV Substation IL***984X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =220 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C19 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8794 | -8.4954
377642X | MV/LV Substation DU***642X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8359 | -10.261
069140 | MV/LV Substation DA***140 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.378 | 7.75 |  | --> | 0.598 | 0 | 0.077 | 0.5 | 0 |  | --> | C20 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3084 | -6.2598
281461 | MV/LV Substation HA***461 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =599 kVA | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C22 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8752 | -8.5311
244742X | MV/LV Substation SC***742X |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =943 kVA | --> | 0.95 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =938 kW | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1075 | -9.7886
081024Z | MV/LV Substation MI***024Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.008 | 0.174 | 0 |  | --> | C16 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.321 | -6.414
288194X | MV/LV Substation EG***194X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.041 | 0.04 | Constrained, otherwise capacity available =544 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2012 | -6.1276
204709 | MV/LV Substation FI***709 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E14 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.156 | -7.453
011079 | MV/LV Substation PO***079 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | C18 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6518 | -7.2542
002184 | MV/LV Substation KI***184 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.09 | 2.36 |  | --> | 0.19 | 0 | 0.02 | 0.16 | 0 |  | --> | C15 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1914 | -6.1256
162865 | MV/LV Substation AU***865 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 0.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.9313 | -7.4633
067213 | MV/LV Substation WO***213 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =224 kVA | --> | 0.38 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =335 kW | --> | C13 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6772 | -8.6532
019530 | MV/LV Substation BA***530 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.05 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C12 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2733 | -9.6144
068091X | MV/LV Substation BO***091X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.277 | 4.6 |  | --> | 0.38 | 0 | 0 | 0.363 | 0 |  | --> | C12 ex KINGSBRIDGE | Kingsbridge [T41,T42] | INCHICORE 220KV |  | 53.3434 | -6.2947
153720 | MV/LV Substation CA***720 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =205 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =330 kW | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7135 | -8.4995
266438 | MV/LV Substation JO***438 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =178 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E17 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.263 | -7.2527
016221Z | MV/LV Substation GR***221Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =588 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =941 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2966 | -6.4766
293623Y | MV/LV Substation CA***623Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9132 | -6.8336
0014051 | MV/LV Substation ST***4051 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C15 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.284 | -6.205
281526Y | MV/LV Substation HE***526Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C16 ex TOGHER | Togher [T41,T42] | TRABEG |  | 51.8749 | -8.5045
048168X | MV/LV Substation CO***168X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 2.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9177 | -7.8598
069286 | MV/LV Substation MA***286 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.47 |  | --> | 0.598 | 0 | 0.033 | 0.5 | 0 |  | --> | C13 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2933 | -6.3012
157268X | MV/LV Substation FA***268X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.302 | 1.55 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | E13 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 53.976 | -7.6455
068452X | MV/LV Substation LU***452X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.295 | 1.37 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex SOUTH KING STREET | South King Street [T41,T42] | FRANCIS STREET |  | 53.3394 | -6.261
2884098 | MV/LV Substation EA***4098 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2189 | -6.1906
0824266 | MV/LV Substation CL***4266 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 2.01 |  | --> | 0.38 | 0 | 0.142 | 0 | 0 | Constrained, otherwise capacity available =260 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.669 | -6.6896
037801X | MV/LV Substation CA***801X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C17 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8402 | -8.9828
1274095 | MV/LV Substation CL***4095 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6135 | -7.932
065146Z | MV/LV Substation HE***146Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5487 | -6.2081
059533Y | MV/LV Substation CO***533Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =269 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.931 | -7.4117
014107X | MV/LV Substation RE***107X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C19 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1685 | -6.9369
015929Z | MV/LV Substation OL***929Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C18 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.1841 | -6.6828
156264 | MV/LV Substation AV***264 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.1856 | -6.83
011722Y | MV/LV Substation KE***722Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.037 | 0.04 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C16 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5408 | -7.2731
059779Y | MV/LV Substation GR***779Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.07 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1258 | -7.4041
377448 | MV/LV Substation GU***448 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9427 | -10.2332
293921Y | MV/LV Substation ST***921Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9145 | -6.8341
151990X | MV/LV Substation GA***990X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =627 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3709 | -8.3418
0644455 | MV/LV Substation BA***4455 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0.041 | 0 | 0 | Constrained, otherwise capacity available =63 kW | --> | C22 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7347 | -6.3483
016057Z | MV/LV Substation LO***057Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =486 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C22 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3666 | -6.5128
365913X | MV/LV Substation FI***913X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C13 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2821 | -6.4103
042603X | MV/LV Substation BA***603X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8713 | -9.2638
059563Y | MV/LV Substation FA***563Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E17 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0999 | -7.4423
069053 | MV/LV Substation DU***053 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.284 | 9.99 |  | --> | 0.598 | 0 | 0.063 | 0.5 | 0 |  | --> | C19 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3146 | -6.2983
012751 | MV/LV Substation BE***751 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8183 | -6.8541
117589 | MV/LV Substation AR***589 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2551 | -8.7217
1544262 | MV/LV Substation HA***4262 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =585 kVA | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3905 | -6.4389
2654109 | MV/LV Substation DR***4109 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.56 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 53.9517 | -7.4977
099232 | MV/LV Substation WO***232 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9831 | -7.6955
015938X | MV/LV Substation HA***938X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 12.6 |  | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | C18 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.229 | -6.6979
002758 | MV/LV Substation SI***758 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.247 | 4.51 |  | --> | 0.38 | 0 | 0.002 | 0.357 | 0 |  | --> | C21 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.2021 | -6.0985
1204354 | MV/LV Substation TY***4354 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E18 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3352 | -7.0478
1444234 | MV/LV Substation CL***4234 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.78 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7536 | -7.3823
281322Z | MV/LV Substation PF***322Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 4.3 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C11 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8329 | -8.3465
2514219 | MV/LV Substation CL***4219 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =622 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C28 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3387 | -8.9356
069104 | MV/LV Substation OA***104 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.445 | 7.75 |  | --> | 0.598 | 0 | 0.118 | 0.485 | 0 |  | --> | C26 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.2924 | -6.2623
082409X | MV/LV Substation BR***409X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E17 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6394 | -6.5593
069245 | MV/LV Substation MO***245 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.458 | 7.75 |  | --> | 0.598 | 0 | 0.018 | 0.5 | 0 |  | --> | C26 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3082 | -6.2461
021168Z | MV/LV Substation GL***168Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.027 | 0.16 | 0 |  | --> | C15 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9347 | -8.3909
363115 | MV/LV Substation BR***115 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5316 | -9.6543
204383X | MV/LV Substation CO***383X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E16 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1409 | -7.4494
049120X | MV/LV Substation NE***120X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.133 | 0.13 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C12 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5882 | -7.937
043265X | MV/LV Substation FO***265X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C19 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9463 | -8.9551
3654154 | MV/LV Substation NA***4154 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =569 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C30 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.322 | -6.4093
138013X | MV/LV Substation MA***013X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.163 | 2.18 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C26 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9151 | -6.9625
0684396 | MV/LV Substation SP***4396 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3494 | -6.2354
067652Y | MV/LV Substation AN***652Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.379 | 6.81 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C03 ex AHANE | Ahane [T102] | AHANE |  | 52.6684 | -8.5287
082101Y | MV/LV Substation GR***101Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7497 | -6.5516
266812 | MV/LV Substation KI***812 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | E12 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3315 | -7.2894
1374069 | MV/LV Substation BA***4069 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 3.74 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex KILFLYNN | Kilflynn [T41,T42] | TRALEE |  | 52.3779 | -9.6165
142374 | MV/LV Substation RA***374 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =79 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C16 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.3021 | -8.764
180770X | MV/LV Substation HE***770X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7364 | -6.8573
050439Y | MV/LV Substation CR***439Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.364 | 7.61 |  | --> | 0.598 | 0 | 0.075 | 0 | 0 | Constrained, otherwise capacity available =506 kW | --> | C11 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4175 | -7.9084
021332 | MV/LV Substation BO***332 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0.005 | 0.371 | 0 |  | --> | C11 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9123 | -8.4207
093297Z | MV/LV Substation GE***297Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =349 kVA | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C20 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.4025 | -6.2636
012497 | MV/LV Substation BA***497 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.7721 | -6.9026
036947X | MV/LV Substation GL***947X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.374 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | E17 ex KILROSS ROAD | Kilross Road [T421] | TIPPERARY |  | 52.4643 | -8.356
005035 | MV/LV Substation GO***035 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C14 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6758 | -6.2861
021827 | MV/LV Substation DR***827 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =76 kW | --> | E16 ex CURRALEIGH | Curraleigh [T421,T422] | KILBARRY |  | 51.913 | -8.7089
075186Y | MV/LV Substation CL***186Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5412 | -6.3823
007568 | MV/LV Substation RA***568 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.24 | -6.5888
081285X | MV/LV Substation GL***285X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C11 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3592 | -6.3615
365524X | MV/LV Substation KI***524X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =438 kVA | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C17 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.329 | -6.427
021202Z | MV/LV Substation OS***202Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9029 | -8.5176
216400 | MV/LV Substation DR***400 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7577 | -8.4179
006027 | MV/LV Substation PE***027 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.124 | 3.12 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.4993 | -6.5727
256169X | MV/LV Substation RI***169X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.338 | 1.28 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C18 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7685 | -8.4952
0744063 | MV/LV Substation KI***4063 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 54.011 | -8.0001
276718 | MV/LV Substation LI***718 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0541 | -9.4664
017594X | MV/LV Substation FI***594X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.527 | -8.9102
1544097 | MV/LV Substation LE***4097 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.005 | 0.36 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4249 | -6.3852
006121 | MV/LV Substation TO***121 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 1.29 |  | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | C13 ex MONFIN | Monfin [T41,T42] | WEXFORD |  | 52.481 | -6.5873
069547 | MV/LV Substation BA***547 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.362 | 7.75 |  | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C16 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3125 | -6.2552
1964098 | MV/LV Substation ST***4098 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.076 | 0.33 |  | --> | 0.095 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E31 ex TRIM | Trim [T421] | NAVAN |  | 53.5742 | -6.9053
288157 | MV/LV Substation AR***157 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.041 | 0.04 | Constrained, otherwise capacity available =133 kVA | --> | 0.19 | 0 | 0.006 | 0.176 | 0 |  | --> | C14 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2025 | -6.1292
066463Z | MV/LV Substation KE***463Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =175 kVA | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =330 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4417 | -6.1964
350006 | MV/LV Substation DA***006 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4736 | -8.2884
039311 | MV/LV Substation TI***311 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =445 kVA | --> | 0.598 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =539 kW | --> | C18 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2896 | -9.0468
0994060 | MV/LV Substation GO***4060 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 5.45 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C13 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9668 | -7.7204
025682X | MV/LV Substation BA***682X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3089 | -8.6769
1564091 | MV/LV Substation CO***4091 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2217 | -6.9185
095039 | MV/LV Substation KI***039 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.432 | 0.7 |  | --> | 0.95 | 0 | 0.11 | 0 | 0 | Constrained, otherwise capacity available =788 kW | --> | C15 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6445 | -9.4805
154417Z | MV/LV Substation TY***417Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =534 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4194 | -6.3825
026481X | MV/LV Substation BA***481X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.19 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C16 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7044 | -8.528
066513Z | MV/LV Substation CO***513Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.063 | 0 | 0 | Constrained, otherwise capacity available =317 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5102 | -6.5312
1394367 | MV/LV Substation BA***4367 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8229 | -7.2576
0814240 | MV/LV Substation AI***4240 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | E17 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3432 | -6.4675
069076 | MV/LV Substation GA***076 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.256 | 0.87 |  | --> | 0.598 | 0 | 0.08 | 0.486 | 0 |  | --> | C14 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3158 | -6.2782
071062 | MV/LV Substation BE***062 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.286 | 5.58 |  | --> | 0.38 | 0 | 0.039 | 0.335 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1055 | -6.062
019098X | MV/LV Substation LI***098X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =310 kVA | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C14 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2875 | -9.6983
035739X | MV/LV Substation RO***739X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.308 | 6.17 |  | --> | 0.38 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C17 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.381 | -7.9131
014180Z | MV/LV Substation GT***180Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.63 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | E11 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1088 | -6.7413
081280Z | MV/LV Substation KN***280Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =370 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3505 | -6.3511
139228Z | MV/LV Substation BO***228Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex OLDCASTLE | Oldcastle [T41,T422] | MULLINGAR |  | 53.7632 | -7.1249
002031X | MV/LV Substation AV***031X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.36 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C16 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.173 | -6.1453
116269 | MV/LV Substation DE***269 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 7.32 |  | --> | 0.095 | 0 | 0.005 | 0.09 | 0 |  | --> | C14 ex CARROWBEG | Carrowbeg [T41,T42] | CARROWBEG |  | 53.8082 | -9.5277
015005 | MV/LV Substation PA***005 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =20 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2478 | -6.6213
054258Y | MV/LV Substation TH***258Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =125 kVA | --> | 0.19 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =151 kW | --> | C15 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0421 | -7.2871
062182 | MV/LV Substation BE***182 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.063 | 3.12 |  | --> | 0.095 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =72 kW | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9622 | -6.3693
022094 | MV/LV Substation AB***094 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1191 | -8.5707
0034052 | MV/LV Substation CU***4052 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9269 | -6.0526
068244X | MV/LV Substation GO***244X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.61 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex SHERIFF STREET | Sheriff Street [T41,T42] | FRANCIS STREET |  | 53.3478 | -6.2424
293431 | MV/LV Substation GR***431 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.02 | 0.43 |  | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =73 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8366 | -6.7824
0734182 | MV/LV Substation MO***4182 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C16 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.4395 | -7.6996
0504441 | MV/LV Substation FA***4441 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 6.49 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C22 ex BUSHFIELD | Bushfield [T41,T42] | ATHLONE |  | 53.4694 | -7.9054
0694002 | MV/LV Substation WA***4002 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.465 | 0.98 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3321 | -6.2452
019032 | MV/LV Substation MA***032 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =222 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C20 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2679 | -9.6883
002136 | MV/LV Substation FA***136 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.351 | 2.36 |  | --> | 0.38 | 0 | 0.063 | 0.327 | 0 |  | --> | C15 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1932 | -6.1247
001598 | MV/LV Substation TR***598 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.234 | 1.55 |  | --> | 0.38 | 0 | 0.013 | 0.347 | 0 |  | --> | C16 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2973 | -6.1598
142005 | MV/LV Substation RO***005 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.2637 | -8.7586
156646 | MV/LV Substation KI***646 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E16 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.2731 | -6.8728
066668Z | MV/LV Substation DR***668Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =105 kVA | --> | 0.19 | 0 | 0.034 | 0 | 0 | Constrained, otherwise capacity available =151 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.417 | -6.1547
069889 | MV/LV Substation DA***889 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.98 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex LEESON STREET | Leeson Street [T41,T42] | MILLTOWN (DR) |  | 53.3305 | -6.2588
021102Z | MV/LV Substation WH***102Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.005 | 0.041 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9364 | -8.4537
046456 | MV/LV Substation TH***456 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.131 | 5.48 |  | --> | 0.19 | 0 | 0.047 | 0.146 | 0 |  | --> | C17 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.3059 | -8.5563
054906Y | MV/LV Substation VO***906Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E13 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9091 | -7.3244
0494227 | MV/LV Substation CL***4227 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7131 | -7.828
117224Y | MV/LV Substation GR***224Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0 | 0.365 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2524 | -8.3228
052108Z | MV/LV Substation ST***108Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =127 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | E14 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.4176 | -7.2939
081074X | MV/LV Substation AN***074X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =270 kVA | --> | 0.38 | 0 | 0 | 0.362 | 0 |  | --> | C19 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3469 | -6.3506
062532 | MV/LV Substation BE***532 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 4.25 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E12 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0131 | -6.3399
028046Y | MV/LV Substation FO***046Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =162 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C18 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.8986 | -8.3015
001619 | MV/LV Substation EL***619 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =418 kVA | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C14 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2562 | -6.133
237196X | MV/LV Substation WO***196X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C16 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.8316 | -6.3896
243881 | MV/LV Substation IN***881 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =69 kVA | --> | 0.095 | 0 | 0.063 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E16 ex INCH | Inch [T421,T422] | OUGHTRAGH |  | 52.1444 | -9.9821
249533 | MV/LV Substation CU***533 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C25 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.208 | -7.7521
052582Z | MV/LV Substation CL***582Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.25 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C16 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.664 | -7.2787
067224 | MV/LV Substation CE***224 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.38 | 0 | 0 | 0.343 | 0 |  | --> | C20 ex ROCHES STREET | Roches Street [T41,T42] | LIMERICK |  | 52.6624 | -8.6294
149301X | MV/LV Substation QU***301X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.5979 | -8.0907
1824241 | MV/LV Substation CA***4241 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =609 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C17 ex TULLA | Tulla [T41,T42] | ENNIS |  | 52.8685 | -8.7646
210366 | MV/LV Substation SH***366 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C21 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9633 | -6.7109
064282Y | MV/LV Substation SI***282Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C13 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7358 | -6.3638
176851X | MV/LV Substation CL***851X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 18.78 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9103 | -9.1249
039241X | MV/LV Substation AR***241X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.333 | 3.45 |  | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C20 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2639 | -9.0708
366603 | MV/LV Substation GA***603 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =568 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2596 | -9.6041
0504195 | MV/LV Substation BU***4195 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex BUSHFIELD |  |  |  | 53.429 | -7.9026
167543 | MV/LV Substation CA***543 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =69 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E21 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9844 | -8.4691
081658Z | MV/LV Substation AD***658Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.01 | 0.363 | 0 |  | --> | E19 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3361 | -6.4632
069484 | MV/LV Substation HE***484 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.078 | 0.304 | 0 |  | --> | C11 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2832 | -6.2759
049606Y | MV/LV Substation DE***606Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5906 | -7.8602
1544195 | MV/LV Substation CL***4195 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =489 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =579 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3823 | -6.3992
021128 | MV/LV Substation CH***128 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =69 kVA | --> | 0.19 | 0 | 0.016 | 0.159 | 0 |  | --> | C24 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9096 | -8.4937
017422X | MV/LV Substation SH***422X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 1.98 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E11 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.6146 | -8.8854
233327X | MV/LV Substation RI***327X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C21 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.1996 | -9.5688
067193 | MV/LV Substation SA***193 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =308 kVA | --> | 0.38 | 0 | 0 | 0.367 | 0 |  | --> | C18 ex BALLINACURRA | Ballinacurra [T41,T42] | LIMERICK |  | 52.6546 | -8.6284
081294Z | MV/LV Substation CO***294Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C15 ex CASTLEKNOCK | Castleknock [T41,T42] | FINGLAS |  | 53.3691 | -6.373
032440X | MV/LV Substation GR***440X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =27 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1495 | -7.0337
068649 | MV/LV Substation GR***649 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.034 | 0.34 | 0 |  | --> | C14 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3773 | -6.2297
011663 | MV/LV Substation SP***663 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6309 | -7.2476
196014 | MV/LV Substation DU***014 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =161 kW | --> | C18 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5515 | -6.7846
192007X | MV/LV Substation ME***007X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.7 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex GWEEDORE | Gweedore [T421] | ARDNAGAPPARY |  | 55.1373 | -8.2233
255447 | MV/LV Substation I ***447 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E12 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6334 | -8.3509
023541X | MV/LV Substation CR***541X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1423 | -8.3354
276963 | MV/LV Substation SH***963 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C12 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0473 | -9.3399
1534137 | MV/LV Substation BA***4137 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E17 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8685 | -8.379
050392Y | MV/LV Substation SL***392Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.38 | 0 | 0.048 | 0 | 0 | Constrained, otherwise capacity available =320 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4259 | -7.9879
014867 | MV/LV Substation BU***867 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =157 kW | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1855 | -6.7854
009411Y | MV/LV Substation IE***411Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.158 | 13.6 |  | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C27 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2452 | -7.1591
067148Y | MV/LV Substation ES***148Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E16 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.7276 | -8.7059
011211 | MV/LV Substation TR***211 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | E25 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6811 | -7.2799
068690X | MV/LV Substation MA***690X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.99 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3338 | -6.2602
0734144 | MV/LV Substation BA***4144 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C15 ex MOATE | Moate [T41,T42] | ATHLONE |  | 53.3949 | -7.7349
139096Y | MV/LV Substation MU***096Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E16 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8645 | -7.5555
276972 | MV/LV Substation CO***972 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.76 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | C12 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0677 | -9.4291
029429 | MV/LV Substation CO***429 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =260 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C18 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.908 | -8.2877
039216X | MV/LV Substation FO***216X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 11.03 |  | --> | 0.38 | 0 | 0.01 | 0.36 | 0 |  | --> | C24 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2712 | -9.0839
068097 | MV/LV Substation RI***097 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =586 kVA | --> | 0.95 | 0 | 0.012 | 0.5 | 0 |  | --> | C14 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3508 | -6.2749
082744Y | MV/LV Substation NA***744Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.496 | 2.01 |  | --> | 0.598 | 0 | 0.086 | 0 | 0 | Constrained, otherwise capacity available =518 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6656 | -6.6959
099156X | MV/LV Substation GO***156X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.385 | 2.96 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C15 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9521 | -7.7327
0014094 | MV/LV Substation RO***4094 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 13.42 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C17 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2749 | -6.1463
0994055 | MV/LV Substation MO***4055 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =271 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9781 | -7.8929
003423X | MV/LV Substation BE***423X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 18.08 |  | --> | 0.095 | 0 | 0.005 | 0.09 | 0 |  | --> | C18 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8812 | -6.0802
160401Y | MV/LV Substation GR***401Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1371 | -7.3725
0744166 | MV/LV Substation DR***4166 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0506 | -8.0402
095289 | MV/LV Substation CR***289 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 0.7 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C20 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.7472 | -9.4306
192573 | MV/LV Substation RA***573 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.172 | 1.56 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0182 | -8.3307
066082 | MV/LV Substation SC***082 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =226 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | C17 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4642 | -6.2177
067111 | MV/LV Substation GA***111 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =205 kVA | --> | 0.38 | 0 | 0.024 | 0.335 | 0 |  | --> | C14 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6604 | -8.6097
154435Z | MV/LV Substation CH***435Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3964 | -6.4385
014942Z | MV/LV Substation AC***942Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =596 kVA | --> | 0.598 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2156 | -6.9977
266121X | MV/LV Substation AB***121X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =75 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E18 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2402 | -7.2655
1564092 | MV/LV Substation MU***4092 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C15 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2071 | -6.8676
0074284 | MV/LV Substation PL***4284 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2315 | -6.5514
2884199 | MV/LV Substation NU***4199 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2521 | -6.2146
377696X | MV/LV Substation HO***696X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8251 | -10.276
082172 | MV/LV Substation ED***172 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5941 | -6.4959
017676 | MV/LV Substation PA***676 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 1.98 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E12 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4342 | -8.9333
235405 | MV/LV Substation CU***405 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E22 ex BEALNABLATH | Bealnablath [T421] | BANDON |  | 51.8204 | -8.889
0684653 | MV/LV Substation EN***4653 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0.024 | 0.5 | 0 |  | --> | C41 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.352 | -6.2308
0124067 | MV/LV Substation DI***4067 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.399 | 1.99 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C11 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8356 | -6.9303
120635Y | MV/LV Substation WA***635Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.277 | -6.8531
130208X | MV/LV Substation KE***208X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7298 | -7.694
365515X | MV/LV Substation CL***515X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C14 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3223 | -6.3555
014053Z | MV/LV Substation RA***053Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =106 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.2218 | -6.9932
365840X | MV/LV Substation BA***840X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =226 kVA | --> | 0.598 | 0 | 0.138 | 0.439 | 0 |  | --> | C22 ex FORTUNESTOWN | Fortunestown [T101,T102] | INCHICORE 220KV |  | 53.2959 | -6.4414
252057 | MV/LV Substation BA***057 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.069 | 2.76 |  | --> | 0.095 | 0 | 0 | 0.091 | 0 |  | --> | C19 ex RECESS | Recess [T41] | SCREEB |  | 53.4668 | -9.8702
052008X | MV/LV Substation LI***008X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.193 | 1.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C17 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.7159 | -7.318
433232 | MV/LV Substation BR***232 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9215 | -8.6362
033548Y | MV/LV Substation KN***548Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =31 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C12 ex GRANAGH | Granagh [T41,T42] | WATERFORD |  | 52.3613 | -7.2882
062554Y | MV/LV Substation ME***554Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.13 | 3.12 |  | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =151 kW | --> | C12 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9953 | -6.3809
281524Z | MV/LV Substation JO***524Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.32 | 5.49 |  | --> | 0.38 | 0 | 0 | 0.369 | 0 |  | --> | C11 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.882 | -8.4451
127139Y | MV/LV Substation CL***139Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6015 | -7.9595
288199 | MV/LV Substation ES***199 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.19 | 0 | 0.04 | 0.146 | 0 |  | --> | C18 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2727 | -6.2105
067219Z | MV/LV Substation KY***219Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =333 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C21 ex CASTLETROY | Castletroy [T41,T42] | ARDNACRUSHA |  | 52.653 | -8.5572
036443 | MV/LV Substation DU***443 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E20 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5558 | -8.0395
063034 | MV/LV Substation GO***034 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C19 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.8552 | -6.5487
0654025 | MV/LV Substation MI***4025 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =539 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6076 | -6.1973
014235Z | MV/LV Substation TH***235Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.0905 | -6.8069
004142Y | MV/LV Substation AR***142Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.133 | 18.08 |  | --> | 0.19 | 0 | 0 | 0.181 | 0 |  | --> | C19 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8094 | -6.1351
081606Z | MV/LV Substation RO***606Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C15 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3307 | -6.5939
0374060 | MV/LV Substation CA***4060 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.394 | 13.05 |  | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C12 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8498 | -8.9707
2534065 | MV/LV Substation FL***4065 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6609 | -8.6983
127521Y | MV/LV Substation CO***521Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6531 | -7.7324
011292 | MV/LV Substation BA***292 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E25 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.7028 | -7.3422
160740 | MV/LV Substation GL***740 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1547 | -7.2212
066817X | MV/LV Substation RA***817X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex SWORDS | Swords [T41,T42] | GLASMORE |  | 53.4462 | -6.2597
062878 | MV/LV Substation PR***878 |  | 20 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.025 | 19.76 |  | --> | 0.031 | 0 | 0.005 | 0.026 | 0 |  | --> | E19 ex MULLAGHARLIN | Mullagharlin [T121,T122] | MULLAGHARLIN |  | 53.9682 | -6.4524
020101 | MV/LV Substation RO***101 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0.13 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C17 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.1023 | -9.5193
207061 | MV/LV Substation KI***061 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.055 | 2.9 |  | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =74 kW | --> | C18 ex GLENGOOLE | Glengoole [T42] | THURLES |  | 52.5687 | -7.6768
046956 | MV/LV Substation WO***956 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 5.78 |  | --> | 0.048 | 0 | 0.005 | 0.041 | 0 |  | --> | C20 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2716 | -8.5173
288269X | MV/LV Substation GO***269X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2806 | -6.2418
345779 | MV/LV Substation SK***779 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.004 | 0.043 | 0 |  | --> | E18 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.3094 | -8.1737
117637X | MV/LV Substation KI***637X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E22 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2018 | -8.4363
138015 | MV/LV Substation KI***015 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.125 | 2.18 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C26 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.9175 | -6.967
048913 | MV/LV Substation MO***913 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.18 | 2.03 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E17 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9169 | -7.8626
035031Y | MV/LV Substation 0R***031Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.181 | 6.17 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C20 ex CAHIR | Cahir [T41,T42] | CAHIR |  | 52.3576 | -7.9927
152451 | MV/LV Substation GL***451 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =97 kVA | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E31 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6331 | -8.2939
068480X | MV/LV Substation RA***480X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.91 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3781 | -6.3274
077212X | MV/LV Substation PU***212X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E25 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.6507 | -8.8676
136009Y | MV/LV Substation BA***009Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.7005 | -8.2079
0684408 | MV/LV Substation HO***4408 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3451 | -6.2343
164509X | MV/LV Substation MA***509X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5472 | -9.269
0234125 | MV/LV Substation BA***4125 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1479 | -8.3961
210003 | MV/LV Substation BR***003 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =255 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C18 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9772 | -6.7208
009234 | MV/LV Substation CL***234 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.024 | 8.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2867 | -7.1206
068123X | MV/LV Substation WE***123X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =259 kVA | --> | 0.38 | 0 | 0 | 0.36 | 0 |  | --> | C14 ex NEWMARKET (DR) | Newmarket (dr) [T41] | FRANCIS STREET |  | 53.3372 | -6.283
062251X | MV/LV Substation MO***251X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0392 | -6.3724
008758X | MV/LV Substation BA***758X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.277 | -6.8345
062660X | MV/LV Substation NE***660X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.067 | 1.03 |  | --> | 0.095 | 0 | 0.051 | 0 | 0 | Constrained, otherwise capacity available =53 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9211 | -6.467
053591Y | MV/LV Substation LY***591Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.006 | 0.087 | 0 |  | --> | E18 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2513 | -7.5456
008876 | MV/LV Substation AD***876 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =337 kW | --> | E11 ex CLONROCHE | Clonroche [T421,T422] | WEXFORD |  | 52.3919 | -6.7198
082543 | MV/LV Substation CO***543 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6091 | -6.6174
095791X | MV/LV Substation PA***791X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.195 | 1.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C25 ex KILKEE | Kilkee [T41] | TULLABRACK |  | 52.6758 | -9.653
0684048 | MV/LV Substation ST***4048 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.409 | 11.14 |  | --> | 0.598 | 0 | 0.019 | 0.5 | 0 |  | --> | C11 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.3642 | -6.302
366201 | MV/LV Substation EL***201 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.446 | 0.45 | Constrained, otherwise capacity available =518 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.2902 | -9.5508
1394032 | MV/LV Substation VI***4032 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex VIRGINIA | Virginia [T41,T42] | MEATH HILL |  | 53.8381 | -7.0884
066637 | MV/LV Substation PL***637 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =383 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4713 | -6.2091
069219 | MV/LV Substation MC***219 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C34 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3297 | -6.3402
093283X | MV/LV Substation BU***283X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0.009 | 0.177 | 0 |  | --> | C11 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3917 | -6.0996
081147Z | MV/LV Substation PA***147Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =301 kVA | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3296 | -6.3766
018219Z | MV/LV Substation IS***219Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.186 | 3.75 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C12 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4458 | -9.5091
013115Z | MV/LV Substation AR***115Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 0.12 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E62 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0545 | -6.9177
206554 | MV/LV Substation CL***554 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.76 |  | --> | 0.048 | 0 | 0.015 | 0.035 | 0 |  | --> | E14 ex BANGOR ERRIS | Bangor Erris [T421] | BELLACORICK |  | 54.1591 | -9.758
281757Z | MV/LV Substation BA***757Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 17.47 |  | --> | 0.95 | 0 | 0.004 | 0.5 | 0 |  | --> | E18 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8886 | -8.5888
019328X | MV/LV Substation GA***328X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.132 | 1.54 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C17 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2586 | -9.6895
011492X | MV/LV Substation AR***492X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 2.8 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.6408 | -7.2301
006687 | MV/LV Substation WH***687 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.5713 | -6.7194
365117X | MV/LV Substation MA***117X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C22 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3301 | -6.3583
037706X | MV/LV Substation WE***706X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =213 kVA | --> | 0.38 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =330 kW | --> | C20 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8306 | -8.9968
012265Y | MV/LV Substation RE***265Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.99 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C18 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.846 | -6.9443
2764027 | MV/LV Substation MI***4027 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.76 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C13 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0417 | -9.4429
0524789 | MV/LV Substation ST***4789 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 10.9 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5411 | -7.354
015173Z | MV/LV Substation CA***173Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 12.6 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2361 | -6.7314
054148 | MV/LV Substation BA***148 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =25 kVA | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =78 kW | --> | E12 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9486 | -7.3036
281053Y | MV/LV Substation CH***053Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | C17 ex CARRIGALINE | Carrigaline [T41,T42] | BARNAHELY |  | 51.7979 | -8.2897
196255X | MV/LV Substation LI***255X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C18 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5621 | -6.7913
139937Y | MV/LV Substation WO***937Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4 |  | --> | 0.598 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8634 | -7.1953
417171X | MV/LV Substation DE***171X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 8.5 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0842 | -8.1089
255457 | MV/LV Substation RO***457 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.09 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6921 | -8.7465
253724 | MV/LV Substation KI***724 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E16 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.5512 | -8.5647
081388Z | MV/LV Substation CH***388Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3372 | -6.3732
004684 | MV/LV Substation HY***684 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =191 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C23 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7338 | -6.2111
253004 | MV/LV Substation WE***004 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5128 | -8.8593
067165 | MV/LV Substation MA***165 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0.007 | 0.173 | 0 |  | --> | C20 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6456 | -8.6145
111912X | MV/LV Substation LA***912X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6948 | -9.4363
016170Z | MV/LV Substation GR***170Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =568 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2987 | -6.476
160131Z | MV/LV Substation EM***131Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0989 | -7.2105
039189 | MV/LV Substation WI***189 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 11.03 |  | --> | 0.38 | 0 | 0.026 | 0.35 | 0 |  | --> | C26 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2662 | -9.1092
251638 | MV/LV Substation CA***638 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =67 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C30 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3953 | -9.0074
049842Y | MV/LV Substation RE***842Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.023 | 1.31 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7975 | -8.0617
003492Y | MV/LV Substation WI***492Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 11.58 |  | --> | 0.38 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =342 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9872 | -6.0797
050612Y | MV/LV Substation CR***612Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C23 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4485 | -7.9327
090842 | MV/LV Substation DR***842 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 3.16 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C20 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7413 | -8.8814
001471 | MV/LV Substation AR***471 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.243 | 1.16 |  | --> | 0.38 | 0 | 0.045 | 0.325 | 0 |  | --> | C14 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.284 | -6.1819
012519X | MV/LV Substation M ***519X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 2.83 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E17 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7346 | -6.9897
021514Z | MV/LV Substation DI***514Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.188 | 6.78 |  | --> | 0.38 | 0 | 0 | 0.35 | 0 |  | --> | C16 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9055 | -8.3575
0014078 | MV/LV Substation MA***4078 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.23 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2794 | -6.1435
276186 | MV/LV Substation DR***186 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 0.76 |  | --> | 0.38 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C18 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0544 | -9.5026
154225Z | MV/LV Substation SO***225Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3858 | -6.4095
039916X | MV/LV Substation LE***916X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.492 | 11.03 |  | --> | 0.598 | 0 | 0.009 | 0.5 | 0 |  | --> | C18 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2665 | -9.1213
018206Z | MV/LV Substation GA***206Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.457 | 3.75 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =574 kW | --> | C11 ex SMEARLA | Smearla [T41,T42] | TRIEN |  | 52.4478 | -9.4903
0154207 | MV/LV Substation SI***4207 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 12.6 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C20 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2407 | -6.646
0384167 | MV/LV Substation GA***4167 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C18 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0612 | -8.823
031560 | MV/LV Substation AU***560 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.967 | -7.7127
154081Y | MV/LV Substation WO***081Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4464 | -6.4829
066545Z | MV/LV Substation HO***545Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =310 kVA | --> | 0.38 | 0 | 0.008 | 0.362 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4461 | -6.2095
0684345 | MV/LV Substation GA***4345 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =587 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CAMDEN ROW | Camden Row [T41] | FRANCIS STREET |  | 53.3411 | -6.276
429085X | MV/LV Substation FI***085X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex ABBEYFEALE | Abbeyfeale [T42] | TRIEN |  | 52.3797 | -9.2842
068542X | MV/LV Substation DA***542X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 28.43 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C39 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3389 | -6.2519
064642 | MV/LV Substation BE***642 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E18 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6897 | -6.3468
433003 | MV/LV Substation HO***003 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C16 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.9054 | -8.5906
0824261 | MV/LV Substation RA***4261 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =167 kVA | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =148 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5866 | -6.6036
089014X | MV/LV Substation KN***014X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.294 | 9.1 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | E19 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1188 | -9.1339
062906X | MV/LV Substation GI***906X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 19.76 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E19 ex MULLAGHARLIN | Mullagharlin [T121,T122] | MULLAGHARLIN |  | 53.9732 | -6.4201
014140Z | MV/LV Substation MA***140Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 0.63 |  | --> | 0.048 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C16 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1039 | -6.8558
031062Y | MV/LV Substation BA***062Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0971 | -7.6509
251544 | MV/LV Substation LA***544 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C28 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.342 | -8.9426
012807X | MV/LV Substation OL***807X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C19 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8312 | -6.9221
253618X | MV/LV Substation HE***618X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =113 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C18 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4711 | -9.1077
153818 | MV/LV Substation MC***818 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =314 kVA | --> | 0.38 | 0 | 0.081 | 0 | 0 | Constrained, otherwise capacity available =308 kW | --> | E17 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.817 | -8.4373
150256X | MV/LV Substation LA***256X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.121 | 3.96 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | E20 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7916 | -7.7777
281208Y | MV/LV Substation DO***208Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =92 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C21 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.748 | -8.3158
068537X | MV/LV Substation PA***537X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =625 kVA | --> | 0.598 | 0 | 0.038 | 0.5 | 0 |  | --> | C11 ex CLONTARF | Clontarf [T42] | FINGLAS |  | 53.3727 | -6.2149
151444 | MV/LV Substation GR***444 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E17 ex BRUFF | Bruff [T42,T421] | LIMERICK |  | 52.514 | -8.62
069639 | MV/LV Substation RA***639 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.238 | 0.91 |  | --> | 0.38 | 0 | 0 | 0.357 | 0 |  | --> | C21 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.2992 | -6.2866
093364Z | MV/LV Substation BE***364Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =257 kW | --> | C20 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.4122 | -6.2184
160674Y | MV/LV Substation TU***674Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C15 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1237 | -7.3329
022983 | MV/LV Substation OL***983 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 4.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1478 | -8.617
127281 | MV/LV Substation GA***281 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6828 | -7.7197
042731 | MV/LV Substation PH***731 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C14 ex KNOCKAPHUNTA | Knockaphunta [T41,T42] | CASTLEBAR |  | 53.8297 | -9.3456
377278 | MV/LV Substation VA***278 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9131 | -10.294
068704X | MV/LV Substation CL***704X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3502 | -6.238
1424023 | MV/LV Substation AT***4023 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex ATHENRY |  |  |  | 53.2923 | -8.7489
067096 | MV/LV Substation UN***096 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.4 | 6.81 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C05 ex AHANE | Ahane [T102] | AHANE |  | 52.6646 | -8.5023
0604211 | MV/LV Substation DR***4211 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.1286 | -7.1597
053786Y | MV/LV Substation CH***786Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =476 kVA | --> | 0.598 | 0 | 0.009 | 0.5 | 0 |  | --> | C23 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2654 | -7.4698
027836X | MV/LV Substation KI***836X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 7.79 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7093 | -9.1464
064109 | MV/LV Substation FI***109 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C16 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7104 | -6.3681
067564Y | MV/LV Substation RA***564Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =125 kVA | --> | 0.19 | 0 | 0 | 0.18 | 0 |  | --> | C16 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6154 | -8.663
204005 | MV/LV Substation WE***005 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =54 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =81 kW | --> | E16 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1401 | -7.454
1094049 | MV/LV Substation FA***4049 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =492 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex SHANNON | Shannon [T41,T42] | DRUMLINE |  | 52.7034 | -8.8973
067553Y | MV/LV Substation CR***553Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =900 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =936 kW | --> | C20 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6402 | -8.6454
0154211 | MV/LV Substation WO***4211 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1232 | -6.5563
081060 | MV/LV Substation CH***060 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =421 kVA | --> | 0.598 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =525 kW | --> | C13 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3429 | -6.3765
276971 | MV/LV Substation CO***971 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.76 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C12 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0683 | -9.4305
046364 | MV/LV Substation C ***364 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 4.13 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | C18 ex AGHAGAD | Aghagad [T41,T42] | SLIGO |  | 54.3596 | -8.541
049529Y | MV/LV Substation CO***529Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 0.21 |  | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =26 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8969 | -7.6548
365122X | MV/LV Substation RO***122X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3286 | -6.3437
154375 | MV/LV Substation CO***375 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =427 kVA | --> | 0.95 | 0 | 0.19 | 0 | 0 | Constrained, otherwise capacity available =728 kW | --> | C12 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.384 | -6.3998
031543 | MV/LV Substation CU***543 |  | 20 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained, otherwise capacity available =13 kVA | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =26 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9867 | -7.7472
156827Y | MV/LV Substation CR***827Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.2151 | -7.0998
161720X | MV/LV Substation OT***720X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex SPIDDAL |  |  |  | 53.2533 | -9.3626
119316Y | MV/LV Substation CO***316Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1989 | -8.867
0174365 | MV/LV Substation TA***4365 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.05 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C19 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.3759 | -9.0542
258595 | MV/LV Substation CR***595 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.06 | 1.86 |  | --> | 0.095 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =66 kW | --> | E18 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.1221 | -7.9085
0034078 | MV/LV Substation KI***4078 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9466 | -6.0357
204746 | MV/LV Substation TI***746 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.02 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.0652 | -7.4261
011949 | MV/LV Substation MA***949 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 0.04 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5262 | -7.3532
281479Z | MV/LV Substation CO***479Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.67 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex CENTRE PARK ROAD | Marina [T105,T106] | MARINA |  | 51.8947 | -8.4657
014115Z | MV/LV Substation CO***115Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =243 kVA | --> | 0.38 | 0 | 0.059 | 0 | 0 | Constrained, otherwise capacity available =314 kW | --> | C12 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1868 | -6.8024
0504235 | MV/LV Substation ID***4235 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.013 | 7.61 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =324 kW | --> | C17 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4195 | -7.8955
065435Z | MV/LV Substation HA***435Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =298 kVA | --> | 0.38 | 0 | 0.071 | 0.313 | 0 |  | --> | C26 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6075 | -6.2014
058077 | MV/LV Substation ST***077 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.4 | 3 |  | --> | 0.598 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =554 kW | --> | C20 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8608 | -8.1997
260695X | MV/LV Substation NE***695X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.498 | 1.67 |  | --> | 0.598 | 0 | 0.048 | 0.5 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8863 | -9.5468
0684745 | MV/LV Substation DO***4745 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =455 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex GRANBY ROW | Granby Row [T41] | MCDERMOTT |  | 53.3536 | -6.2678
054517Y | MV/LV Substation DR***517Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0.041 | 0 | 0 | Constrained, otherwise capacity available =154 kW | --> | C12 ex PALLAS | Pallas [T41,T42] | PORTLAOISE |  | 53.0343 | -7.3164
026454Y | MV/LV Substation CO***454Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 8.66 |  | --> | 0.048 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | C14 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7611 | -8.672
052920X | MV/LV Substation KI***920X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5075 | -7.1437
007029 | MV/LV Substation OP***029 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =904 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =937 kW | --> | C19 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3377 | -6.4622
069773 | MV/LV Substation BR***773 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 7.75 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MILLTOWN (DR) | Milltown (dr) [T101,T102] | INCHICORE 220KV |  | 53.3139 | -6.261
012491Y | MV/LV Substation PR***491Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =384 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C19 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8377 | -6.9137
153270X | MV/LV Substation CN***270X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =129 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E17 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8143 | -8.4355
1544094 | MV/LV Substation HO***4094 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =236 kVA | --> | 0.38 | 0 | 0.301 | 0.134 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4241 | -6.3756
156126Z | MV/LV Substation TU***126Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1832 | -6.9425
068640X | MV/LV Substation BE***640X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 28.43 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex BEDFORD ROW | Bedford Row [T41,T42,T43,T44] | FRANCIS STREET |  | 53.3461 | -6.2612
013721Y | MV/LV Substation AD***721Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.029 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9924 | -6.9978
127236Z | MV/LV Substation SE***236Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =129 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C18 ex HOLYCROSS ROAD | Holycross Road [T41,T42] | THURLES |  | 52.6828 | -7.8247
0014024 | MV/LV Substation RO***4024 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.23 |  | --> | 0.598 | 0 | 0.081 | 0.5 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2827 | -6.1449
184116 | MV/LV Substation HO***116 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.184 | 3.38 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C18 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1198 | -6.7317
033727X | MV/LV Substation WH***727X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C18 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3732 | -7.3805
0664263 | MV/LV Substation DI***4263 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4795 | -6.1406
039262 | MV/LV Substation CA***262 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.3033 | -8.9289
142730X | MV/LV Substation CN***730X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.19 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C16 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.3088 | -8.7508
0564206 | MV/LV Substation WO***4206 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.364 | 0.89 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C19 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1036 | -7.9121
084886 | MV/LV Substation NE***886 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E11 ex KILCOLGAN | Kilcolgan [T42,T421] | GALWAY 110KV |  | 53.2017 | -8.8782
152723X | MV/LV Substation GL***723X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =179 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.65 | -8.3965
010681 | MV/LV Substation NO***681 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5176 | -7.1327
066516X | MV/LV Substation LA***516X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =303 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5124 | -6.531
053384 | MV/LV Substation AR***384 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.252 | 2.39 |  | --> | 0.38 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =325 kW | --> | C12 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2786 | -7.4951
066940 | MV/LV Substation GR***940 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E18 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5118 | -6.2245
065025 | MV/LV Substation KE***025 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5364 | -6.1008
021542X | MV/LV Substation LE***542X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0.02 | 0.075 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8972 | -8.5744
052572X | MV/LV Substation QU***572X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.51 | -7.078
0024067 | MV/LV Substation HA***4067 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.041 | 0.04 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2115 | -6.1076
2524152 | MV/LV Substation TH***4152 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 1.32 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C15 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4379 | -10.0764
2884234 | MV/LV Substation CI***4234 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2359 | -6.193
154291Z | MV/LV Substation BE***291Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.004 | 0.178 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.401 | -6.4388
030096X | MV/LV Substation ST***096X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =382 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E14 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9499 | -7.843
021084Z | MV/LV Substation UP***084Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0.016 | 0.08 | 0 |  | --> | C31 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9515 | -8.4328
139203Z | MV/LV Substation MO***203Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8166 | -7.2603
005457 | MV/LV Substation TO***457 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.032 | 17.8 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | E24 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6561 | -6.2562
041299Y | MV/LV Substation KP***299Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =391 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7982 | -8.9152
033055Y | MV/LV Substation KN***055Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C12 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.483 | -7.2136
258552 | MV/LV Substation GL***552 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.068 | 1.86 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E18 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.0559 | -7.936
156854X | MV/LV Substation MU***854X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C17 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.2215 | -7.1014
067549Y | MV/LV Substation QU***549Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =819 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex ROCHES STREET | Roches Street [T41,T42] | LIMERICK |  | 52.6634 | -8.6304
377452X | MV/LV Substation CU***452X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0662 | -9.9102
196244X | MV/LV Substation AT***244X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =609 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.6181 | -6.9066
053754Y | MV/LV Substation ES***754Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 2.39 |  | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | C12 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2939 | -7.502
004815 | MV/LV Substation BA***815 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 18.08 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8005 | -6.1725
1804267 | MV/LV Substation SE***4267 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.68 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.8557 | -6.9855
031029Y | MV/LV Substation KI***029Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =612 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C14 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0919 | -7.6146
081448Y | MV/LV Substation NU***448Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3437 | -6.556
258420 | MV/LV Substation CA***420 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.159 | 1.86 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E17 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.1781 | -7.927
120552Y | MV/LV Substation EN***552Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 3.5 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4105 | -6.8478
149037X | MV/LV Substation BY***037X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6482 | -8.1938
009171 | MV/LV Substation CO***171 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 13.6 |  | --> | 0.38 | 0 | 0.021 | 0.35 | 0 |  | --> | C23 ex KILLOTERAN | Killoteran [T101,T102] | KILLOTERAN |  | 52.2549 | -7.1423
039328 | MV/LV Substation TI***328 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =338 kW | --> | C18 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2917 | -9.0454
109413 | MV/LV Substation FA***413 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =585 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex SHANNON | Shannon [T41,T42] | DRUMLINE |  | 52.7051 | -8.9022
099063 | MV/LV Substation KN***063 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.318 | 5.45 |  | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C17 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9556 | -7.7404
075594X | MV/LV Substation CO***594X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.084 | 1.13 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E18 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6165 | -6.6132
117335Y | MV/LV Substation WA***335Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2126 | -8.5125
1604392 | MV/LV Substation BO***4392 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.178 | -7.2598
016224Z | MV/LV Substation CA***224Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3921 | -6.5556
009020 | MV/LV Substation CO***020 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 8.16 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C11 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2744 | -7.1341
495222 | MV/LV Substation CU***222 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E18 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.9183 | -9.7949
253342X | MV/LV Substation M ***342X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5091 | -8.875
030623 | MV/LV Substation CO***623 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E20 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9644 | -8.0389
0534128 | MV/LV Substation ME***4128 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E24 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1717 | -7.7343
069620 | MV/LV Substation KN***620 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.158 | 4.47 |  | --> | 0.19 | 0 | 0.027 | 0.164 | 0 |  | --> | C20 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2822 | -6.3248
0524522 | MV/LV Substation AN***4522 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | C21 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5172 | -7.3427
031059 | MV/LV Substation SP***059 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =262 kVA | --> | 0.38 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0856 | -7.633
167137Z | MV/LV Substation BA***137Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | E11 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 52.0659 | -8.6131
049039Z | MV/LV Substation BA***039Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C17 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.7451 | -7.9255
156568 | MV/LV Substation ES***568 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.3096 | -7.1276
054196Z | MV/LV Substation PO***196Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C23 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0378 | -7.2963
067062Z | MV/LV Substation GR***062Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.235 | 13.8 |  | --> | 0.38 | 0 | 0 | 0.357 | 0 |  | --> | C19 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6641 | -8.5774
002930 | MV/LV Substation EL***930 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.396 | 4.51 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1816 | -6.1148
120809 | MV/LV Substation EN***809 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.035 | 3.5 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =162 kW | --> | E11 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4139 | -6.8305
046060 | MV/LV Substation MU***060 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.28 | 5.48 |  | --> | 0.38 | 0 | 0 | 0.363 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2794 | -8.4499
154268Z | MV/LV Substation CU***268Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =301 kVA | --> | 0.38 | 0 | 0.01 | 0.359 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4153 | -6.3871
060331Y | MV/LV Substation CL***331Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1356 | -7.2187
009073Y | MV/LV Substation LU***073Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 8.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2954 | -7.0564
008574Z | MV/LV Substation AN***574Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =131 kVA | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4027 | -6.93
064902 | MV/LV Substation BA***902 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C20 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7369 | -6.2756
002920 | MV/LV Substation SW***920 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 4.51 |  | --> | 0.38 | 0 | 0.047 | 0.331 | 0 |  | --> | C14 ex BOGHALL ROAD | Boghall Road [T41,T42] | FASSAROE |  | 53.1839 | -6.1069
127256Y | MV/LV Substation PE***256Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5883 | -7.8706
039095X | MV/LV Substation AN***095X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.284 | 11.03 |  | --> | 0.38 | 0 | 0.005 | 0.36 | 0 |  | --> | C28 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2512 | -9.151
366208X | MV/LV Substation RE***208X |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.187 | 0.45 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.1276 | -9.6868
068876 | MV/LV Substation EY***876 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CAMDEN ROW | Camden Row [T41] | FRANCIS STREET |  | 53.3332 | -6.2569
2884057 | MV/LV Substation EI***4057 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C18 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2446 | -6.2376
0524385 | MV/LV Substation LO***4385 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.39 | 10.9 |  | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C13 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5447 | -7.3419
001025 | MV/LV Substation TA***025 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.2 | 1.16 |  | --> | 0.38 | 0 | 0.088 | 0.287 | 0 |  | --> | C17 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2936 | -6.1922
028057Y | MV/LV Substation CO***057Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 19.7 |  | --> | 0.38 | 0 | 0.006 | 0.36 | 0 |  | --> | C14 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8576 | -8.2922
0494231 | MV/LV Substation CL***4231 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.7166 | -7.8828
041115Y | MV/LV Substation TE***115Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7655 | -8.9652
0524636 | MV/LV Substation ED***4636 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.5333 | -7.1683
067281 | MV/LV Substation DR***281 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C11 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6538 | -8.6573
1364258 | MV/LV Substation BA***4258 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.28 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C21 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.6911 | -8.4732
154514 | MV/LV Substation BA***514 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4094 | -6.3732
167511Y | MV/LV Substation TR***511Y |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =619 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | E21 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.952 | -8.445
003699X | MV/LV Substation BA***699X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.135 | 11.58 |  | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9641 | -6.0612
002923 | MV/LV Substation PO***923 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1728 | -6.1877
0014052 | MV/LV Substation PA***4052 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.23 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2823 | -6.1447
377820 | MV/LV Substation T ***820 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =58 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8687 | -10.3348
196223X | MV/LV Substation OA***223X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =567 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =590 kW | --> | C15 ex TRIM | Trim [T41,T42] | NAVAN |  | 53.5665 | -6.8002
0684015 | MV/LV Substation DI***4015 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =570 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3518 | -6.2711
206903 | MV/LV Substation SE***903 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.367 | 1.6 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | E12 ex BELMULLET | Belmullet [T421] | BELLACORICK |  | 54.2163 | -9.9878
064948 | MV/LV Substation CO***948 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E15 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6363 | -6.2434
153005 | MV/LV Substation NE***005 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | E12 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8068 | -8.4464
130151X | MV/LV Substation BO***151X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C25 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6716 | -7.4532
003384Y | MV/LV Substation CU***384Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.48 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KILMARTIN | Kilmartin [T41] | ARKLOW |  | 53.0422 | -6.0889
119895 | MV/LV Substation GL***895 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 4.16 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C15 ex NEWMARKET (SR) | Newmarket (sr) [T41,T42] | GLENLARA |  | 52.2797 | -9.1821
026226 | MV/LV Substation AR***226 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C15 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7068 | -8.5084
260718X | MV/LV Substation DA***718X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.67 |  | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8827 | -9.5535
0274073 | MV/LV Substation CA***4073 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 3.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7894 | -8.9767
006655Y | MV/LV Substation ME***655Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.323 | 3.12 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C14 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5157 | -6.5693
1564323 | MV/LV Substation MU***4323 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2879 | -6.9668
039037Y | MV/LV Substation RO***037Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C24 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2702 | -8.9866
068166X | MV/LV Substation GR***166X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.6 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3467 | -6.2671
066264X | MV/LV Substation SA***264X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C16 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4353 | -6.1244
0014083 | MV/LV Substation CU***4083 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.23 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2839 | -6.1427
068560X | MV/LV Substation ME***560X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.47 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C20 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.342 | -6.3148
0814114 | MV/LV Substation BA***4114 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =377 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C27 ex GRANGE CASTLE | Grange Castle [T101,T102] | INCHICORE 220KV |  | 53.3186 | -6.448
110298 | MV/LV Substation ME***298 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.142 | 0.76 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E11 ex KILGARVAN | Kilgarvan [T421] | KNOCKEARAGH |  | 51.9183 | -9.4481
0044145 | MV/LV Substation HE***4145 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 18.08 |  | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8007 | -6.1759
011290Z | MV/LV Substation KI***290Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5557 | -7.3491
377108Y | MV/LV Substation FE***108Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.8665 | -10.2536
365533X | MV/LV Substation B/***533X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =867 kVA | --> | 0.95 | 0 | 0.166 | 0.5 | 0 |  | --> | C13 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3252 | -6.3607
007646Z | MV/LV Substation KE***646Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =104 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C18 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3136 | -6.4575
039872X | MV/LV Substation GE***872X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =878 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =933 kW | --> | C12 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2743 | -9.044
120438X | MV/LV Substation CO***438X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 3.5 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex DUNFIRTH | Dunfirth [T122] | DUNFIRTH |  | 53.4347 | -6.8526
061422X | MV/LV Substation CO***422X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 2.04 |  | --> | 0.095 | 0 | 0.045 | 0 | 0 | Constrained, otherwise capacity available =60 kW | --> | C19 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.051 | -6.9021
368424X | MV/LV Substation SP***424X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7876 | -8.7531
062040Y | MV/LV Substation TH***040Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9728 | -6.3914
0934020 | MV/LV Substation MI***4020 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.4178 | -6.2025
024657 | MV/LV Substation VE***657 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 2.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C14 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2623 | -8.6615
127592Y | MV/LV Substation BI***592Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 5.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.4996 | -7.8713
0314136 | MV/LV Substation BA***4136 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9961 | -7.7506
253870X | MV/LV Substation CL***870X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | C17 ex BALLYGAR | Ballygar [T41,T42] | ATHLONE |  | 53.479 | -8.5245
006018 | MV/LV Substation TH***018 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.086 | 3.12 |  | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C14 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5004 | -6.5571
196971 | MV/LV Substation RO***971 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 0.33 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E31 ex TRIM | Trim [T421] | NAVAN |  | 53.5366 | -6.8372
288017 | MV/LV Substation SA***017 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.266 | 1.16 |  | --> | 0.38 | 0 | 0.047 | 0.326 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2836 | -6.2334
065140 | MV/LV Substation BA***140 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0.028 | 0.344 | 0 |  | --> | C25 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5823 | -6.1207
119026 | MV/LV Substation BA***026 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =602 kVA | --> | 0.598 | 0 | 0.25 | 0 | 0 | Constrained, otherwise capacity available =410 kW | --> | C18 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1431 | -8.9069
068490X | MV/LV Substation SM***490X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.6 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex WOLFE TONE STREET | Wolfe Tone Street [T101,T102] | FINGLAS |  | 53.3479 | -6.2787
065141 | MV/LV Substation MI***141 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C16 ex BALBRIGGAN | Balbriggan [T42] | GLASMORE |  | 53.6093 | -6.1852
067220Z | MV/LV Substation CA***220Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 13.8 |  | --> | 0.598 | 0 | 0.05 | 0.5 | 0 |  | --> | C18 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6656 | -8.5793
054003 | MV/LV Substation DU***003 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =214 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C23 ex PORTLAOISE | Portlaoise [T41,T42] | PORTLAOISE |  | 53.0364 | -7.2885
001660 | MV/LV Substation SK***660 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.395 | 0.86 |  | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3073 | -6.1959
253217 | MV/LV Substation S/***217 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =27 kW | --> | C14 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.4902 | -9.0235
152040 | MV/LV Substation MU***040 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C12 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6431 | -8.3983
144434X | MV/LV Substation LI***434X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 2.78 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7491 | -7.3277
038042Y | MV/LV Substation AR***042Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E15 ex GORT | Gort [T41,T42] | ENNIS |  | 53.152 | -8.8068
108601 | MV/LV Substation BA***601 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 1.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.5449 | -8.1419
066399Z | MV/LV Substation TE***399Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =290 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | E16 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5111 | -6.3987
288225X | MV/LV Substation DU***225X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2879 | -6.2415
165034 | MV/LV Substation PO***034 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C13 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6101 | -8.76
037990X | MV/LV Substation MO***990X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =593 kVA | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C15 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.8506 | -9.0132
214027X | MV/LV Substation KE***027X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C15 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.746 | -9.15
001135 | MV/LV Substation SY***135 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =249 kVA | --> | 0.38 | 0 | 0.021 | 0.343 | 0 |  | --> | C13 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.2893 | -6.2394
003406Y | MV/LV Substation BR***406Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.262 | 11.58 |  | --> | 0.38 | 0 | 0.046 | 0 | 0 | Constrained, otherwise capacity available =327 kW | --> | C21 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9882 | -6.0747
288019X | MV/LV Substation RO***019X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0.003 | 0.368 | 0 |  | --> | C13 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2083 | -6.1161
007816X | MV/LV Substation RI***816X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 0.14 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.35 | -6.4665
253815X | MV/LV Substation TH***815X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | E21 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6175 | -8.7457
081429X | MV/LV Substation MA***429X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.077 | 7.91 |  | --> | 0.19 | 0 | 0.041 | 0.142 | 0 |  | --> | C23 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3778 | -6.3825
081209Z | MV/LV Substation LI***209Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =516 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C12 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3551 | -6.3944
139861X | MV/LV Substation CL***861X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 4 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8638 | -7.2509
2544009 | MV/LV Substation DU***4009 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E21 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6222 | -8.7496
039437X | MV/LV Substation W ***437X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 11.03 |  | --> | 0.19 | 0 | 0.036 | 0.16 | 0 |  | --> | C34 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.278 | -9.0736
293827 | MV/LV Substation KE***827 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.431 | 0.43 | Constrained, otherwise capacity available =624 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E18 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8667 | -6.56
210465 | MV/LV Substation LI***465 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C19 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9387 | -6.7877
0064369 | MV/LV Substation BL***4369 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.38 |  | --> | 0.598 | 0 | 0.03 | 0.5 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.4484 | -6.3465
340445 | MV/LV Substation VE***445 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C18 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.9855 | -8.4942
142918X | MV/LV Substation CA***918X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =143 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C16 ex ATHENRY | Athenry [T41,T42] | GALWAY 110KV |  | 53.3071 | -8.7537
081428X | MV/LV Substation CH***428X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =139 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C17 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3353 | -6.3691
1544169 | MV/LV Substation MO***4169 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.066 | 0 | 0 | Constrained, otherwise capacity available =318 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3904 | -6.5894
288918 | MV/LV Substation CA***918 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.348 | 19.52 |  | --> | 0.38 | 0 | 0.031 | 0.35 | 0 |  | --> | C30 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2857 | -6.2436
034667X | MV/LV Substation BA***667X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 0.95 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C15 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3565 | -7.7313
340687 | MV/LV Substation DU***687 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =146 kVA | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =153 kW | --> | C16 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.9524 | -8.3572
053039 | MV/LV Substation SP***039 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =187 kVA | --> | 0.19 | 0 | 0 | 0.188 | 0 |  | --> | C17 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2689 | -7.4921
075494X | MV/LV Substation BA***494X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5164 | -6.306
067321X | MV/LV Substation R ***321X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.095 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | C11 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.7018 | -8.6479
0144263 | MV/LV Substation LO***4263 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =315 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1565 | -6.9229
368289X | MV/LV Substation CO***289X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8015 | -8.7709
039248X | MV/LV Substation KI***248X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.336 | 3.45 |  | --> | 0.38 | 0 | 0.005 | 0.367 | 0 |  | --> | C18 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2695 | -9.058
034015 | MV/LV Substation TH***015 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.228 | 5.88 |  | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =351 kW | --> | C12 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.3606 | -7.6988
154258Z | MV/LV Substation TH***258Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =168 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3769 | -6.3925
0684253 | MV/LV Substation CA***4253 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3484 | -6.2322
003918X | MV/LV Substation FE***918X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.106 | 11.58 |  | --> | 0.19 | 0 | 0.064 | 0 | 0 | Constrained, otherwise capacity available =129 kW | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9839 | -6.0603
237051X | MV/LV Substation CH***051X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8972 | -6.4427
009138 | MV/LV Substation IN***138 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C16 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2449 | -7.1491
154100Z | MV/LV Substation ST***100Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =110 kVA | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C11 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3811 | -6.3982
251063X | MV/LV Substation TO***063X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =197 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C30 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3952 | -9.0338
0694065 | MV/LV Substation WI***4065 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.34 |  | --> | 0.598 | 0 | 0.085 | 0.5 | 0 |  | --> | C13 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.3093 | -6.3308
149378 | MV/LV Substation SE***378 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6518 | -8.143
038560X | MV/LV Substation KI***560X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0389 | -8.9468
019048 | MV/LV Substation DE***048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.047 | 0.05 | Constrained, otherwise capacity available =261 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C18 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2837 | -9.6808
122044 | MV/LV Substation KI***044 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 4.18 |  | --> | 0.19 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8486 | -6.8041
0654104 | MV/LV Substation BA***4104 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.045 | 0.334 | 0 |  | --> | C25 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.5841 | -6.1402
021478Z | MV/LV Substation AS***478Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =292 kVA | --> | 0.38 | 0 | 0.018 | 0.352 | 0 |  | --> | C11 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9086 | -8.4185
077198X | MV/LV Substation FE***198X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E16 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.567 | -8.7836
007008 | MV/LV Substation MA***008 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C19 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3303 | -6.4493
1544436 | MV/LV Substation OA***4436 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4131 | -6.4617
081229Z | MV/LV Substation PA***229Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =958 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3306 | -6.3708
069755 | MV/LV Substation BR***755 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 3.34 |  | --> | 0.598 | 0 | 0 | 0.483 | 0 |  | --> | C18 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.314 | -6.3359
237484 | MV/LV Substation KI***484 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =66 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8729 | -6.3814
052493X | MV/LV Substation NE***493X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.5149 | -7.3813
023097Y | MV/LV Substation KI***097Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1738 | -8.2338
0084468 | MV/LV Substation NB***4468 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.2 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.1961 | -6.8447
064196Y | MV/LV Substation WE***196Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C17 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7146 | -6.3535
365738X | MV/LV Substation BA***738X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 |  | --> | 0.38 | 0 | 0.04 | 0.318 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3105 | -6.3471
039140 | MV/LV Substation CO***140 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | C11 ex HEADFORD ROAD | Headford Road [T41,T42] | GALWAY 110KV |  | 53.2768 | -9.049
008689 | MV/LV Substation BR***689 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.137 | 0.2 |  | --> | 0.19 | 0 | 0.12 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E15 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.307 | -6.7993
066298Z | MV/LV Substation ST***298Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =357 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4925 | -6.1157
196502 | MV/LV Substation CA***502 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 1.34 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.4913 | -6.9144
027823 | MV/LV Substation SH***823 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 7.79 |  | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C19 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.7561 | -9.0294
039025 | MV/LV Substation SE***025 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 11.03 |  | --> | 0.19 | 0 | 0.033 | 0.156 | 0 |  | --> | C33 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2611 | -9.117
081171Z | MV/LV Substation F.***171Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.38 | 0 | 0 | 0.349 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.327 | -6.3439
251104X | MV/LV Substation AN***104X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C30 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3839 | -9.0704
059690Y | MV/LV Substation DR***690Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | E17 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0154 | -7.3618
050279 | MV/LV Substation BA***279 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C22 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4492 | -7.9859
363693 | MV/LV Substation LI***693 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 3.25 |  | --> | 0.095 | 0 | 0.044 | 0 | 0 | Constrained, otherwise capacity available =56 kW | --> | E16 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.4875 | -9.5775
365143X | MV/LV Substation RO***143X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3171 | -6.3467
064880Y | MV/LV Substation FI***880Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C18 ex RATHMULLAN | Rathmullan [T41,T42] | DRYBRIDGE |  | 53.7038 | -6.3293
008031Z | MV/LV Substation PA***031Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 0.24 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ROSBERCON | Rosbercon [T41,T42] | WATERFORD |  | 52.3687 | -7.0272
074485X | MV/LV Substation SH***485X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9378 | -8.1162
034324 | MV/LV Substation KN***324 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 0.57 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.5251 | -7.7215
010153X | MV/LV Substation RA***153X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.6235 | -6.8128
049859Y | MV/LV Substation CL***859Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.213 | 0.21 | Constrained, otherwise capacity available =281 kVA | --> | 0.38 | 0 | 0.061 | 0 | 0 | Constrained, otherwise capacity available =318 kW | --> | E18 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7489 | -7.797
002122 | MV/LV Substation AR***122 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 2.36 |  | --> | 0.38 | 0 | 0.03 | 0.341 | 0 |  | --> | C13 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1978 | -6.1176
011658Y | MV/LV Substation BO***658Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =354 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C14 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6017 | -6.9271
1114273 | MV/LV Substation EY***4273 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.94 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex CASTLETOWNBERE | Castletownbere [T421] | BALLYLICKY |  | 51.6924 | -9.9545
068773 | MV/LV Substation GR***773 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.38 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3389 | -6.2441
036051 | MV/LV Substation LA***051 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4784 | -8.1529
069727 | MV/LV Substation HX***727 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.498 | 9.99 |  | --> | 0.598 | 0 | 0.002 | 0.5 | 0 |  | --> | C12 ex HAROLDS CROSS | Harolds Cross [T101,T102] | POOLBEG |  | 53.3235 | -6.278
265962X | MV/LV Substation RA***962X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.066 | 0.07 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1229 | -7.573
0544250 | MV/LV Substation CR***4250 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.9011 | -7.4572
0314132 | MV/LV Substation HI***4132 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0941 | -7.6826
154737 | MV/LV Substation ST***737 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.028 | 0 | 0.01 | 0.02 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4028 | -6.4564
015012Y | MV/LV Substation EL***012Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 12.6 |  | --> | 0.38 | 0 | 0.083 | 0.306 | 0 |  | --> | C12 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2177 | -6.6555
2884198 | MV/LV Substation GL***4198 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =893 kVA | --> | 0.95 | 0 | 0.05 | 0.5 | 0 |  | --> | C17 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2433 | -6.1914
041585X | MV/LV Substation BE***585X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7848 | -8.9195
029119 | MV/LV Substation CA***119 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =498 kVA | --> | 0.598 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =565 kW | --> | C17 ex KILLACLOYNE | Killacloyne [T41,T42] | MIDLETON |  | 51.9083 | -8.2688
001809 | MV/LV Substation OB***809 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 1.55 |  | --> | 0.38 | 0 | 0.035 | 0.341 | 0 |  | --> | C11 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2896 | -6.1863
069700 | MV/LV Substation BE***700 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 9.28 |  | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C21 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3298 | -6.2303
011224Y | MV/LV Substation PA***224Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =82 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C23 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6803 | -7.024
071020 | MV/LV Substation SE***020 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 5.58 |  | --> | 0.048 | 0 | 0.009 | 0.037 | 0 |  | --> | C12 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.1057 | -6.0462
066164 | MV/LV Substation CO***164 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =61 kVA | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =83 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4711 | -6.1278
075838X | MV/LV Substation BA***838X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.4888 | -6.2949
151704 | MV/LV Substation AS***704 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex GARRYSPILLANE | Garryspillane [T41] | TIPPERARY |  | 52.3632 | -8.2576
066046Y | MV/LV Substation DU***046Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =218 kVA | --> | 0.38 | 0 | 0.001 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5076 | -6.5363
162402 | MV/LV Substation RA***402 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.166 | 7.25 |  | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C18 ex CONVOY | Convoy [T41,T42] | LETTERKENNY |  | 54.8743 | -7.602
023562 | MV/LV Substation CA***562 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =80 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C18 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1416 | -8.3154
064487X | MV/LV Substation DU***487X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6301 | -6.4218
256160X | MV/LV Substation CA***160X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.28 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C22 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7663 | -8.5043
062853 | MV/LV Substation CO***853 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.053 | 1.03 |  | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9266 | -6.403
151403X | MV/LV Substation MC***403X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =542 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E15 ex BRUFF | Bruff [T42,T421] | LIMERICK |  | 52.5252 | -8.4755
095415X | MV/LV Substation MO***415X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.7 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex KILRUSH | Kilrush [T41,T42] | TULLABRACK |  | 52.6796 | -9.5581
082550Y | MV/LV Substation TA***550Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.132 | 2.01 |  | --> | 0.19 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C12 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6679 | -6.6813
1204238 | MV/LV Substation TH***4238 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C15 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2869 | -6.8639
0934174 | MV/LV Substation SA***4174 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C20 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3878 | -6.2968
2074123 | MV/LV Substation BA***4123 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.6415 | -7.5443
021456Z | MV/LV Substation TI***456Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.173 | 6.78 |  | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C41 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9026 | -8.4275
081228Z | MV/LV Substation PA***228Z |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =744 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3318 | -6.3709
0144088 | MV/LV Substation PU***4088 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1493 | -6.9025
060031 | MV/LV Substation MU***031 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C16 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1791 | -7.2456
063117X | MV/LV Substation PH***117X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | C15 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.9369 | -6.5641
082572Y | MV/LV Substation LI***572Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6014 | -6.5905
062274X | MV/LV Substation MA***274X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.187 | 3.12 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C20 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9643 | -6.3648
276254 | MV/LV Substation AR***254 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =556 kVA | --> | 0.598 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C11 ex COOLCORCORAN | Coolcorcoran [T41,T42] | KNOCKEARAGH |  | 52.0616 | -9.4952
007061X | MV/LV Substation HO***061X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 16.12 |  | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | E12 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3491 | -6.5724
011996X | MV/LV Substation DU***996X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C21 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6933 | -7.2679
127434X | MV/LV Substation TU***434X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6698 | -7.684
081410X | MV/LV Substation GR***410X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =122 kVA | --> | 0.19 | 0 | 0.013 | 0.169 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3487 | -6.3959
019983 | MV/LV Substation KE***983 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.18 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | C12 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2682 | -9.7379
160597X | MV/LV Substation SW***597X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =326 kW | --> | C15 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1593 | -7.1853
368990 | MV/LV Substation HA***990 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =979 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =947 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.8433 | -8.7932
006003 | MV/LV Substation MA***003 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.35 | 3.12 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | C17 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5018 | -6.5694
009429Y | MV/LV Substation RO***429Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.141 | 8.16 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C12 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2699 | -7.106
066109 | MV/LV Substation LI***109 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.031 | 0 | 0 | 0.031 | 0 |  | --> | C16 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4442 | -6.1941
029505X | MV/LV Substation GO***505X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9375 | -8.1876
2814360 | MV/LV Substation GO***4360 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C22 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8004 | -8.4047
0934247 | MV/LV Substation SE***4247 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =874 kVA | --> | 0.95 | 0 | 0.029 | 0.5 | 0 |  | --> | C12 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3877 | -6.1026
365800X | MV/LV Substation WO***800X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =242 kVA | --> | 0.38 | 0 | 0.044 | 0.325 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2741 | -6.3264
082721 | MV/LV Substation BA***721 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E17 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6046 | -6.7874
049295Y | MV/LV Substation ST***295Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.169 | 2.8 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C17 ex GLEBE | Glebe [T41,T42] | RICHMOND |  | 53.7325 | -7.7802
144947X | MV/LV Substation MU***947X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.7561 | -7.175
022224 | MV/LV Substation CL***224 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 4.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1653 | -8.6486
266558 | MV/LV Substation ST***558 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 3.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2882 | -7.1662
0814264 | MV/LV Substation ST***4264 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =537 kVA | --> | 0.598 | 0 | 0.018 | 0.5 | 0 |  | --> | C12 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3549 | -6.4048
120213Y | MV/LV Substation MO***213Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E19 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.4513 | -7.019
063705X | MV/LV Substation TA***705X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =151 kVA | --> | 0.19 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C15 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.9229 | -6.5432
0114275 | MV/LV Substation CI***4275 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.476 | 5.05 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =577 kW | --> | C21 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6572 | -7.2468
0664353 | MV/LV Substation TH***4353 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =564 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5039 | -6.532
028405X | MV/LV Substation RE***405X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 19.7 |  | --> | 0.598 | 0 | 0.02 | 0.5 | 0 |  | --> | C12 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8547 | -8.298
011620Z | MV/LV Substation UP***620Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =32 kW | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.626 | -7.0466
006538Y | MV/LV Substation BR***538Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.12 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.51 | -6.5919
062640Y | MV/LV Substation MA***640Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.185 | 3.12 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9576 | -6.3807
125022 | MV/LV Substation MI***022 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C16 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2625 | -8.275
015889Z | MV/LV Substation MU***889Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1505 | -6.632
001148 | MV/LV Substation CA***148 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.182 | 1.55 |  | --> | 0.38 | 0 | 0.083 | 0.288 | 0 |  | --> | C11 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2936 | -6.1794
117175Y | MV/LV Substation BA***175Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =184 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E22 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1983 | -8.3613
093019Z | MV/LV Substation JO***019Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C20 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.3872 | -6.3008
056317 | MV/LV Substation LO***317 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0923 | -8.1269
036697 | MV/LV Substation AC***697 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E18 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5096 | -8.2173
026898X | MV/LV Substation MC***898X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7118 | -8.6518
029387Y | MV/LV Substation WO***387Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.8679 | -8.1631
167496Y | MV/LV Substation CO***496Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =25 kW | --> | E21 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9731 | -8.4569
003036 | MV/LV Substation ST***036 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =170 kVA | --> | 0.19 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9342 | -6.2401
069321 | MV/LV Substation ST***321 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.303 | 3.34 |  | --> | 0.38 | 0 | 0.007 | 0.361 | 0 |  | --> | C20 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.3122 | -6.3393
012678 | MV/LV Substation PA***678 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =60 kVA | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | C24 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8631 | -6.8615
0624247 | MV/LV Substation CO***4247 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.318 | 0.72 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C12 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.0022 | -6.3772
075543 | MV/LV Substation CA***543 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0.58 |  | --> | 0.19 | 0 | 0.049 | 0 | 0 | Constrained, otherwise capacity available =124 kW | --> | E17 ex FERNS | Ferns [T421] | CRANE |  | 52.6173 | -6.4241
064567X | MV/LV Substation ST***567X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.6922 | -6.4232
029164Y | MV/LV Substation RO***164Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C17 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9125 | -8.1689
180081Y | MV/LV Substation FA***081Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.258 | 0.68 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C24 ex MULLAGH | Mullagh [T44] | MEATH HILL |  | 53.813 | -6.9449
293905 | MV/LV Substation TI***905 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =90 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.89 | -6.619
305002 | MV/LV Substation BA***002 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.131 | 0.3 |  | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =336 kW | --> | C15 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.1901 | -7.9867
066091 | MV/LV Substation BA***091 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =74 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E20 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4816 | -6.235
034913X | MV/LV Substation DR***913X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.143 | 0.57 |  | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =166 kW | --> | C16 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3658 | -7.7167
008548 | MV/LV Substation AL***548 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 0.2 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E17 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.1744 | -6.8799
029329Y | MV/LV Substation KN***329Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =287 kVA | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C22 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9185 | -8.1837
176803 | MV/LV Substation RA***803 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 18.78 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E14 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | MACROOM |  | 51.9185 | -9.1212
0894109 | MV/LV Substation TU***4109 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.56 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | E20 ex ENNISCRONE | Enniscrone [T421,T422] | MOY |  | 54.2083 | -9.0979
0664163 | MV/LV Substation HA***4163 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5121 | -6.5372
049442X | MV/LV Substation BA***442X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.6442 | -7.6707
050414Y | MV/LV Substation CR***414Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C24 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.374 | -7.9935
003909X | MV/LV Substation KE***909X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 11.58 |  | --> | 0.19 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.983 | -6.0654
049411Z | MV/LV Substation AI***411Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.13 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5926 | -7.6442
182070X | MV/LV Substation BA***070X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.8728 | -8.4888
005534X | MV/LV Substation ID***534X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =205 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | E19 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.712 | -6.4923
1804180 | MV/LV Substation CA***4180 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.27 |  | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7371 | -6.9296
154453Z | MV/LV Substation DU***453Z |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =521 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.4148 | -6.4796
011976X | MV/LV Substation HE***976X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.307 | 5.05 |  | --> | 0.38 | 0 | 0.109 | 0 | 0 | Constrained, otherwise capacity available =286 kW | --> | C14 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6547 | -7.2268
008949X | MV/LV Substation MA***949X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =386 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3835 | -6.9575
015676 | MV/LV Substation PO***676 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =87 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1205 | -6.5859
025670Y | MV/LV Substation BE***670Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =397 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4028 | -8.5832
029590Y | MV/LV Substation TA***590Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex CARRIGSHANE | Carrigshane [T41] | MIDLETON |  | 51.8421 | -8.1698
255176X | MV/LV Substation NE***176X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6307 | -8.4423
033042 | MV/LV Substation BA***042 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =309 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C17 ex DEERPARK | Deerpark [T41,T42] | BALLYDINE |  | 52.3531 | -7.4116
009674X | MV/LV Substation BE***674X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0.53 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =150 kW | --> | C16 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2589 | -7.1059
1544139 | MV/LV Substation HA***4139 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =447 kVA | --> | 0.598 | 0 | 0.031 | 0 | 0 | Constrained, otherwise capacity available =550 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.387 | -6.4375
019143 | MV/LV Substation RU***143 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.091 | 1.54 |  | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2497 | -9.7004
156953Y | MV/LV Substation GO***953Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3355 | -7.051
1114237 | MV/LV Substation SU***4237 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =505 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6816 | -9.4593
004278Y | MV/LV Substation BA***278Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.739 | -6.316
051508X | MV/LV Substation AS***508X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 2.22 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | E21 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3902 | -7.6707
014197Z | MV/LV Substation TR***197Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =256 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1532 | -6.9129
0254400 | MV/LV Substation BR***4400 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.3446 | -8.9849
014076 | MV/LV Substation TH***076 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =555 kW | --> | C17 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.177 | -6.8058
111407X | MV/LV Substation GO***407X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =31 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.7193 | -9.4377
016240Z | MV/LV Substation GR***240Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =896 kVA | --> | 0.95 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =928 kW | --> | E58 ex GRANGE CASTLE |  |  |  | 53.2945 | -6.4756
009701 | MV/LV Substation SN***701 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 3.76 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex BELVIEW | Belview [T421,T422] | WATERFORD |  | 52.2602 | -7.0677
017212Z | MV/LV Substation FE***212Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.094 | 1.98 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E12 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.4169 | -8.9233
093370Z | MV/LV Substation BY***370Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =596 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4091 | -6.2395
068399 | MV/LV Substation NE***399 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.224 | 1.47 |  | --> | 0.598 | 0 | 0.055 | 0.5 | 0 |  | --> | C11 ex MARROWBONE LANE | Marrowbone Lane [T42] | INCHICORE 220KV |  | 53.3369 | -6.2997
1204345 | MV/LV Substation SI***4345 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E14 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3465 | -7.0189
075225Y | MV/LV Substation SE***225Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 0.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex FERNS | Ferns [T421] | CRANE |  | 52.5861 | -6.4887
068602X | MV/LV Substation LI***602X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =882 kVA | --> | 0.95 | 0 | 0.011 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.352 | -6.2532
0154371 | MV/LV Substation CA***4371 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =518 kVA | --> | 0.598 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =565 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2973 | -6.6848
013461X | MV/LV Substation A ***461X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 0.12 |  | --> | 0.095 | 0 | 0.005 | 0.091 | 0 |  | --> | C12 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9873 | -6.965
0664078 | MV/LV Substation TA***4078 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =127 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4309 | -6.1685
0044251 | MV/LV Substation LO***4251 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =148 kW | --> | E13 ex SHILLELAGH | Shillelagh [T421,T422] | CARLOW |  | 52.7622 | -6.41
118676X | MV/LV Substation BU***676X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.3501 | -8.2548
095294 | MV/LV Substation KI***294 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =110 kVA | --> | 0.19 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =160 kW | --> | C15 ex CRANNY | Cranny [T41] | ENNIS |  | 52.7235 | -9.3198
0564159 | MV/LV Substation LI***4159 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.89 |  | --> | 0.048 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =28 kW | --> | E20 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0279 | -8.0459
0684178 | MV/LV Substation GL***4178 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =867 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3542 | -6.2555
014375X | MV/LV Substation FU***375X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 0.12 |  | --> | 0.048 | 0 | 0.02 | 0.03 | 0 |  | --> | C12 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0062 | -6.8158
069508 | MV/LV Substation WI***508 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.29 | 9.28 |  | --> | 0.38 | 0 | 0.013 | 0.355 | 0 |  | --> | C19 ex PEMBROKE | Pembroke [T41,T42,T43,T44] | RINGSEND |  | 53.3265 | -6.2158
060223Y | MV/LV Substation MU***223Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C16 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1784 | -7.2477
003096 | MV/LV Substation WO***096 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.934 | -6.2424
160950Y | MV/LV Substation MO***950Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0909 | -7.207
0934152 | MV/LV Substation IN***4152 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =209 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4143 | -6.3142
026764X | MV/LV Substation PA***764X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =53 kVA | --> | 0.19 | 0 | 0.044 | 0 | 0 | Constrained, otherwise capacity available =136 kW | --> | C16 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7077 | -8.527
0254144 | MV/LV Substation AN***4144 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C17 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4051 | -8.5883
0934149 | MV/LV Substation SI***4149 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.364 | 2.86 |  | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C19 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3932 | -6.2692
037244Y | MV/LV Substation SO***244Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C16 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8368 | -8.9962
0494080 | MV/LV Substation CL***4080 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E16 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8414 | -7.4657
099895 | MV/LV Substation FE***895 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.043 | 5.45 |  | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =72 kW | --> | C14 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.9599 | -7.7488
154308Y | MV/LV Substation TE***308Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =140 kVA | --> | 0.19 | 0 | 0.058 | 0.139 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.423 | -6.4717
0214205 | MV/LV Substation BI***4205 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =523 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9116 | -8.4798
029418 | MV/LV Substation BA***418 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.005 | 0.042 | 0 |  | --> | C18 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9843 | -8.1024
243158 | MV/LV Substation GA***158 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E16 ex DINGLE | Dingle [T421,T422] | OUGHTRAGH |  | 52.1501 | -10.2276
156293 | MV/LV Substation CA***293 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.058 | 2.1 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E17 ex LISDRUM | Lisdrum [T422] | LISDRUM |  | 54.1857 | -7.0322
001735 | MV/LV Substation BL***735 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.313 | 0.86 |  | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3037 | -6.1878
005504 | MV/LV Substation CO***504 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.09 | 17.8 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E19 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6459 | -6.2859
031363Y | MV/LV Substation GO***363Y |  | 20 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =186 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0851 | -7.5683
1504074 | MV/LV Substation PR***4074 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.7967 | -7.7198
003420Y | MV/LV Substation NE***420Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0027 | -6.0857
184018 | MV/LV Substation DR***018 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.288 | 3.38 |  | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C13 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1223 | -6.7402
068635X | MV/LV Substation FA***635X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.2 | 1.86 |  | --> | 0.38 | 0 | 0.015 | 0.341 | 0 |  | --> | C16 ex FAIRVIEW | Fairview [T41] | MCDERMOTT |  | 53.3626 | -6.2374
016060Z | MV/LV Substation PI***060Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C21 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4805 | -6.5558
365007X | MV/LV Substation BA***007X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =237 kVA | --> | 0.38 | 0 | 0.043 | 0.325 | 0 |  | --> | C13 ex BELGARD | Belgard [T41,T42] | COOKSTOWN |  | 53.2894 | -6.3497
026766 | MV/LV Substation DA***766 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C17 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7919 | -8.5825
067886Y | MV/LV Substation CA***886Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.382 | 13.8 |  | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C21 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6586 | -8.5885
160895X | MV/LV Substation DE***895X |  | 20 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0.03 | 0.12 |  | --> | 0.028 | 0 | 0 | 0.028 | 0 |  | --> | E64 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0385 | -7.0847
293002 | MV/LV Substation CH***002 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.38 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =319 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9409 | -6.7093
0684176 | MV/LV Substation GL***4176 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C13 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3542 | -6.2554
2544132 | MV/LV Substation EM***4132 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C14 ex HEADFORD | Headford [T41,T42] | CLOON |  | 53.5263 | -9.0132
054341 | MV/LV Substation BE***341 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.99 | -7.4849
365146X | MV/LV Substation PA***146X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =369 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3179 | -6.3414
007615 | MV/LV Substation FU***615 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.4 |  | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | E11 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2165 | -6.5285
0394043 | MV/LV Substation ST***4043 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.235 | 3.45 |  | --> | 0.38 | 0 | 0 | 0.357 | 0 |  | --> | C19 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2725 | -9.0661
031305 | MV/LV Substation BA***305 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =17 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | E18 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0462 | -7.5694
019076 | MV/LV Substation JO***076 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.304 | 2.18 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C21 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2641 | -9.7172
366147X | MV/LV Substation EA***147X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.45 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0996 | -9.6546
305798 | MV/LV Substation FE***798 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.163 | 4.61 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E12 ex LUMCLOON | Lumcloon [T421,T422] | DALLOW |  | 53.2693 | -7.8366
1574050 | MV/LV Substation TU***4050 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.1233 | -7.7696
117480X | MV/LV Substation SP***480X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E20 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.2124 | -8.5202
029267Y | MV/LV Substation OR***267Y |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =349 kW | --> | C13 ex CLOYNE | Cloyne [T41] | MIDLETON |  | 51.8557 | -8.0354
350372 | MV/LV Substation CA***372 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 1.57 |  | --> | 0.19 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =172 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4674 | -8.328
074259X | MV/LV Substation GO***259X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9601 | -8.1743
281664Z | MV/LV Substation BR***664Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.01 | 17.47 |  | --> | 0.048 | 0 | 0 | 0.042 | 0 |  | --> | E12 ex COOLROE | Coolroe [T121,T122] | COOLROE |  | 51.8879 | -8.6877
0584477 | MV/LV Substation SR***4477 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C25 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8082 | -8.1411
253202 | MV/LV Substation C/***202 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.4916 | -9.0183
192695 | MV/LV Substation SE***695 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.7 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex GWEEDORE | Gweedore [T421] | ARDNAGAPPARY |  | 55.1406 | -8.0925
014907 | MV/LV Substation BR***907 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 |  | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1393 | -6.839
014780 | MV/LV Substation BA***780 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C13 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1669 | -6.827
036030 | MV/LV Substation ST***030 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =335 kW | --> | E17 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.4784 | -8.1631
034217Y | MV/LV Substation MO***217Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.5245 | -7.7553
305001 | MV/LV Substation RA***001 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.099 | 0.3 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | C15 ex BANAGHER | Banagher [T41,T42] | DALLOW |  | 53.1925 | -7.9899
015298Z | MV/LV Substation OA***298Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E20 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1755 | -6.5314
039743X | MV/LV Substation DU***743X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0.004 | 0.186 | 0 |  | --> | C22 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2899 | -8.9947
049283 | MV/LV Substation SH***283 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 2.8 |  | --> | 0.95 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =892 kW | --> | C16 ex GLEBE | Glebe [T41,T42] | RICHMOND |  | 53.7288 | -7.7978
125563 | MV/LV Substation RO***563 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CLOONLOUGH | Cloonlough [T41,T42] | BARRYMORE |  | 52.2392 | -8.4074
066707 | MV/LV Substation BU***707 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.5015 | -6.1182
064229Y | MV/LV Substation MO***229Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =127 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C13 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7161 | -6.2554
015940Z | MV/LV Substation SC***940Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =227 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =552 kW | --> | C18 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.1957 | -6.7428
001061 | MV/LV Substation SH***061 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =385 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2316 | -6.1127
4334082 | MV/LV Substation UR***4082 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.8559 | -8.7323
031974 | MV/LV Substation BO***974 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =133 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C17 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0941 | -7.6983
099425 | MV/LV Substation MO***425 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =181 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9742 | -7.6012
060801X | MV/LV Substation CA***801X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.1811 | -7.2434
013652Y | MV/LV Substation RH***652Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0.014 | 0.364 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9979 | -6.9779
019748 | MV/LV Substation ED***748 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.54 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C16 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2709 | -9.7014
068745 | MV/LV Substation BO***745 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 3.38 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3347 | -6.2467
053029 | MV/LV Substation WH***029 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =118 kVA | --> | 0.19 | 0 | 0.038 | 0.15 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2768 | -7.4821
064191Z | MV/LV Substation GL***191Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7535 | -6.4945
252081 | MV/LV Substation SW***081 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.086 | 1.32 |  | --> | 0.095 | 0 | 0.009 | 0.086 | 0 |  | --> | C15 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4283 | -10.0541
0214108 | MV/LV Substation AL***4108 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =399 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C15 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9308 | -8.3907
007739X | MV/LV Substation NU***739X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 16.12 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3852 | -6.4494
034304Y | MV/LV Substation LI***304Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 5.88 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.405 | -7.7004
017376X | MV/LV Substation IJ***376X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.373 | 1.58 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C12 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.6116 | -9.0924
029289 | MV/LV Substation BA***289 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9336 | -8.0911
156347Z | MV/LV Substation CA***347Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C17 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.2253 | -7.0924
062159X | MV/LV Substation LO***159X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.69 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C20 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0066 | -6.4054
0104037 | MV/LV Substation CO***4037 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C17 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.5707 | -6.9109
0124186 | MV/LV Substation LE***4186 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.321 | 2.83 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.7012 | -6.9523
012518Y | MV/LV Substation CL***518Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.99 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.779 | -6.941
013275 | MV/LV Substation KI***275 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E62 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0347 | -6.9059
0074265 | MV/LV Substation AR***4265 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =264 kVA | --> | 0.38 | 0 | 0.152 | 0 | 0 | Constrained, otherwise capacity available =248 kW | --> | C13 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3166 | -6.4765
002110 | MV/LV Substation AR***110 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 2.36 |  | --> | 0.598 | 0 | 0.055 | 0.5 | 0 |  | --> | C12 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.199 | -6.1223
209615X | MV/LV Substation LE***615X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =165 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.0327 | -7.6517
154353Z | MV/LV Substation BA***353Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4179 | -6.3845
014790Z | MV/LV Substation RA***790Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =135 kVA | --> | 0.19 | 0 | 0.058 | 0 | 0 | Constrained, otherwise capacity available =138 kW | --> | C20 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1667 | -6.905
081194X | MV/LV Substation ST***194X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =294 kVA | --> | 0.38 | 0 | 0.009 | 0.359 | 0 |  | --> | C11 ex LIFFEY VALLEY | Liffey Valley [T41,T42] | INCHICORE 220KV |  | 53.3439 | -6.4007
003431Y | MV/LV Substation LI***431Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.278 | 11.58 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C25 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9863 | -6.0566
1304037 | MV/LV Substation TE***4037 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E12 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.7697 | -7.499
051527X | MV/LV Substation CL***527X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.365 | 2.22 |  | --> | 0.38 | 0 | 0.007 | 0.37 | 0 |  | --> | E14 ex CLARA | Clara [T421,T422] | THORNSBERRY |  | 53.3375 | -7.6068
009787X | MV/LV Substation MA***787X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.329 | 0.53 |  | --> | 0.38 | 0 | 0.052 | 0 | 0 | Constrained, otherwise capacity available =332 kW | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.252 | -7.0748
082154Z | MV/LV Substation LI***154Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.01 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C18 ex ABBEYLAND | Abbeyland [T41,T42] | NAVAN |  | 53.6615 | -6.7342
253659Y | MV/LV Substation GA***659Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C23 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5388 | -8.8693
082006 | MV/LV Substation LO***006 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C30 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6503 | -6.677
139587X | MV/LV Substation BA***587X |  | 20 kV | _ | LV | 45 kVA :Pole Substation | 0.045 | --> | 0.045 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.043 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E21 ex FINEA | Finea [T421,T422] | SHANKILL |  | 53.8361 | -7.3472
067033Y | MV/LV Substation BR***033Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.331 | 13.8 |  | --> | 0.38 | 0 | 0.01 | 0.363 | 0 |  | --> | C18 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6665 | -8.5578
495747 | MV/LV Substation CA***747 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 1.5 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E17 ex ACHILL | Achill [T422] | CARROWBEG |  | 53.958 | -9.9688
204015 | MV/LV Substation NU***015 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =346 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | E16 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1341 | -7.4501
039010Y | MV/LV Substation SR***010Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =271 kVA | --> | 0.38 | 0 | 0 | 0.362 | 0 |  | --> | C22 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2844 | -8.9786
0814419 | MV/LV Substation TH***4419 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3323 | -6.4079
503460 | MV/LV Substation NA***460 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 1.69 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.036 | -7.3819
349080 | MV/LV Substation SW***080 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.35 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8553 | -8.9949
184259 | MV/LV Substation TH***259 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.077 | 3.38 |  | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C19 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1129 | -6.7535
029218 | MV/LV Substation GE***218 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9052 | -8.0371
041972 | MV/LV Substation MA***972 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.76 | -9.1144
001578 | MV/LV Substation LA***578 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.289 | 1.16 |  | --> | 0.38 | 0 | 0.134 | 0.265 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2815 | -6.2143
1224049 | MV/LV Substation CO***4049 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.491 | 4.18 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.909 | -6.8047
2534310 | MV/LV Substation LI***4310 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C15 ex TUAM NORTH | Tuam North [T41,T42] | CLOON |  | 53.5076 | -8.872
237859 | MV/LV Substation RE***859 |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =931 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =940 kW | --> | C12 ex DUNLEER | Dunleer [T41,T42] | DRYBRIDGE |  | 53.7972 | -6.2273
062821X | MV/LV Substation DR***821X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9226 | -6.3959
154266Z | MV/LV Substation BI***266Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0.01 | 0.362 | 0 |  | --> | C39 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4188 | -6.3834
1564109 | MV/LV Substation EL***4109 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C14 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2342 | -6.9658
077407 | MV/LV Substation KI***407 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E16 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5927 | -8.7594
153819 | MV/LV Substation PA***819 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =337 kVA | --> | 0.38 | 0 | 0.038 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | E17 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8181 | -8.4423
162222X | MV/LV Substation TR***222X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C20 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.8822 | -7.7453
015072 | MV/LV Substation MI***072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =254 kVA | --> | 0.38 | 0 | 0.066 | 0 | 0 | Constrained, otherwise capacity available =311 kW | --> | C14 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2161 | -6.6595
176073Y | MV/LV Substation MI***073Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 18.78 |  | --> | 0.19 | 0 | 0.01 | 0.176 | 0 |  | --> | E11 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | HARTNETTS CROSS |  | 51.907 | -8.9765
034561 | MV/LV Substation BA***561 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 0.57 |  | --> | 0.048 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =26 kW | --> | E23 ex LAWLESSTOWN | Lawlesstown [T42,T421] | DOON |  | 52.3926 | -7.8119
2524110 | MV/LV Substation KY***4110 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 2.76 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C13 ex RECESS | Recess [T41] | SCREEB |  | 53.5617 | -9.8999
256151X | MV/LV Substation TE***151X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.28 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.7715 | -8.4814
008005X | MV/LV Substation HO***005X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.205 | 0.2 | Constrained, otherwise capacity available =363 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | E17 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.1644 | -6.8807
075759 | MV/LV Substation CL***759 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E17 ex CRANE | Crane [T122] | CRANE |  | 52.5757 | -6.5005
122738 | MV/LV Substation ME***738 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 4.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C17 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8905 | -6.7089
066699Z | MV/LV Substation PA***699Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =434 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4554 | -6.2196
010546X | MV/LV Substation MA***546X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | E11 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.5257 | -7.1381
006427Y | MV/LV Substation BA***427Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.13 | 4.38 |  | --> | 0.19 | 0 | 0.012 | 0.171 | 0 |  | --> | E13 ex CRANE | Crane [T122] | CRANE |  | 52.4391 | -6.4773
0654238 | MV/LV Substation BA***4238 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5105 | -6.1475
248533X | MV/LV Substation TE***533X |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =277 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | E13 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.519 | -6.658
350470 | MV/LV Substation MC***470 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.57 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C18 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4564 | -8.2763
039500X | MV/LV Substation GO***500X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 11.03 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C36 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.3002 | -9.1053
266527 | MV/LV Substation MI***527 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2433 | -7.2706
210306 | MV/LV Substation DU***306 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9806 | -6.6348
056051Y | MV/LV Substation CL***051Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.89 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C21 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.0806 | -7.8796
054019X | MV/LV Substation PA***019X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =82 kW | --> | C15 ex MOUNTRATH | Mountrath [T41,T42] | PORTLAOISE |  | 52.8836 | -7.4465
064280Z | MV/LV Substation GR***280Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C12 ex MORNINGTON ROAD | Mornington Road [T41,T42] | DRYBRIDGE |  | 53.7049 | -6.3005
012641 | MV/LV Substation JE***641 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 1.99 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8899 | -6.9351
053259Z | MV/LV Substation MU***259Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0.003 | 0.042 | 0 |  | --> | E18 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2529 | -7.5438
154741 | MV/LV Substation SU***741 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C23 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4046 | -6.4479
118963X | MV/LV Substation GA***963X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.045 | 2 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C17 ex BALLINASLOE | Ballinasloe [T41,T42] | SOMERSET |  | 53.3209 | -8.2427
157310X | MV/LV Substation FO***310X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E11 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 54.0611 | -7.7929
034158 | MV/LV Substation CL***158 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.165 | 0.95 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C18 ex SPA ROAD | Spa Road [T41,T42] | DOON |  | 52.3601 | -7.6588
118180 | MV/LV Substation BA***180 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =35 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.4418 | -8.5107
160179Y | MV/LV Substation BA***179Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C11 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.1618 | -7.4154
164433X | MV/LV Substation CO***433X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =56 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5582 | -9.2555
196236X | MV/LV Substation ST***236X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.137 | 1.34 |  | --> | 0.19 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | E23 ex ATHBOY | Athboy [T423] | NAVAN |  | 53.5323 | -6.959
037596X | MV/LV Substation CA***596X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.17 | 13.05 |  | --> | 0.19 | 0 | 0.005 | 0.182 | 0 |  | --> | C12 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8358 | -8.9775
1614131 | MV/LV Substation UG***4131 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.062 | 11.03 |  | --> | 0.095 | 0 | 0.003 | 0.088 | 0 |  | --> | C27 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.3303 | -9.1708
0624110 | MV/LV Substation ST***4110 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.0565 | -6.2008
039896X | MV/LV Substation AT***896X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.356 | 3.45 |  | --> | 0.38 | 0 | 0 | 0.374 | 0 |  | --> | C13 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2703 | -9.0569
2494084 | MV/LV Substation TA***4084 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C19 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.0986 | -8.004
052909Y | MV/LV Substation PA***909Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =628 kVA | --> | 0.598 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C16 ex NEWBROOK | Newbrook [T42] | MULLINGAR |  | 53.5177 | -7.3596
031385Y | MV/LV Substation BA***385Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0857 | -7.5521
120013 | MV/LV Substation GI***013 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =108 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | E11 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3396 | -7.067
015317Z | MV/LV Substation NE***317Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 12.6 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C18 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2148 | -6.7098
0664535 | MV/LV Substation ES***4535 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.4904 | -6.3697
122969 | MV/LV Substation ME***969 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.098 | 4.18 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C17 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8879 | -6.7129
120449Y | MV/LV Substation DO***449Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C16 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2399 | -6.9631
0124260 | MV/LV Substation CO***4260 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.7332 | -7.1097
0194040 | MV/LV Substation RO***4040 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.22 | 2.18 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =355 kW | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2845 | -9.7064
021754Z | MV/LV Substation LA***754Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.321 | 6.78 |  | --> | 0.38 | 0 | 0 | 0.369 | 0 |  | --> | C36 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.897 | -8.3284
081645X | MV/LV Substation ST***645X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C15 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3484 | -6.4447
251112 | MV/LV Substation LO***112 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E47 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3878 | -8.8457
081224Z | MV/LV Substation CE***224Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =519 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C17 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3368 | -6.3795
082963Y | MV/LV Substation LO***963Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E19 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7846 | -6.6475
158640X | MV/LV Substation CL***640X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex ENNIS NORTH | Ennis North [T41,T42] | ENNIS |  | 52.9607 | -9.0793
017087 | MV/LV Substation MA***087 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.215 | 1.05 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C14 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.45 | -9.0563
108571 | MV/LV Substation BE***571 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.146 | 1.57 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C17 ex BALLYSHANNON | Ballyshannon [T41,T42] | CATHALEENS FALL |  | 54.4776 | -8.0969
012016 | MV/LV Substation KI***016 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.317 | 1.99 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C17 ex GRAIGUE | Graigue [T41,T42] | CARLOW |  | 52.8271 | -6.9377
062074Y | MV/LV Substation CA***074Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.69 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C23 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0077 | -6.4029
031133Y | MV/LV Substation GO***133Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E13 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9513 | -7.732
288072 | MV/LV Substation CH***072 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =219 kVA | --> | 0.38 | 0 | 0.123 | 0.263 | 0 |  | --> | C16 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2289 | -6.1246
014779 | MV/LV Substation TO***779 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C14 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.1978 | -6.7601
026256Z | MV/LV Substation AN***256Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | C17 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7915 | -8.6029
365123 | MV/LV Substation AL***123 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.482 | 13.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex COOKSTOWN | Cookstown [T101,T102] | CARRICKMINES |  | 53.2871 | -6.3754
003473 | MV/LV Substation BA***473 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.075 | 11.58 |  | --> | 0.095 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | C23 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9672 | -6.0988
154433Z | MV/LV Substation CO***433Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C24 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.3986 | -6.3782
503434 | MV/LV Substation MO***434 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.69 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C18 ex NEWTOWNCUNNINGHAM | Newtowncunningham [T41,T42] | LETTERKENNY |  | 55.0307 | -7.4579
003553Y | MV/LV Substation BA***553Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9038 | -6.0483
021742X | MV/LV Substation BL***742X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =143 kVA | --> | 0.19 | 0 | 0.012 | 0.173 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9204 | -8.4978
068839X | MV/LV Substation EA***839X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 6.65 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex EAST WALL ROAD | East Wall Road [T41,T42] | MCDERMOTT |  | 53.357 | -6.2214
0074336 | MV/LV Substation FA***4336 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.14 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3507 | -6.4805
017392X | MV/LV Substation AN***392X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.397 | 1.98 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E14 ex RATHKEALE | Rathkeale [T421,T422] | RATHKEALE |  | 52.5063 | -8.7395
293254 | MV/LV Substation CA***254 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.161 | 2.83 |  | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E13 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6879 | -6.784
065925 | MV/LV Substation ST***925 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =165 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5346 | -6.096
081455X | MV/LV Substation WE***455X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C18 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3521 | -6.3565
065428Z | MV/LV Substation HA***428Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.031 | 0.346 | 0 |  | --> | C22 ex STEPHENSTOWN | Stephenstown [T101,T102] | FINGLAS |  | 53.6135 | -6.2109
007265X | MV/LV Substation BA***265X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.393 | 1.4 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E12 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2455 | -6.3294
405431 | MV/LV Substation PU***431 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 3.03 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex MOVILLE | Moville [T421,T422] | TRILLICK |  | 55.2498 | -7.171
365782X | MV/LV Substation LI***782X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =396 kVA | --> | 0.598 | 0 | 0.037 | 0.5 | 0 |  | --> | C20 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2789 | -6.3696
204488 | MV/LV Substation CA***488 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1246 | -7.4276
093304 | MV/LV Substation GL***304 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =207 kVA | --> | 0.38 | 0 | 0.043 | 0.321 | 0 |  | --> | C16 ex MERVILLE | Merville [T41,T42] | FINGLAS |  | 53.384 | -6.2924
003007 | MV/LV Substation AV***007 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C11 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 52.9148 | -6.2281
053280 | MV/LV Substation DA***280 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C21 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.214 | -7.4094
0284027 | MV/LV Substation BE***4027 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | C13 ex COW CROSS |  |  |  | 51.8765 | -8.3298
062186X | MV/LV Substation VI***186X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.31 | 5.69 |  | --> | 0.598 | 0 | 0.044 | 0 | 0 | Constrained, otherwise capacity available =521 kW | --> | C14 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 53.9992 | -6.4076
039682 | MV/LV Substation CA***682 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C20 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.3066 | -8.915
039633 | MV/LV Substation HA***633 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.056 | 0.33 | 0 |  | --> | C27 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2696 | -9.0421
068572 | MV/LV Substation TY***572 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.388 | 3 |  | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3359 | -6.3258
068667X | MV/LV Substation MA***667X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3452 | -6.2345
032988X | MV/LV Substation DU***988X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1487 | -6.9954
288842 | MV/LV Substation TI***842 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C13 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.26 | -6.2939
005814 | MV/LV Substation CL***814 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 17.8 |  | --> | 0.095 | 0 | 0.02 | 0.079 | 0 |  | --> | E22 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6424 | -6.3434
062243X | MV/LV Substation VA***243X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.081 | 1.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9341 | -6.3859
066196 | MV/LV Substation PO***196 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =562 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4877 | -6.1146
0094217 | MV/LV Substation GR***4217 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.95 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C25 ex TYCOR | Tycor [T41,T42] | WATERFORD |  | 52.2658 | -7.1649
075243 | MV/LV Substation MO***243 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 4.38 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.5129 | -6.2479
028059Y | MV/LV Substation WA***059Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C13 ex COW CROSS |  |  |  | 51.8588 | -8.3146
081208X | MV/LV Substation SC***208X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =329 kVA | --> | 0.38 | 0 | 0.01 | 0.363 | 0 |  | --> | C12 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3327 | -6.356
067718 | MV/LV Substation SR***718 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 13.8 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.613 | -8.5289
016026Z | MV/LV Substation ST***026Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =282 kVA | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3385 | -6.5514
046121X | MV/LV Substation SM***121X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 |  | --> | 0.598 | 0 | 0 | 0.477 | 0 |  | --> | C12 ex FINISKLIN | Finisklin [T41,T42] | SLIGO |  | 54.2755 | -8.4947
216539 | MV/LV Substation MA***539 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =171 kW | --> | C23 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7615 | -8.4132
053464 | MV/LV Substation CL***464 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =238 kVA | --> | 0.38 | 0 | 0.017 | 0.345 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2624 | -7.4825
111037 | MV/LV Substation MA***037 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C15 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.681 | -9.4519
248611X | MV/LV Substation TH***611X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E19 ex KILCOCK | Kilcock [T421,T422] | GRIFFINRATH |  | 53.3941 | -6.6696
136731X | MV/LV Substation CH***731X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =193 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C12 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.639 | -8.2052
0694064 | MV/LV Substation AR***4064 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.91 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C16 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.3192 | -6.3066
2884207 | MV/LV Substation NE***4207 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.041 | 0.04 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C11 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2217 | -6.1113
007917Z | MV/LV Substation CL***917Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 16.12 |  | --> | 0.048 | 0 | 0.006 | 0.043 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3372 | -6.5651
065727 | MV/LV Substation TY***727 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C11 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5335 | -6.1551
007564Y | MV/LV Substation PA***564Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.103 | 0.14 |  | --> | 0.19 | 0 | 0.081 | 0 | 0 | Constrained, otherwise capacity available =116 kW | --> | C15 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3456 | -6.4825
068272 | MV/LV Substation PA***272 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.334 | 7.91 |  | --> | 0.38 | 0 | 0.023 | 0.354 | 0 |  | --> | C24 ex PELLETSTOWN | Pelletstown [T101,T102] | FINGLAS |  | 53.3724 | -6.323
233156 | MV/LV Substation FA***156 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C21 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.1719 | -9.5492
003461Y | MV/LV Substation NA***461Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.155 | 11.58 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C18 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 52.9644 | -6.1454
089053 | MV/LV Substation RI***053 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.1 |  | --> | 0.95 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =888 kW | --> | C14 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.112 | -9.1539
293862X | MV/LV Substation BO***862X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E17 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.8864 | -6.7013
0054312 | MV/LV Substation RO***4312 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 17.8 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E22 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6705 | -6.4051
068491 | MV/LV Substation MO***491 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.168 | 3.38 |  | --> | 0.38 | 0 | 0 | 0.347 | 0 |  | --> | C11 ex MERRION SQUARE | Merrion Square [T41,T42] | RINGSEND |  | 53.3373 | -6.2455
029550 | MV/LV Substation GO***550 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =35 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9145 | -8.0456
063039 | MV/LV Substation FI***039 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8551 | -6.5358
074410 | MV/LV Substation OP***410 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 54.0014 | -8.0772
068944 | MV/LV Substation MO***944 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.028 | 3 |  | --> | 0.38 | 0 | 0 | 0.326 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3415 | -6.2996
293444Y | MV/LV Substation KI***444Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.431 | 0.43 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.756 | -6.8077
050145Y | MV/LV Substation DU***145Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =433 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =571 kW | --> | C17 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.4225 | -7.9359
060489Y | MV/LV Substation SK***489Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.019 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.949 | -6.9929
158639X | MV/LV Substation TH***639X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =352 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C21 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9342 | -9.3394
026265 | MV/LV Substation CA***265 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =124 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.6964 | -8.5141
2884102 | MV/LV Substation CL***4102 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =434 kVA | --> | 0.598 | 0 | 0.014 | 0.5 | 0 |  | --> | C14 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2559 | -6.2022
001140 | MV/LV Substation SW***140 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.456 | 1.55 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.3005 | -6.177
0824220 | MV/LV Substation CH***4220 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =88 kW | --> | E17 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5878 | -6.7424
253850Z | MV/LV Substation RO***850Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =386 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E21 ex GLENAMADDY | Glenamaddy [T422] | ATHLONE |  | 53.6131 | -8.5936
052934Z | MV/LV Substation CO***934Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 1.25 |  | --> | 0.38 | 0 | 0.065 | 0 | 0 | Constrained, otherwise capacity available =327 kW | --> | C17 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.6975 | -7.3627
023569Y | MV/LV Substation CU***569Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C14 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.1601 | -8.2725
288219X | MV/LV Substation RE***219X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.041 | 0.04 | Constrained, otherwise capacity available =147 kVA | --> | 0.19 | 0 | 0 | 0.183 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2112 | -6.1698
127403 | MV/LV Substation TH***403 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =776 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =919 kW | --> | C15 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.675 | -7.8102
007411Y | MV/LV Substation GO***411Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =553 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C19 ex MULGANNON | Mulgannon [T41,T42] | WEXFORD |  | 52.3311 | -6.4509
081057Z | MV/LV Substation LI***057Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =407 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =567 kW | --> | C19 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.352 | -6.3926
156095 | MV/LV Substation BI***095 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex CLONES | Clones [T41,T42] | SHANKILL |  | 54.2182 | -7.1184
055270Y | MV/LV Substation SH***270Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =177 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | E22 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9822 | -7.9193
0664384 | MV/LV Substation TH***4384 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =624 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E17 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.5068 | -6.53
069170 | MV/LV Substation OW***170 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.444 | 0.91 |  | --> | 0.598 | 0 | 0.08 | 0.5 | 0 |  | --> | C21 ex KIMMAGE | Kimmage [T41,T42] | INCHICORE 220KV |  | 53.2966 | -6.2878
154175Z | MV/LV Substation WI***175Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =192 kVA | --> | 0.38 | 0 | 0 | 0.351 | 0 |  | --> | C17 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.4143 | -6.412
0814278 | MV/LV Substation YE***4278 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =380 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3303 | -6.3859
590433 | MV/LV Substation CN***433 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex CONG |  |  |  | 53.5283 | -9.6274
011923X | MV/LV Substation HE***923X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | C17 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6335 | -7.275
069854 | MV/LV Substation LI***854 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =202 kVA | --> | 0.38 | 0 | 0 | 0.352 | 0 |  | --> | C11 ex BALLYBODEN | Ballyboden [T41,T42] | COOKSTOWN |  | 53.2772 | -6.2643
0684586 | MV/LV Substation PR***4586 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex PHIBSBORO | Phibsboro [T41,T42] | FINGLAS |  | 53.3536 | -6.2746
081060Z | MV/LV Substation LI***060Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =488 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =579 kW | --> | C19 ex PALMERSTOWN | Palmerstown [T41,T42] | FINGLAS |  | 53.3532 | -6.3893
071415 | MV/LV Substation ST***415 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =22 kVA | --> | 0.048 | 0 | 0.016 | 0.032 | 0 |  | --> | C22 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.129 | -6.0941
064774X | MV/LV Substation KE***774X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | E16 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6588 | -6.2667
014107 | MV/LV Substation KA***107 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.63 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =595 kW | --> | C17 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1374 | -6.7363
067976Y | MV/LV Substation RH***976Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 13.8 |  | --> | 0.38 | 0 | 0.03 | 0.355 | 0 |  | --> | C13 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.6649 | -8.5985
037018 | MV/LV Substation CA***018 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8351 | -8.9827
249088Z | MV/LV Substation GL***088Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C16 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1464 | -7.8258
053664Y | MV/LV Substation CL***664Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C19 ex CLONMINCH | Clonminch [T41,T422] | THORNSBERRY |  | 53.2624 | -7.4803
162370 | MV/LV Substation CO***370 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C11 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.8266 | -7.4914
139807X | MV/LV Substation RO***807X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8795 | -7.2936
037342 | MV/LV Substation CL***342 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8245 | -8.9684
182517X | MV/LV Substation RA***517X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.8914 | -8.5086
052406Z | MV/LV Substation HA***406Z |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | C23 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5238 | -7.3079
144035 | MV/LV Substation FR***035 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.162 | 2.78 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.7342 | -7.4007
012749X | MV/LV Substation TA***749X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.287 | 2.83 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6973 | -6.9733
154381Z | MV/LV Substation WA***381Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3929 | -6.3705
0654293 | MV/LV Substation OR***4293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =364 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5235 | -6.0957
363698 | MV/LV Substation CA***698 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.353 | 3.25 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E18 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5118 | -9.6747
1274298 | MV/LV Substation RO***4298 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C16 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.7087 | -7.7879
067530X | MV/LV Substation AN***530X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.309 | 6.81 |  | --> | 0.38 | 0 | 0.01 | 0.36 | 0 |  | --> | C03 ex AHANE | Ahane [T102] | AHANE |  | 52.6682 | -8.5303
039587X | MV/LV Substation CA***587X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =301 kVA | --> | 0.38 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =348 kW | --> | C12 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2761 | -8.9716
244482 | MV/LV Substation LI***482 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E21 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1145 | -9.6678
220747X | MV/LV Substation PU***747X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.36 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.1593 | -9.3456
1394439 | MV/LV Substation BE***4439 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C19 ex BAILIEBORO | Bailieboro [T41,T42] | MEATH HILL |  | 53.8756 | -7.0429
067338 | MV/LV Substation CO***338 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C13 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6423 | -8.6761
007954 | MV/LV Substation KI***954 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.115 | 1.4 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2577 | -6.4564
014700X | MV/LV Substation NE***700X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =152 kVA | --> | 0.19 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =139 kW | --> | C14 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.225 | -6.9915
011214X | MV/LV Substation BO***214X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.037 | 0.04 | Constrained, otherwise capacity available =100 kVA | --> | 0.19 | 0 | 0.09 | 0 | 0 | Constrained, otherwise capacity available =109 kW | --> | C19 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5416 | -7.3864
070011 | MV/LV Substation DR***011 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 4.16 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C22 ex NEWMARKET (SR) | Newmarket (sr) [T41,T42] | GLENLARA |  | 52.1314 | -9.0134
3654090 | MV/LV Substation TY***4090 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C21 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2984 | -6.3456
011944Z | MV/LV Substation CO***944Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =582 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =592 kW | --> | C18 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6543 | -7.2532
2654007 | MV/LV Substation DR***4007 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.56 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C18 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 53.9161 | -7.5107
011344 | MV/LV Substation BA***344 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =119 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C16 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.661 | -7.2603
058247 | MV/LV Substation CL***247 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C26 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.9422 | -8.2276
0714090 | MV/LV Substation HO***4090 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 | Constrained, otherwise capacity available =598 kW | --> | C11 ex GREYSTONES | Greystones [T41,T42] | FASSAROE |  | 53.1394 | -6.0832
059630X | MV/LV Substation CR***630X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.996 | -7.4447
0394344 | MV/LV Substation WO***4344 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2579 | -8.9213
090977 | MV/LV Substation EN***977 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.185 | 3.16 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C20 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7398 | -8.9271
003888 | MV/LV Substation RO***888 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =163 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C16 ex RATHDRUM | Rathdrum [T42] | ARKLOW |  | 53.0117 | -6.3251
026326Z | MV/LV Substation CL***326Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C18 ex KINSALE | Kinsale [T41,T42] | BANDON |  | 51.7041 | -8.6242
015331Z | MV/LV Substation AB***331Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =545 kVA | --> | 0.598 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2928 | -6.6808
081368X | MV/LV Substation PE***368X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =363 kVA | --> | 0.598 | 0 | 0.034 | 0.5 | 0 |  | --> | C28 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3323 | -6.3864
039823X | MV/LV Substation HI***823X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.03 |  | --> | 0.598 | 0 | 0.038 | 0.5 | 0 |  | --> | C13 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2715 | -9.0781
160142Y | MV/LV Substation HE***142Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | E11 ex PORTLAOISE |  |  |  | 53.0555 | -7.2245
209011X | MV/LV Substation HY***011X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C14 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.2256 | -7.7011
288250 | MV/LV Substation BA***250 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =265 kVA | --> | 0.38 | 0 | 0 | 0.361 | 0 |  | --> | C20 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2767 | -6.2237
066652Z | MV/LV Substation KI***652Z |  | 20 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =861 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =931 kW | --> | E15 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5114 | -6.4018
025060Y | MV/LV Substation OI***060Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex MILFORD (MWR) | Milford (mwr) [T41] | CHARLEVILLE |  | 52.3365 | -8.8428
127006Z | MV/LV Substation BA***006Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 5.89 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5358 | -7.8736
0534268 | MV/LV Substation MO***4268 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 2.39 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex SRAH | Srah [T41,T42] | THORNSBERRY |  | 53.2883 | -7.5251
293298 | MV/LV Substation PK***298 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =160 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E13 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.8834 | -6.8156
009512Y | MV/LV Substation DE***512Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.193 | 0.53 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C21 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2545 | -7.1127
288290X | MV/LV Substation RO***290X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.34 | 1.16 |  | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C21 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2758 | -6.2284
039269 | MV/LV Substation UN***269 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C17 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2764 | -9.0602
117468X | MV/LV Substation CO***468X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =322 kVA | --> | 0.38 | 0 | 0.007 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | E14 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1707 | -8.606
058513Y | MV/LV Substation SP***513Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.311 | 3 |  | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =346 kW | --> | C21 ex NENAGH | Nenagh [T41,T42] | NENAGH |  | 52.8589 | -8.2186
209799X | MV/LV Substation TU***799X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C12 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.997 | -7.8968
130917 | MV/LV Substation BU***917 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.55 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex EDGEWORTHSTOWN | Edgeworthstown [T421,T422] | RICHMOND |  | 53.7033 | -7.6126
281575Z | MV/LV Substation FO***575Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 5.49 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | C17 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.8714 | -8.4844
001182 | MV/LV Substation NU***182 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =244 kVA | --> | 0.38 | 0 | 0.066 | 0.309 | 0 |  | --> | C18 ex DUNDRUM | Dundrum [T41,T42] | BLACKROCK |  | 53.3074 | -6.2377
081081Z | MV/LV Substation CA***081Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =157 kVA | --> | 0.19 | 0 | 0.008 | 0.178 | 0 |  | --> | C18 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3475 | -6.4293
060751Y | MV/LV Substation DO***751Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 2.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.1296 | -7.1321
253296X | MV/LV Substation CL***296X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 10.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C22 ex CLOON | Cloon [T42,T421] | CLOON |  | 53.4827 | -8.8405
0154238 | MV/LV Substation TH***4238 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0.081 | 0 | 0 | Constrained, otherwise capacity available =314 kW | --> | C11 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2068 | -6.6484
050637X | MV/LV Substation CA***637X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 7.61 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4172 | -7.8987
0524473 | MV/LV Substation KI***4473 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C16 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.6721 | -7.3076
081361Y | MV/LV Substation CE***361Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =812 kVA | --> | 0.95 | 0 | 0.057 | 0 | 0 | Constrained, otherwise capacity available =882 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3374 | -6.5403
070034 | MV/LV Substation CO***034 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.139 | 0.76 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E17 ex RATHMORE | Rathmore [T42,T421] | KNOCKEARAGH |  | 52.0595 | -9.0639
049424 | MV/LV Substation GO***424 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C17 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6908 | -7.851
001490 | MV/LV Substation AM***490 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =91 kVA | --> | 0.19 | 0 | 0.023 | 0.157 | 0 |  | --> | C13 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2584 | -6.1745
012707 | MV/LV Substation OA***707 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =118 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =163 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8461 | -6.9172
016229Z | MV/LV Substation CA***229Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =307 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C22 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3322 | -6.537
053948Y | MV/LV Substation TH***948Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 0.89 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E24 ex BIRR | Birr [T41,T422] | DALLOW |  | 53.1793 | -7.718
046037X | MV/LV Substation HA***037X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.08 | 5.48 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | C11 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2766 | -8.4665
1204307 | MV/LV Substation KI***4307 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.3009 | -6.9196
065446 | MV/LV Substation LO***446 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.095 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5462 | -6.0871
067626 | MV/LV Substation CR***626 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E18 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5745 | -8.6668
021340X | MV/LV Substation MI***340X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C26 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.903 | -8.5531
053968Y | MV/LV Substation AR***968Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =68 kVA | --> | 0.095 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =80 kW | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.2374 | -7.319
0054294 | MV/LV Substation SE***4294 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6775 | -6.2119
156025 | MV/LV Substation FA***025 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =8 kVA | --> | 0.095 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =68 kW | --> | C13 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2472 | -6.9785
120456Y | MV/LV Substation PO***456Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E20 ex EDENDERRY | Edenderry [T421,T422] | BLAKE |  | 53.3601 | -7.2105
0014245 | MV/LV Substation NU***4245 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2578 | -6.1523
064362 | MV/LV Substation CE***362 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex DULEEK | Duleek [T421,T422] | DRYBRIDGE |  | 53.6809 | -6.3854
030120X | MV/LV Substation GA***120X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | E17 ex FOXHOLE | Foxhole [T421,T422] | DUNGARVAN |  | 51.9563 | -7.8595
064598X | MV/LV Substation LI***598X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C17 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7164 | -6.4592
156504Y | MV/LV Substation KI***504Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =166 kVA | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3957 | -7.0059
021253 | MV/LV Substation SH***253 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.38 | 0 | 0.01 | 0.329 | 0 |  | --> | C27 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.902 | -8.4791
288243 | MV/LV Substation KI***243 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =320 kVA | --> | 0.38 | 0 | 0.013 | 0.359 | 0 |  | --> | C11 ex SANDYFORD | Sandyford [T41,T42] | CARRICKMINES |  | 53.2702 | -6.2335
590799X | MV/LV Substation MA***799X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex CONG |  |  |  | 53.5177 | -9.5633
039706 | MV/LV Substation GO***706 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.333 | 11.03 |  | --> | 0.38 | 0 | 0.01 | 0.363 | 0 |  | --> | C24 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2584 | -9.0965
3654068 | MV/LV Substation AR***4068 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =509 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex WHITESTOWN | Whitestown [T41,T42] | COOKSTOWN |  | 53.2789 | -6.3818
063040 | MV/LV Substation MA***040 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =134 kVA | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C18 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8539 | -6.5392
031179Y | MV/LV Substation DU***179Y |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C20 ex COLLIGAN | Colligan [T41,T42] | DUNGARVAN |  | 52.0868 | -7.6288
017244Z | MV/LV Substation LO***244Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex FOYNES | Foynes [T41,T42] | RATHKEALE |  | 52.5948 | -9.1928
067070Z | MV/LV Substation CI***070Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =155 kVA | --> | 0.38 | 0 | 0 | 0.345 | 0 |  | --> | C22 ex GARRYOWEN | Garryowen [T41,T42] | LIMERICK |  | 52.6481 | -8.5742
288034X | MV/LV Substation SA***034X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 |  | --> | 0.19 | 0 | 0.014 | 0.116 | 0 |  | --> | C19 ex CARRICKMINES | Carrickmines [T41,T42] | CARRICKMINES |  | 53.2642 | -6.2155
2074017 | MV/LV Substation MI***4017 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.6145 | -7.6393
293985 | MV/LV Substation TU***985 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | E12 ex BALTINGLASS | Baltinglass [T421,T422] | STRATFORD |  | 52.9654 | -6.6939
001097X | MV/LV Substation LE***097X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.55 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.2992 | -6.1776
037912 | MV/LV Substation TH***912 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C15 ex CAHIRCALLA | Cahircalla [T41,T42] | ENNIS |  | 52.8303 | -8.9905
154561Z | MV/LV Substation AC***561Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C20 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.3928 | -6.3667
081123Z | MV/LV Substation TH***123Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =129 kVA | --> | 0.19 | 0 | 0 | 0.18 | 0 |  | --> | C17 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3557 | -6.4521
0654379 | MV/LV Substation GO***4379 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =602 kVA | --> | 0.598 | 0 | 0.016 | 0 | 0 | Constrained, otherwise capacity available =583 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5254 | -6.0941
192982 | MV/LV Substation FI***982 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 1.56 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =597 kW | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0335 | -8.4037
156004 | MV/LV Substation BE***004 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C13 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2358 | -6.9714
028096 | MV/LV Substation BA***096 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =88 kVA | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C12 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9549 | -8.4205
164002X | MV/LV Substation RO***002X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C12 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.5527 | -9.2589
067300Y | MV/LV Substation SO***300Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.598 | 0 | 0.028 | 0.5 | 0 |  | --> | C14 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6282 | -8.6637
276266 | MV/LV Substation BA***266 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 0.76 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex WOODFORD | Woodford [T41,T42] | KNOCKEARAGH |  | 52.0579 | -9.474
007081Z | MV/LV Substation KN***081Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.025 | 16.12 |  | --> | 0.048 | 0 | 0 | 0.044 | 0 |  | --> | E17 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3424 | -6.5763
214003X | MV/LV Substation LI***003X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =23 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C14 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.7669 | -9.026
132495Y | MV/LV Substation RA***495Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C16 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.1997 | -8.5654
0134064 | MV/LV Substation WI***4064 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0174 | -6.9899
015516 | MV/LV Substation TI***516 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2056 | -6.6209
154318 | MV/LV Substation FO***318 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =296 kVA | --> | 0.38 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =353 kW | --> | C18 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.392 | -6.4061
349081 | MV/LV Substation WA***081 |  | 10 kV | _ | LV | 30 kVA :Pole Substation | 0.03 | --> | 0.03 | 0 | 2.35 |  | --> | 0.028 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =21 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8673 | -8.9818
005182Y | MV/LV Substation GO***182Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.349 | 3.03 |  | --> | 0.38 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C24 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6737 | -6.2967
041857 | MV/LV Substation RO***857 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =161 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | E12 ex DALTON | Dalton [T421,T422] | DALTON |  | 53.7184 | -9.0196
001135X | MV/LV Substation CA***135X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.86 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3076 | -6.192
180875X | MV/LV Substation BE***875X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.282 | 1.4 |  | --> | 0.38 | 0 | 0.072 | 0 | 0 | Constrained, otherwise capacity available =310 kW | --> | C23 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7222 | -6.8797
025223X | MV/LV Substation CR***223X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.4441 | -8.4896
0814395 | MV/LV Substation GR***4395 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E22 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3287 | -6.4654
220036X | MV/LV Substation PU***036X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.138 | 2.33 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E14 ex MOY | Moy [T421,T422] | MOY |  | 54.1841 | -9.2209
250019X | MV/LV Substation CO***019X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.26 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0935 | -8.2199
046349X | MV/LV Substation JO***349X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =921 kVA | --> | 0.95 | 0 | 0.04 | 0.5 | 0 |  | --> | C17 ex CRANMORE | Cranmore [T41,T42] | SLIGO |  | 54.2709 | -8.4769
075870X | MV/LV Substation NE***870X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.096 | 0.58 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E11 ex FERNS | Ferns [T421] | CRANE |  | 52.5964 | -6.5069
009726 | MV/LV Substation IS***726 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.155 | 0.53 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C11 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2532 | -7.0596
122939 | MV/LV Substation VO***939 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 4.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.7982 | -6.7319
093362Z | MV/LV Substation RA***362Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =534 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex GRANGE (DR) | Grange (dr) [T41,T42] | GRANGE (DR) |  | 53.4016 | -6.1496
180988 | MV/LV Substation CA***988 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C14 ex KELLS | Kells [T41,T42] | NAVAN |  | 53.7409 | -6.8621
0084438 | MV/LV Substation GR***4438 |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.2831 | -6.9866
0154115 | MV/LV Substation W.***4115 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.139 | -6.6266
021274Z | MV/LV Substation TI***274Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =498 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex MAYFIELD | Mayfield [T41,T42] | KILBARRY |  | 51.9034 | -8.4278
046154 | MV/LV Substation RO***154 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 5.78 |  | --> | 0.095 | 0 | 0 | 0.091 | 0 |  | --> | C11 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2659 | -8.4872
251250X | MV/LV Substation MU***250X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C30 ex CLAREGALWAY | Claregalway [T42,T421] | GALWAY 110KV |  | 53.3792 | -8.9429
0504525 | MV/LV Substation TR***4525 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 7.61 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C20 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4257 | -7.9031
069134 | MV/LV Substation ST***134 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.423 | 3.34 |  | --> | 0.598 | 0 | 0.035 | 0.5 | 0 |  | --> | C13 ex GREENHILLS | Greenhills [T42] | INCHICORE 220KV |  | 53.3105 | -6.329
365645X | MV/LV Substation GL***645X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =334 kVA | --> | 0.38 | 0 | 0.009 | 0.364 | 0 |  | --> | C15 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2777 | -6.33
110011X | MV/LV Substation RO***011X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.76 |  | --> | 0.048 | 0 | 0.017 | 0 | 0 | Constrained, otherwise capacity available =34 kW | --> | E11 ex KILGARVAN | Kilgarvan [T421] | KNOCKEARAGH |  | 51.9032 | -9.4453
3634049 | MV/LV Substation AS***4049 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.194 | 3.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5477 | -9.4815
377720X | MV/LV Substation SH***720X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =89 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 52.0559 | -9.9422
0234381 | MV/LV Substation GE***4381 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex CASTLELYONS | Castlelyons [T421,T422] | BARRYMORE |  | 52.0614 | -8.3374
011612X | MV/LV Substation PA***612X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =39 kVA | --> | 0.048 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =26 kW | --> | C11 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6582 | -7.2798
049992Y | MV/LV Substation CR***992Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.133 | 0.13 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C18 ex BALLYMAHON | Ballymahon [T41,T42] | ATHLONE |  | 53.5586 | -7.7535
0394255 | MV/LV Substation MA***4255 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.344 | 11.03 |  | --> | 0.38 | 0 | 0.003 | 0.37 | 0 |  | --> | C23 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2756 | -9.1175
026607Y | MV/LV Substation OL***607Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 8.66 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C13 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7335 | -8.7568
160446X | MV/LV Substation FL***446X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =96 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C18 ex PORTARLINGTON | Portarlington [T41,T42] | PORTLAOISE |  | 53.1543 | -7.2155
207371 | MV/LV Substation CL***371 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.6454 | -7.5899
039616 | MV/LV Substation CL***616 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =143 kVA | --> | 0.19 | 0 | 0.018 | 0.169 | 0 |  | --> | C22 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2881 | -9.003
019297 | MV/LV Substation BA***297 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.164 | 1.54 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.259 | -9.715
036797 | MV/LV Substation CH***797 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E18 ex GARRANACANTY | Garranacanty [T421,T422] | TIPPERARY |  | 52.5531 | -8.177
009191 | MV/LV Substation SH***191 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =481 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C30 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2497 | -7.1374
038456X | MV/LV Substation RA***456X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =41 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0731 | -8.7792
0684252 | MV/LV Substation BL***4252 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =558 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex CAMDEN ROW | Camden Row [T41] | FRANCIS STREET |  | 53.3366 | -6.2753
066839Z | MV/LV Substation LE***839Z |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =390 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4885 | -6.1117
366022X | MV/LV Substation CO***022X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.093 | 0.45 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0937 | -9.5847
433403 | MV/LV Substation WO***403 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9341 | -8.7881
210517Y | MV/LV Substation SC***517Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9786 | -6.7163
039769 | MV/LV Substation BR***769 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =479 kVA | --> | 0.598 | 0 | 0.006 | 0.5 | 0 |  | --> | C22 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2895 | -9.0016
120249 | MV/LV Substation AB***249 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BLAKE | Blake [T41,T42] | BLAKE |  | 53.2795 | -6.864
066799 | MV/LV Substation LE***799 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5302 | -6.3117
233283X | MV/LV Substation TE***283X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C25 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2317 | -9.4699
365879X | MV/LV Substation CA***879X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =593 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3121 | -6.3461
005214 | MV/LV Substation CO***214 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.37 | 17.8 |  | --> | 0.38 | 0 | 0.008 | 0.37 | 0 |  | --> | E13 ex BANOGE | Banoge [T121,T122] | BANOGE |  | 52.6462 | -6.232
024708X | MV/LV Substation DO***708X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.201 | 2.14 |  | --> | 0.38 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =335 kW | --> | C13 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2172 | -8.5877
028041 | MV/LV Substation WI***041 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 19.7 |  | --> | 0.598 | 0 | 0.042 | 0.5 | 0 |  | --> | C14 ex COW CROSS | Cow Cross [T102,T41] | COW CROSS |  | 51.8557 | -8.2828
065099 | MV/LV Substation P+***099 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =150 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C19 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5751 | -6.1128
377212 | MV/LV Substation BA***212 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | E12 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9539 | -10.1783
001112X | MV/LV Substation TH***112X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.363 | 19.52 |  | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C13 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2871 | -6.2361
281546Z | MV/LV Substation FA***546Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =501 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =581 kW | --> | C13 ex DENNEHYS CROSS | Dennehys Cross [T41,T42] | TRABEG |  | 51.8902 | -8.5073
0674028 | MV/LV Substation SH***4028 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =389 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C14 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6616 | -8.6937
237161X | MV/LV Substation GR***161X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex KILSARAN | Kilsaran [T42] | DRYBRIDGE |  | 53.8696 | -6.3929
0164006 | MV/LV Substation TE***4006 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =118 kVA | --> | 0.19 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =155 kW | --> | C21 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3853 | -6.54
206955 | MV/LV Substation LA***955 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.078 | 2.76 |  | --> | 0.095 | 0 | 0 | 0.092 | 0 |  | --> | E14 ex BANGOR ERRIS | Bangor Erris [T421] | BELLACORICK |  | 54.2401 | -9.7252
069692 | MV/LV Substation BA***692 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3141 | -6.346
066250Z | MV/LV Substation CA***250Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4731 | -6.2374
009772 | MV/LV Substation BA***772 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 8.16 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2978 | -7.1161
025983 | MV/LV Substation KI***983 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 2.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E11 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.4362 | -8.7042
011211Z | MV/LV Substation KE***211Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.037 | 0.04 | Constrained, otherwise capacity available =108 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C16 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.5329 | -7.2819
1584174 | MV/LV Substation CA***4174 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C21 ex ENNISTYMON | Ennistymon [T41,T42] | ENNIS |  | 52.9203 | -9.3415
059311X | MV/LV Substation GO***311X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =69 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C14 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.993 | -7.3643
258933 | MV/LV Substation TH***933 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 1.86 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex CREESLOUGH | Creeslough [T421] | ARDNAGAPPARY |  | 55.177 | -7.9289
099422X | MV/LV Substation DR***422X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.935 | -7.6844
012495Y | MV/LV Substation 4 ***495Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =328 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C11 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8453 | -6.9029
220650X | MV/LV Substation AN***650X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 1.36 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex CROSSMOLINA | Crossmolina [T41,T42] | MOY |  | 54.0354 | -9.3244
039153 | MV/LV Substation CO***153 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.182 | 3.45 |  | --> | 0.38 | 0 | 0.031 | 0.326 | 0 |  | --> | C19 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.2756 | -9.0692
077413 | MV/LV Substation BR***413 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E25 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.6157 | -8.7295
5904087 | MV/LV Substation CR***4087 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 1.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E17 ex CONG | Cong [T421,T422] | CLOON |  | 53.5422 | -9.2122
122429 | MV/LV Substation LI***429 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 4.18 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9045 | -6.7981
176260Y | MV/LV Substation FL***260Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.333 | 18.78 |  | --> | 0.38 | 0 | 0.1 | 0.301 | 0 |  | --> | E17 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | HARTNETTS CROSS |  | 51.9454 | -9.1599
037341Y | MV/LV Substation AB***341Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.367 | 13.05 |  | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C20 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8459 | -8.9835
012431Y | MV/LV Substation GL***431Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.145 | 2.83 |  | --> | 0.19 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E12 ex BAGENALSTOWN | Bagenalstown [T421,T422] | CARLOW |  | 52.6972 | -6.9675
049014Z | MV/LV Substation CO***014Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.213 | 0.21 | Constrained, otherwise capacity available =370 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | E21 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7627 | -7.835
015336Z | MV/LV Substation CH***336Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =98 kVA | --> | 0.19 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =158 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2907 | -6.6844
184237 | MV/LV Substation CA***237 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.409 | 3.38 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =578 kW | --> | C18 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1266 | -6.7494
365609X | MV/LV Substation GR***609X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0.028 | 0.343 | 0 |  | --> | C22 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.275 | -6.3324
074038X | MV/LV Substation PO***038X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9391 | -8.1173
0684441 | MV/LV Substation VE***4441 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =500 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex CLONTARF | Clontarf [T42] | FINGLAS |  | 53.3751 | -6.199
0384037 | MV/LV Substation KI***4037 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex GORT | Gort [T41,T42] | ENNIS |  | 53.0656 | -8.7683
1444027 | MV/LV Substation FO***4027 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex CASTLECOMER | Castlecomer [T41,T42] | BALLYRAGGET |  | 52.7533 | -7.3073
265656 | MV/LV Substation EN***656 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.066 | 0.07 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | E15 ex BALLYCONNELL | Ballyconnell [T421,T422] | GORTAWEE |  | 54.1202 | -7.5755
052585Y | MV/LV Substation RO***585Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.175 | 1.25 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C17 ex LOUGHANALLA | Loughanalla [T41,T42] | MULLINGAR |  | 53.7088 | -7.3523
0774058 | MV/LV Substation MA***4058 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.38 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | E16 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.556 | -8.7945
004352Y | MV/LV Substation ME***352Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 18.08 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.7875 | -6.1732
007045Z | MV/LV Substation MU***045Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.088 | 1.4 |  | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =86 kW | --> | E20 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2429 | -6.546
082615Y | MV/LV Substation PH***615Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =83 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.602 | -6.6183
281807Z | MV/LV Substation HI***807Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =469 kVA | --> | 0.598 | 0 | 0.041 | 0.5 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.8847 | -8.5739
154096Z | MV/LV Substation BR***096Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0.005 | 0.366 | 0 |  | --> | C41 ex COLLEGE PARK | College Park [T101,T102,T103] | COLLEGE PARK |  | 53.4045 | -6.4107
078016 | MV/LV Substation LA***016 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =130 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C12 ex CHARLESTOWN | Charlestown [T41] | TONROE |  | 53.9635 | -8.7918
029276Y | MV/LV Substation CA***276Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =763 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MIDLETON | Midleton [T101,T102] | MIDLETON |  | 51.9119 | -8.1786
049869 | MV/LV Substation DR***869 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.21 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8216 | -7.5325
081133Z | MV/LV Substation ST***133Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.002 | 0.185 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3148 | -6.401
368261X | MV/LV Substation FA***261X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C15 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7465 | -8.6266
204084X | MV/LV Substation FO***084X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =189 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | E17 ex BUNCRANA | Buncrana [T421,T422] | TRILLICK |  | 55.1235 | -7.1967
002068X | MV/LV Substation ST***068X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.2 | 2.36 |  | --> | 0.19 | 0 | 0 | 0.19 | 0 |  | --> | C20 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1864 | -6.1247
153225 | MV/LV Substation TH***225 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E18 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7194 | -8.4992
021596Z | MV/LV Substation RO***596Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C12 ex RIVERSTOWN | Riverstown [T41,T42] | KILBARRY |  | 51.9505 | -8.4215
2494153 | MV/LV Substation CA***4153 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C25 ex KILCLOHER | Kilcloher [T41,T42] | DUNGARVAN |  | 52.1556 | -7.756
281420 | MV/LV Substation MO***420 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.052 | 4.3 |  | --> | 0.095 | 0 | 0.013 | 0.079 | 0 |  | --> | C11 ex RINGASKIDDY 110KV | Ringaskiddy 110kv [T42] | BARNAHELY |  | 51.8411 | -8.3419
032821 | MV/LV Substation GA***821 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1752 | -7.036
054649 | MV/LV Substation BA***649 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E12 ex ABBEYLEIX | Abbeyleix [T422] | PORTLAOISE |  | 52.9314 | -7.3136
032001 | MV/LV Substation PO***001 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.38 | 0 | 0.044 | 0 | 0 | Constrained, otherwise capacity available =315 kW | --> | C16 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1628 | -7.1506
009420Y | MV/LV Substation AY***420Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =362 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C16 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2472 | -7.0851
059447X | MV/LV Substation KI***447X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E19 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.983 | -7.4141
093193 | MV/LV Substation RI***193 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =318 kVA | --> | 0.38 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C31 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.3981 | -6.2124
010458 | MV/LV Substation KI***458 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C16 ex GRAIGUENAMANAGH | Graiguenamanagh [T41,T42] | KILKENNY |  | 52.5123 | -7.0453
2104233 | MV/LV Substation DR***4233 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9689 | -6.6945
015529Z | MV/LV Substation BA***529Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.3026 | -6.6995
2664018 | MV/LV Substation CA***4018 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.3058 | -7.2577
0164003 | MV/LV Substation CA***4003 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3779 | -6.5544
001030X | MV/LV Substation LI***030X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.093 | 1.16 |  | --> | 0.19 | 0 | 0 | 0.175 | 0 |  | --> | C17 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.2929 | -6.195
122990 | MV/LV Substation TH***990 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.258 | 4.18 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =360 kW | --> | C19 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.8717 | -6.7877
157197 | MV/LV Substation KI***197 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.099 | 1.55 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E13 ex CARRIGALLEN | Carrigallen [T421] | CARRICK ON SHANNON |  | 53.9786 | -7.6334
067114Y | MV/LV Substation MO***114Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =554 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C19 ex CAHERDAVIN | Caherdavin [T41,T42] | ARDNACRUSHA |  | 52.6739 | -8.646
054732X | MV/LV Substation RA***732X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =99 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 52.9594 | -7.2282
009137 | MV/LV Substation RE***137 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =328 kW | --> | C18 ex WATERFORD IND EST | Waterford Ind Est [T41,T42,T44] | BUTLERSTOWN |  | 52.2465 | -7.1424
265890 | MV/LV Substation LO***890 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.56 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C17 ex KILLESHANDRA | Killeshandra [T41,T42] | GORTAWEE |  | 54.0732 | -7.5881
0624293 | MV/LV Substation WU***4293 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.375 | 1.03 |  | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =363 kW | --> | C15 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9696 | -6.4145
009153 | MV/LV Substation RI***153 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | E12 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.2356 | -7.0616
009412Y | MV/LV Substation LI***412Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C16 ex GRANGE (SR) | Grange (sr) [T41,T42] | BUTLERSTOWN |  | 52.2463 | -7.0841
060261Y | MV/LV Substation BE***261Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 2.57 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C17 ex ERRIGAL | Errigal [T41,T422] | SHANKILL |  | 54.0815 | -7.08
050349Y | MV/LV Substation SI***349Y |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =716 kVA | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =910 kW | --> | C23 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.425 | -7.9422
032437X | MV/LV Substation BA***437X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =77 kW | --> | C19 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.198 | -7.1171
0634112 | MV/LV Substation ST***4112 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C15 ex STICKILLEN | Stickillen [T41,T42] | DRYBRIDGE |  | 53.8496 | -6.5415
039670 | MV/LV Substation OA***670 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =306 kVA | --> | 0.38 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =345 kW | --> | C18 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2751 | -8.929
006090 | MV/LV Substation KI***090 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.095 | 4.38 |  | --> | 0.095 | 0 | 0 | 0.094 | 0 |  | --> | E14 ex CRANE | Crane [T122] | CRANE |  | 52.5107 | -6.6447
288163 | MV/LV Substation SH***163 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.041 | 0.04 | Constrained, otherwise capacity available =722 kVA | --> | 0.95 | 0 | 0.012 | 0.5 | 0 |  | --> | C13 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2061 | -6.112
127631X | MV/LV Substation OU***631X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0.086 | 5.89 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | C20 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5141 | -7.8872
0014086 | MV/LV Substation FR***4086 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.55 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C20 ex MONKSTOWN | Monkstown [T41,T42] | BLACKROCK |  | 53.3016 | -6.1836
017010 | MV/LV Substation SO***010 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.295 | 1.05 |  | --> | 0.38 | 0 | 0.002 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C15 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.449 | -9.0604
260874 | MV/LV Substation NE***874 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.67 |  | --> | 0.048 | 0 | 0.005 | 0.043 | 0 |  | --> | E18 ex NEWPORT | Newport [T421] | CARROWBEG |  | 53.8807 | -9.5476
0694173 | MV/LV Substation PE***4173 |  | 10 kV | _ | LV | 1000 kVA :Kiosk Substation | 1 | --> | 1 | 0.5 | 17.78 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C24 ex RINGSEND | Ringsend [T101,T102] | POOLBEG |  | 53.3409 | -6.2131
149442 | MV/LV Substation C ***442 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =72 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | C11 ex DONEGAL | Donegal [T41,T42] | CATHALEENS FALL |  | 54.6544 | -8.1386
3684044 | MV/LV Substation KI***4044 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =190 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C12 ex BALLYHAUNIS | Ballyhaunis [T41,T42] | DALTON |  | 53.7745 | -8.7651
1964014 | MV/LV Substation PU***4014 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex ATHBOY | Athboy [T42] | NAVAN |  | 53.6134 | -6.8712
055755 | MV/LV Substation MO***755 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.108 | 0.18 |  | --> | 0.19 | 0 | 0.051 | 0 | 0 | Constrained, otherwise capacity available =139 kW | --> | C16 ex TOOMEVARA | Toomevara [T42] | NENAGH |  | 52.8793 | -7.9578
046135X | MV/LV Substation BR***135X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.028 | 5.48 |  | --> | 0.095 | 0 | 0 | 0.085 | 0 |  | --> | C15 ex BALLYTIVNAN | Ballytivnan [T41,T42] | SLIGO |  | 54.2773 | -8.454
065083 | MV/LV Substation ST***083 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =536 kVA | --> | 0.598 | 0 | 0.026 | 0 | 0 | Constrained, otherwise capacity available =566 kW | --> | C15 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5294 | -6.0949
008492Z | MV/LV Substation WO***492Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.19 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =164 kW | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3875 | -6.9298
082601 | MV/LV Substation LI***601 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | E11 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6037 | -6.5868
365497X | MV/LV Substation MC***497X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =388 kVA | --> | 0.38 | 0 | 0 | 0.378 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3294 | -6.3542
093191 | MV/LV Substation RI***191 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =364 kW | --> | C31 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.3996 | -6.214
019187X | MV/LV Substation GA***187X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.18 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C18 ex BALLYRICKARD | Ballyrickard [T41,T42] | TRALEE |  | 52.2707 | -9.7091
011728 | MV/LV Substation KI***728 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.68 | -7.18
266388 | MV/LV Substation DR***388 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =153 kVA | --> | 0.19 | 0 | 0.022 | 0 | 0 | Constrained, otherwise capacity available =167 kW | --> | E17 ex CARNDONAGH | Carndonagh [T421,T422] | TRILLICK |  | 55.2974 | -7.2548
049149Z | MV/LV Substation CL***149Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.159 | 0.21 |  | --> | 0.19 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | E21 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.7629 | -7.8318
365560 | MV/LV Substation HO***560 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =559 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex SEMPERIT | Semperit [T41,T42,T43] | GRANGE CASTLE |  | 53.3287 | -6.3562
136825 | MV/LV Substation TH***825 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =176 kVA | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.6766 | -7.9924
065239Z | MV/LV Substation FE***239Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =26 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E23 ex BALTRASNA | Baltrasna [T121,T122] | BALTRASNA |  | 53.623 | -6.397
015457 | MV/LV Substation DU***457 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =32 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2072 | -6.572
068455 | MV/LV Substation DO***455 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 11.14 |  | --> | 0.598 | 0 | 0.005 | 0.5 | 0 |  | --> | C28 ex CABRA | Cabra [T101,T102] | FINGLAS |  | 53.372 | -6.3089
039080 | MV/LV Substation BO***080 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =271 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =362 kW | --> | C13 ex MONEENAGEISHA | Moneenageisha [T41,T42] | GALWAY 110KV |  | 53.2825 | -9.0374
142537X | MV/LV Substation GL***537X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E23 ex ATHENRY | Athenry [T423] | GALWAY 110KV |  | 53.2954 | -8.6742
068934 | MV/LV Substation BR***934 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.182 | 4.6 |  | --> | 0.38 | 0 | 0 | 0.349 | 0 |  | --> | C18 ex KINGSBRIDGE | Kingsbridge [T41,T42] | INCHICORE 220KV |  | 53.3481 | -6.3078
281413 | MV/LV Substation RO***413 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =366 kVA | --> | 0.38 | 0 | 0.016 | 0.364 | 0 |  | --> | C17 ex BISHOPSTOWN | Bishopstown [T41,T42] | KILBARRY |  | 51.887 | -8.5772
066662Z | MV/LV Substation BO***662Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =330 kVA | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | E17 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4436 | -6.2319
039124 | MV/LV Substation GA***124 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0.023 | 0 | 0 | Constrained, otherwise capacity available =354 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2505 | -8.9702
039052 | MV/LV Substation CL***052 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.33 | 3.45 |  | --> | 0.38 | 0 | 0 | 0.37 | 0 |  | --> | C19 ex TRIMMS LANE | Trimms Lane [T41,T42] | SALTHILL |  | 53.275 | -9.0669
068507X | MV/LV Substation RA***507X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =569 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3533 | -6.251
099277X | MV/LV Substation PA***277X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.097 | 2.96 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.999 | -7.6615
099476 | MV/LV Substation RO***476 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C15 ex CULLION | Cullion [T41,T42] | LETTERKENNY |  | 54.9489 | -7.6376
377451 | MV/LV Substation CA***451 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =76 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E15 ex GURRANEBANE | Gurranebane [T421,T422] | OUGHTRAGH |  | 51.9506 | -10.2132
062905Y | MV/LV Substation DE***905Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.33 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C17 ex DUNDALK | Dundalk [T41,T42] | DUNDALK |  | 54.0007 | -6.4161
345073X | MV/LV Substation WA***073X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =492 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E17 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2539 | -8.2979
111767Z | MV/LV Substation CU***767Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =373 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =376 kW | --> | C16 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6875 | -9.4367
001053X | MV/LV Substation BR***053X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.366 | 13.42 |  | --> | 0.38 | 0 | 0 | 0.375 | 0 |  | --> | C18 ex POTTERY ROAD | Pottery Road [T101,T102] | CARRICKMINES |  | 53.2843 | -6.1127
066278Z | MV/LV Substation CL***278Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | E16 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5137 | -6.4065
012398Y | MV/LV Substation LI***398Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =359 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =367 kW | --> | C24 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8604 | -6.8627
005939 | MV/LV Substation WA***939 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =293 kVA | --> | 0.38 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =352 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.682 | -6.2944
062727Y | MV/LV Substation FA***727Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E15 ex JENKINSTOWN | Jenkinstown [T421,T422] | DUNDALK |  | 54.0399 | -6.3873
012880 | MV/LV Substation MO***880 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0.027 | 0 | 0 | Constrained, otherwise capacity available =350 kW | --> | C11 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8441 | -6.8983
066799Z | MV/LV Substation CO***799Z |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =89 kVA | --> | 0.095 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =75 kW | --> | E15 ex BATTER LANE TEMPORARY | Batter Lane Temporary 38kv [T421] | GLASMORE |  | 53.5154 | -6.1944
176412 | MV/LV Substation LE***412 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | E12 ex MACROOM | Macroom [T422] | MACROOM |  | 51.9381 | -8.8724
074819 | MV/LV Substation BR***819 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =62 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C14 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9527 | -8.0958
365142X | MV/LV Substation SY***142X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C13 ex BALLYMOUNT | Ballymount [T41,T42] | INCHICORE 220KV |  | 53.3171 | -6.349
074865 | MV/LV Substation JA***865 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.434 | 8.5 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =571 kW | --> | E14 ex ARIGNA | Arigna [T121] | ARIGNA |  | 54.0474 | -8.0444
062591Y | MV/LV Substation RA***591Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.118 | 3.12 |  | --> | 0.19 | 0 | 0.053 | 0 | 0 | Constrained, otherwise capacity available =139 kW | --> | C21 ex MARSHES | Marshes [T41,T42] | DUNDALK |  | 53.9643 | -6.3761
099025 | MV/LV Substation AR***025 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.298 | 2.96 |  | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C11 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9577 | -7.7193
0224156 | MV/LV Substation CL***4156 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 4.55 |  | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C21 ex MALLOW | Mallow [T41,T42] | MALLOW |  | 52.1516 | -8.6283
074372X | MV/LV Substation FI***372X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C13 ex CARRICK ON SHANNON | Carrick On Shannon [T41,T42] | CARRICK ON SHANNON |  | 53.9384 | -8.1085
036923X | MV/LV Substation LA***923X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.037 | 1.4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E17 ex KILROSS ROAD | Kilross Road [T421] | TIPPERARY |  | 52.4681 | -8.2764
165996 | MV/LV Substation CO***996 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =149 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =344 kW | --> | C11 ex CLONAKILTY | Clonakilty [T41,T42] | DUNMANWAY |  | 51.6494 | -8.862
0664417 | MV/LV Substation FL***4417 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =341 kVA | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C13 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.4424 | -6.2846
082824Y | MV/LV Substation BO***824Y |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =493 kVA | --> | 0.598 | 0 | 0.035 | 0 | 0 | Constrained, otherwise capacity available =554 kW | --> | E12 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6375 | -6.6519
081411Y | MV/LV Substation AV***411Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =480 kVA | --> | 0.598 | 0 | 0.039 | 0 | 0 | Constrained, otherwise capacity available =549 kW | --> | C12 ex LEIXLIP | Leixlip [T41,T42] | GRIFFINRATH |  | 53.3697 | -6.4848
023694X | MV/LV Substation CA***694X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =29 kVA | --> | 0.048 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C13 ex CURRAGLASS | Curraglass [T41] | BARRYMORE |  | 52.1041 | -8.0709
0124150 | MV/LV Substation FL***4150 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8194 | -6.8694
027307 | MV/LV Substation BA***307 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 3.16 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C22 ex ENNISKEANE | Enniskeane [T41,T42] | BANDON |  | 51.7357 | -8.9545
152834 | MV/LV Substation KE***834 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =27 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E33 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.5526 | -8.344
156752Y | MV/LV Substation EM***752Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =199 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E14 ex EMYVALE | Emyvale [T422] | LISDRUM |  | 54.3404 | -6.9584
349337 | MV/LV Substation BU***337 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.369 | 2.35 |  | --> | 0.38 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C15 ex KILTIMAGH | Kiltimagh [T41] | CASTLEBAR |  | 53.8594 | -8.9905
016220Z | MV/LV Substation GR***220Z |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =468 kVA | --> | 0.598 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =539 kW | --> | E60 ex GRANGE CASTLE |  |  |  | 53.3013 | -6.4776
117491X | MV/LV Substation KI***491X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E14 ex COLLOONEY | Collooney [T421,T422] | SLIGO |  | 54.1814 | -8.4943
156820 | MV/LV Substation KI***820 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2513 | -7.1412
0684509 | MV/LV Substation RO***4509 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.2 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C26 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3422 | -6.2493
093086Y | MV/LV Substation WR***086Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =486 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C11 ex SUTTON | Sutton [T41,T42] | GRANGE (DR) |  | 53.3896 | -6.0746
250694 | MV/LV Substation RA***694 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C27 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.1736 | -8.3321
015566Z | MV/LV Substation D1***566Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.35 | 12.6 |  | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C22 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2328 | -6.6744
093287Z | MV/LV Substation TI***287Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 12.96 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex ARTANE | Artane [T101,T102] | FINGLAS |  | 53.3848 | -6.211
015251Y | MV/LV Substation LA***251Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C17 ex NAAS | Naas [T41,T42] | KILTEEL |  | 53.2061 | -6.7265
022449X | MV/LV Substation MI***449X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =36 kW | --> | C15 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1293 | -8.6641
255526 | MV/LV Substation CA***526 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.068 | 2.09 |  | --> | 0.19 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =157 kW | --> | C17 ex KILCAR | Kilcar [T41] | BINBANE |  | 54.6586 | -8.6337
1394217 | MV/LV Substation CO***4217 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8637 | -7.3012
345687 | MV/LV Substation BL***687 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.19 | 0 | 0.015 | 0.155 | 0 |  | --> | E15 ex MANORHAMILTON | Manorhamilton [T422] | SLIGO |  | 54.2911 | -7.8778
089004 | MV/LV Substation DO***004 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.337 | 9.1 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | E19 ex ARDNAREE | Ardnaree [T42,T421] | MOY |  | 54.1171 | -9.1344
021078Y | MV/LV Substation CO***078Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =253 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C12 ex FAIRHILL | Fairhill [T42] | KILBARRY |  | 51.9015 | -8.4711
0084027 | MV/LV Substation GL***4027 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.205 | 0.2 | Constrained, otherwise capacity available =331 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | E17 ex BEALISTOWN | Bealistown [T421,T422] | GREAT ISLAND |  | 52.1651 | -6.8833
013688Y | MV/LV Substation CH***688Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =370 kVA | --> | 0.38 | 0 | 0.016 | 0.364 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9901 | -6.977
009036 | MV/LV Substation ME***036 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.308 | 3.82 |  | --> | 0.38 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =357 kW | --> | C17 ex WATERFORD | Waterford [T41,T42] | WATERFORD |  | 52.2628 | -7.1275
062050Z | MV/LV Substation AL***050Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 5.69 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C19 ex RAMPARTS | Ramparts [T41,T42] | DUNDALK |  | 54.0024 | -6.3959
059173Y | MV/LV Substation RO***173Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =147 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C20 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 54.0043 | -7.3472
043008 | MV/LV Substation ST***008 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.297 | 0.43 |  | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C18 ex SWINFORD | Swinford [T41,T42] | CASTLEBAR |  | 53.9404 | -8.9518
054166Z | MV/LV Substation HE***166Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 52.9531 | -7.1954
156052 | MV/LV Substation RO***052 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =365 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C19 ex DRUMBEAR | Drumbear [T41,T42] | LISDRUM |  | 54.2399 | -6.987
117979 | MV/LV Substation BA***979 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 0.32 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BALLYMOTE | Ballymote [T41] | SLIGO |  | 54.0835 | -8.5197
068054 | MV/LV Substation KE***054 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.312 | 3 |  | --> | 0.598 | 0 | 0.058 | 0.5 | 0 |  | --> | C37 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3399 | -6.3134
192824 | MV/LV Substation FI***824 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.192 | 1.56 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C13 ex DERRYBEG | Derrybeg [T41,T42] | ARDNAGAPPARY |  | 55.0107 | -8.2509
021013X | MV/LV Substation PA***013X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =594 kVA | --> | 0.598 | 0 | 0.012 | 0.5 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9222 | -8.493
154673 | MV/LV Substation RO***673 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =552 kVA | --> | 0.598 | 0 | 0.05 | 0 | 0 | Constrained, otherwise capacity available =551 kW | --> | C25 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4042 | -6.3539
0524169 | MV/LV Substation SA***4169 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.363 | 10.9 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C14 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5365 | -7.3511
0014135 | MV/LV Substation CH***4135 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =1000 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2439 | -6.1416
003461 | MV/LV Substation BA***461 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.098 | 18.08 |  | --> | 0.19 | 0 | 0.016 | 0.176 | 0 |  | --> | C18 ex ARKLOW | Arklow [T101,T102] | ARKLOW |  | 52.8816 | -6.0989
021868X | MV/LV Substation GL***868X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =115 kVA | --> | 0.19 | 0 | 0.033 | 0.154 | 0 |  | --> | C21 ex KILBARRY | Kilbarry [T101,T43] | KILBARRY |  | 51.9174 | -8.4836
015499X | MV/LV Substation SE***499X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =36 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.223 | -6.5496
0154279 | MV/LV Substation CI***4279 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C16 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2485 | -6.5959
109132 | MV/LV Substation FA***132 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =360 kVA | --> | 0.38 | 0 | 0.086 | 0.311 | 0 |  | --> | C18 ex SHANNON | Shannon [T41,T42] | DRUMLINE |  | 52.7075 | -8.9009
008806Y | MV/LV Substation CA***806Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =195 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3823 | -6.9548
055736 | MV/LV Substation MO***736 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =28 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | E20 ex ROSCREA | Roscrea [T41,T42] | IKERRIN |  | 52.9432 | -7.6624
059520Y | MV/LV Substation LI***520Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =556 kW | --> | C14 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9926 | -7.3626
0824453 | MV/LV Substation BE***4453 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.5914 | -6.7055
005033 | MV/LV Substation BA***033 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =316 kVA | --> | 0.38 | 0 | 0.128 | 0 | 0 | Constrained, otherwise capacity available =274 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6834 | -6.2885
034781X | MV/LV Substation TI***781X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.154 | 5.88 |  | --> | 0.19 | 0 | 0.018 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C13 ex ARDGEEHA | Ardgeeha [T41,T42] | DOON |  | 52.361 | -7.6841
015723 | MV/LV Substation TU***723 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.2882 | -6.621
021066 | MV/LV Substation RO***066 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 6.78 |  | --> | 0.095 | 0 | 0 | 0.095 | 0 |  | --> | C41 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9034 | -8.4212
3654046 | MV/LV Substation RI***4046 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0 | 0.371 | 0 |  | --> | C14 ex OLDBAWN | Oldbawn [T41,T42] | COOKSTOWN |  | 53.2814 | -6.3754
0154397 | MV/LV Substation R4***4397 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =400 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C17 ex SALLINS | Sallins [T41,T42] | GRIFFINRATH |  | 53.3012 | -6.6945
0234283 | MV/LV Substation LI***4283 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =272 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C13 ex FERMOY NORTH | Fermoy North [T41,T42] | BARRYMORE |  | 52.139 | -8.2658
064535 | MV/LV Substation MO***535 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =95 kVA | --> | 0.095 | 0 | 0.03 | 0 | 0 | Constrained, otherwise capacity available =72 kW | --> | E18 ex JULIANSTOWN | Julianstown [T421,T422] | DRYBRIDGE |  | 53.6674 | -6.3686
2044094 | MV/LV Substation CA***4094 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.02 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex BALLYMACARRY | Ballymacarry [T421] | TRILLICK |  | 55.0748 | -7.4544
021025X | MV/LV Substation IR***025X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =541 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.932 | -8.5662
052224X | MV/LV Substation CA***224X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 10.9 |  | --> | 0.095 | 0 | 0.006 | 0.089 | 0 |  | --> | C13 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5706 | -7.3263
021094 | MV/LV Substation SU***094 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =383 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9348 | -8.5704
288284X | MV/LV Substation BA***284X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =157 kVA | --> | 0.19 | 0 | 0 | 0.184 | 0 |  | --> | C18 ex LOUGHLINSTOWN | Loughlinstown [T41,T42] | CARRICKMINES |  | 53.2349 | -6.1797
144850X | MV/LV Substation SW***850X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 2.78 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex BALLYRAGGET | Ballyragget [T421,T422] | BALLYRAGGET |  | 52.745 | -7.3186
293010 | MV/LV Substation NU***010 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.43 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.721 | -6.6898
005794 | MV/LV Substation CR***794 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =185 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6781 | -6.3024
004289Y | MV/LV Substation HA***289Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.04 | 0.45 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C15 ex KILMAGIG | Kilmagig [T42] | ARKLOW |  | 52.8475 | -6.358
012400Y | MV/LV Substation CA***400Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.19 | 0 | 0.048 | 0 | 0 | Constrained, otherwise capacity available =132 kW | --> | C11 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8494 | -6.9053
017110Z | MV/LV Substation CL***110Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.174 | 4.23 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C13 ex CHURCHTOWN | Churchtown [T41] | RATHKEALE |  | 52.4564 | -9.0458
136602 | MV/LV Substation LI***602 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.7442 | -8.0915
0544421 | MV/LV Substation TI***4421 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E12 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 52.9701 | -7.2116
150365X | MV/LV Substation HE***365X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.173 | 3.96 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8381 | -7.9311
253037 | MV/LV Substation CU***037 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.17 | 10.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =186 kW | --> | C22 ex CLOON | Cloon [T42,T421] | CLOON |  | 53.5166 | -8.8452
0324042 | MV/LV Substation BA***4042 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =321 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C25 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1624 | -7.1606
154565Z | MV/LV Substation PH***565Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =312 kVA | --> | 0.38 | 0 | 0.016 | 0.356 | 0 |  | --> | C22 ex MACETOWN | Macetown [T101,T102] | MACETOWN |  | 53.3981 | -6.4377
081573X | MV/LV Substation SI***573X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =103 kVA | --> | 0.19 | 0 | 0.05 | 0.139 | 0 |  | --> | C13 ex BALGADDY | Balgaddy [T41,T42] | GRANGE CASTLE |  | 53.3465 | -6.453
0674377 | MV/LV Substation CO***4377 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =627 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C13 ex DOCK ROAD | Dock Road [T41,T42] | LIMERICK |  | 52.6299 | -8.6733
0154445 | MV/LV Substation RY***4445 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex JOHNSTOWN | Johnstown [T41,T42] | KILTEEL |  | 53.2327 | -6.5793
013091Z | MV/LV Substation MO***091Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0.003 | 0.368 | 0 |  | --> | E62 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0345 | -6.8982
109109 | MV/LV Substation P ***109 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 0.38 | Constrained, otherwise capacity available =394 kVA | --> | 0.38 | 0 | 0 | 0.379 | 0 |  | --> | C17 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.708 | -8.8919
1644113 | MV/LV Substation BA***4113 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C11 ex SKIBBEREEN | Skibbereen [T41,T42] | DUNMANWAY |  | 51.597 | -9.2668
066690Z | MV/LV Substation GA***690Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =267 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =361 kW | --> | C19 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4524 | -6.155
013687Y | MV/LV Substation CA***687Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.049 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C26 ex ATHY | Athy [T101,T102] | ATHY |  | 53.0002 | -7.003
066391X | MV/LV Substation FA***391X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =496 kVA | --> | 0.598 | 0 | 0.08 | 0 | 0 | Constrained, otherwise capacity available =521 kW | --> | E11 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4865 | -6.147
066151Y | MV/LV Substation FI***151Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =365 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C19 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4527 | -6.1547
365004Y | MV/LV Substation CO***004Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.305 | -6.4956
2934378 | MV/LV Substation AN***4378 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.1 | 0.43 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | E15 ex TULLOW | Tullow [T421,T422] | CARLOW |  | 52.8058 | -6.7352
001016X | MV/LV Substation SE***016X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.301 | 1.16 |  | --> | 0.38 | 0 | 0 | 0.366 | 0 |  | --> | C16 ex MOUNT MERRION | Mount Merrion [T41,T42] | CARRICKMINES |  | 53.3073 | -6.2044
0654102 | MV/LV Substation DU***4102 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =491 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =586 kW | --> | C14 ex BALBRIGGAN | Balbriggan [T42] | GLASMORE |  | 53.6038 | -6.1856
066666X | MV/LV Substation ST***666X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | E11 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.452 | -6.3039
253057 | MV/LV Substation P ***057 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =117 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =178 kW | --> | C13 ex TUAM SOUTH | Tuam South [T42] | CLOON |  | 53.5156 | -8.8538
093532Z | MV/LV Substation CL***532Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C22 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.3932 | -6.3
039605 | MV/LV Substation RI***605 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =557 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C28 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2893 | -9.025
066325X | MV/LV Substation CR***325X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =128 kVA | --> | 0.19 | 0 | 0.037 | 0 | 0 | Constrained, otherwise capacity available =152 kW | --> | E15 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5082 | -6.4028
109060 | MV/LV Substation JU***060 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0.38 |  | --> | 0.598 | 0 | 0 | 0.48 | 0 |  | --> | C22 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.6933 | -8.9209
0934053 | MV/LV Substation TH***4053 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =339 kVA | --> | 0.598 | 0 | 0.011 | 0.5 | 0 |  | --> | C28 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4071 | -6.1776
052062X | MV/LV Substation CL***062X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =136 kVA | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C17 ex DELVIN | Delvin [T41,T42] | MULLINGAR |  | 53.6639 | -7.0144
0814433 | MV/LV Substation LO***4433 |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | E21 ex ADAMSTOWN | Adamstown [T121,T122] | INCHICORE 220KV |  | 53.3325 | -6.4182
350481 | MV/LV Substation DR***481 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.142 | 1.57 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | C15 ex BUNDORAN | Bundoran [T41,T42] | CATHALEENS FALL |  | 54.4723 | -8.3211
049148Z | MV/LV Substation SL***148Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.166 | 0.21 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8187 | -7.7612
127516Y | MV/LV Substation MC***516Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 5.89 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C14 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5345 | -7.8968
216117X | MV/LV Substation DR***117X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C23 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7591 | -8.4102
064117 | MV/LV Substation GL***117 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =286 kVA | --> | 0.38 | 0 | 0.033 | 0 | 0 | Constrained, otherwise capacity available =340 kW | --> | C20 ex DRYBRIDGE | Drybridge [T41,T42] | DRYBRIDGE |  | 53.7197 | -6.3432
109124 | MV/LV Substation RU***124 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.381 | 0.38 | Constrained, otherwise capacity available =399 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C22 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7124 | -8.9069
0194108 | MV/LV Substation RE***4108 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.047 | 0.05 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =188 kW | --> | C14 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2873 | -9.6955
238695 | MV/LV Substation AK***695 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =40 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E12 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6285 | -9.2177
014114Z | MV/LV Substation GR***114Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =154 kVA | --> | 0.19 | 0 | 0.021 | 0 | 0 | Constrained, otherwise capacity available =168 kW | --> | C13 ex ATHGARVAN | Athgarvan [T41,T44] | NEWBRIDGE |  | 53.162 | -6.8112
006549Y | MV/LV Substation SH***549Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.306 | 3.12 |  | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =365 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5114 | -6.5945
015649Z | MV/LV Substation ST***649Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.379 | 12.6 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C12 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.211 | -6.6595
046241X | MV/LV Substation RU***241X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.273 | 5.78 |  | --> | 0.38 | 0 | 0.022 | 0.346 | 0 |  | --> | C11 ex OAKFIELD | Oakfield [T41,T42] | SLIGO |  | 54.2589 | -8.4738
062614Y | MV/LV Substation RE***614Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.72 |  | --> | 0.598 | 0 | 0.028 | 0 | 0 | Constrained, otherwise capacity available =572 kW | --> | C15 ex COES ROAD | Coes Road [T41,T42] | DUNDALK |  | 54.006 | -6.367
039297 | MV/LV Substation GA***297 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.127 | 11.03 |  | --> | 0.19 | 0 | 0.01 | 0.172 | 0 |  | --> | C32 ex SALTHILL | Salthill [T101,T102] | SALTHILL |  | 53.2796 | -9.0784
071747 | MV/LV Substation PR***747 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 5.58 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C11 ex KILCOOLE | Kilcoole [T41,T42] | FASSAROE |  | 53.0692 | -6.1102
0114514 | MV/LV Substation DU***4514 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C15 ex TALBOTS INCH | Talbots Inch [T41,T42] | KILKENNY |  | 52.6661 | -7.2712
037634 | MV/LV Substation GA***634 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 13.05 |  | --> | 0.095 | 0 | 0.021 | 0.076 | 0 |  | --> | C19 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8449 | -8.9488
109094 | MV/LV Substation CL***094 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.342 | 0.38 |  | --> | 0.38 | 0 | 0 | 0.372 | 0 |  | --> | C15 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7019 | -8.8841
077025 | MV/LV Substation BL***025 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =73 kVA | --> | 0.095 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =84 kW | --> | E16 ex PATRICKSWELL | Patrickswell [T421,T422] | LIMERICK |  | 52.5668 | -8.7944
068161X | MV/LV Substation TE***161X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =478 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3548 | -6.2577
3654114 | MV/LV Substation BE***4114 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3028 | -6.3885
021562X | MV/LV Substation CO***562X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.491 | 6.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C35 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8957 | -8.3474
011790Z | MV/LV Substation PL***790Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.045 | 5.05 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex MCDONAGH | Mcdonagh [T41,T42] | KILKENNY |  | 52.6645 | -7.2276
132416Y | MV/LV Substation CO***416Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =59 kVA | --> | 0.095 | 0 | 0.061 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C17 ex LOUGHREA | Loughrea [T41,T42] | SOMERSET |  | 53.2048 | -8.5888
2484006 | MV/LV Substation RA***4006 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 0.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E33 ex TRIM | Trim [T421] | NAVAN |  | 53.4828 | -6.8099
023128 | MV/LV Substation BA***128 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex CURRAGLASS | Curraglass [T41] | BARRYMORE |  | 52.1125 | -8.1367
068652X | MV/LV Substation JA***652X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =740 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3524 | -6.2548
161843X | MV/LV Substation RA***843X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =42 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C13 ex SPIDDAL |  |  |  | 53.2493 | -9.3006
015666X | MV/LV Substation GI***666X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.07 | 12.6 |  | --> | 0.095 | 0 | 0 | 0.091 | 0 |  | --> | C23 ex MONREAD | Monread [T101,T102] | MONREAD |  | 53.2336 | -6.7209
139433X | MV/LV Substation NO***433X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 4 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C17 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8517 | -7.2012
249409X | MV/LV Substation FE***409X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex LISMORE | Lismore [T41,T42] | DUNGARVAN |  | 52.1851 | -7.9807
127494 | MV/LV Substation BA***494 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C14 ex TEMPLEMORE | Templemore [T41,T42] | IKERRIN |  | 52.7574 | -7.7306
038532 | MV/LV Substation TU***532 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =81 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E15 ex GORT | Gort [T41,T42] | ENNIS |  | 53.1353 | -8.7863
008839 | MV/LV Substation MO***839 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =33 kVA | --> | 0.048 | 0 | 0.02 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | C14 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.4088 | -6.937
0684579 | MV/LV Substation HA***4579 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0 | 0 | Constrained, otherwise capacity available =551 kVA | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C12 ex CAMDEN ROW | Camden Row [T41] | FRANCIS STREET |  | 53.3338 | -6.2641
182240 | MV/LV Substation AJ***240 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =310 kVA | --> | 0.38 | 0 | 0.06 | 0 | 0 | Constrained, otherwise capacity available =323 kW | --> | C11 ex SCARIFF | Scariff [T42] | ENNIS |  | 52.8975 | -8.5442
067004 | MV/LV Substation CR***004 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =156 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C11 ex MOYLISH | Moylish [T41,T42] | ARDNACRUSHA |  | 52.6814 | -8.651
081307X | MV/LV Substation WO***307X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =291 kVA | --> | 0.38 | 0 | 0.034 | 0.34 | 0 |  | --> | C15 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.352 | -6.465
0214221 | MV/LV Substation IN***4221 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9012 | -8.3782
014506 | MV/LV Substation MA***506 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.022 | 0.63 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1242 | -6.8808
003496Y | MV/LV Substation CL***496Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 11.58 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C19 ex BALLYBEG | Ballybeg [T101,T102] | CARRICKMINES |  | 53.0179 | -6.0675
4334058 | MV/LV Substation CL***4058 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C12 ex BALLAGHADERREEN | Ballaghaderreen [T41,T42] | TONROE |  | 53.8303 | -8.6309
1274491 | MV/LV Substation ST***4491 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex LOUGHTAGALLA | Loughtagalla [T41,T42] | THURLES |  | 52.6929 | -7.7649
093090 | MV/LV Substation PI***090 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.241 | 2.86 |  | --> | 0.38 | 0 | 0.062 | 0.312 | 0 |  | --> | C19 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3932 | -6.273
1844084 | MV/LV Substation BR***4084 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.0647 | -6.7013
042721X | MV/LV Substation CL***721X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8599 | -9.2462
067369 | MV/LV Substation LU***369 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.038 | 13.8 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.5777 | -8.5196
025083 | MV/LV Substation GO***083 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =70 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C12 ex KILMALLOCK | Kilmallock [T41,T42] | CHARLEVILLE |  | 52.3952 | -8.5696
0624294 | MV/LV Substation WU***4294 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.392 | 1.03 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C15 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9659 | -6.4144
009230Y | MV/LV Substation PA***230Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.53 | Constrained, otherwise capacity available =611 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C17 ex MANOR STREET | Manor Street [T41,T42] | WATERFORD |  | 52.2576 | -7.1099
037270 | MV/LV Substation KE***270 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.041 | 13.05 |  | --> | 0.048 | 0 | 0.016 | 0.034 | 0 |  | --> | C19 ex ENNIS | Ennis [T101,T102] | ENNIS |  | 52.8311 | -8.88
0054283 | MV/LV Substation MI***4283 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 3.03 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =585 kW | --> | C17 ex RAMSTOWN | Ramstown [T41,T42] | CRANE |  | 52.6697 | -6.2885
042391 | MV/LV Substation GR***391 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8626 | -9.1906
068072 | MV/LV Substation IS***072 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 20.78 |  | --> | 0.598 | 0 | 0.016 | 0.5 | 0 |  | --> | C21 ex HEUSTON SQUARE | Heuston Square [T101,T102] | INCHICORE 220KV |  | 53.3481 | -6.3119
068381X | MV/LV Substation TO***381X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 9.02 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex MISERY HILL | Misery Hill [T101,T102] | POOLBEG |  | 53.3464 | -6.253
012494Y | MV/LV Substation 4 ***494Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C11 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8456 | -6.9012
2884159 | MV/LV Substation DY***4159 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.16 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex BREWERY ROAD | Brewery Road [T41,T42] | CARRICKMINES |  | 53.2782 | -6.2135
019006X | MV/LV Substation BL***006X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.277 | 1.54 |  | --> | 0.38 | 0 | 0.065 | 0 | 0 | Constrained, otherwise capacity available =315 kW | --> | C22 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.2556 | -9.737
156608X | MV/LV Substation SL***608X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 2.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C18 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.176 | -6.99
111652Y | MV/LV Substation PO***652Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =24 kVA | --> | 0.048 | 0 | 0.036 | 0 | 0 | Constrained, otherwise capacity available =17 kW | --> | C16 ex BANTRY | Bantry [T41,T42] | BALLYLICKY |  | 51.6752 | -9.4724
167037Y | MV/LV Substation BL***037Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9323 | -8.5704
0934009 | MV/LV Substation M5***4009 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =164 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C17 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.397 | -6.3305
081394Z | MV/LV Substation RO***394Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.38 | 0 | 0 | 0.348 | 0 |  | --> | C14 ex CLONDALKIN | Clondalkin [T41,T42,T44] | INCHICORE 220KV |  | 53.3284 | -6.3954
192032X | MV/LV Substation IO***032X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.19 | 1.7 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E15 ex GWEEDORE | Gweedore [T421] | ARDNAGAPPARY |  | 55.0259 | -8.1466
009046 | MV/LV Substation RO***046 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.236 | 8.16 |  | --> | 0.38 | 0 | 0.013 | 0 | 0 | Constrained, otherwise capacity available =347 kW | --> | C12 ex MOUNT MISERY | Mount Misery [T41,T42] | WATERFORD |  | 52.2672 | -7.1007
063929 | MV/LV Substation LY***929 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =198 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =185 kW | --> | C19 ex BALLYBAILIE | Ballybailie [T41,T42] | DUNDALK |  | 53.8644 | -6.5498
122880 | MV/LV Substation EN***880 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 4.18 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C18 ex KINGSCOURT | Kingscourt [T41,T42] | MEATH HILL |  | 53.9006 | -6.8083
001074X | MV/LV Substation KE***074X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.175 | 4.01 |  | --> | 0.19 | 0 | 0.01 | 0.179 | 0 |  | --> | C15 ex BALLINCLEA | Ballinclea [T41] | CHERRYWOOD |  | 53.2615 | -6.1202
014605Z | MV/LV Substation CU***605Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.63 |  | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C16 ex KILCULLEN | Kilcullen [T41,T42,T424] | STRATFORD |  | 53.1176 | -6.8242
007634Y | MV/LV Substation CL***634Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.235 | 16.12 |  | --> | 0.38 | 0 | 0.05 | 0.32 | 0 |  | --> | E14 ex WEXFORD | Wexford [T121,T122] | WEXFORD |  | 52.3313 | -6.4955
066190Y | MV/LV Substation OM***190Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =398 kVA | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.4169 | -6.2395
024784X | MV/LV Substation AR***784X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.092 | 2.14 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C14 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2479 | -8.6705
009519 | MV/LV Substation EL***519 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.168 | 3.76 |  | --> | 0.19 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =156 kW | --> | E15 ex BELVIEW | Belview [T421,T422] | WATERFORD |  | 52.2662 | -7.0723
093317 | MV/LV Substation PR***317 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =173 kVA | --> | 0.19 | 0 | 0 | 0.186 | 0 |  | --> | C22 ex UNIDARE | Unidare [T41,T42] | FINGLAS |  | 53.3944 | -6.3194
069812 | MV/LV Substation RA***812 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 0.87 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C17 ex GARVILLE AVENUE | Garville Avenue [T42] | MILLTOWN (DR) |  | 53.3214 | -6.2666
039335 | MV/LV Substation CO***335 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =566 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C27 ex GALWAY 110KV | Galway 110kv [T102,T103] | GALWAY 110KV |  | 53.2701 | -9.0464
093112 | MV/LV Substation FE***112 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =148 kVA | --> | 0.38 | 0 | 0.037 | 0.317 | 0 |  | --> | C16 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3988 | -6.2005
006088Y | MV/LV Substation RE***088Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.079 | 3.12 |  | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.4979 | -6.5788
066497Z | MV/LV Substation CO***497Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.19 | 0 | 0 | 0.172 | 0 |  | --> | C19 ex KILMORE | Kilmore [T101,T102,T103] | FINGLAS |  | 53.416 | -6.2404
0684291 | MV/LV Substation ST***4291 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =574 kVA | --> | 0.598 | 0 | 0.076 | 0.5 | 0 |  | --> | C12 ex GLOUCESTER PLACE | Gloucester Place [T41,T42] | MCDERMOTT |  | 53.3531 | -6.2527
066725X | MV/LV Substation KI***725X |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =126 kVA | --> | 0.19 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4267 | -6.1704
0684352 | MV/LV Substation MA***4352 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C19 ex MARROWBONE LANE |  |  |  | 53.3395 | -6.2861
0214224 | MV/LV Substation RI***4224 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.381 | 6.78 |  | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C18 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.9071 | -8.383
340105X | MV/LV Substation TO***105X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =628 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C16 ex DUNGLOE | Dungloe [T41,T42] | ARDNAGAPPARY |  | 54.98 | -8.4398
153757 | MV/LV Substation BO***757 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =34 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E14 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.7887 | -8.3792
008009X | MV/LV Substation CO***009X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =85 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C20 ex KNOCKMULLEN | Knockmullen [T42,T421] | GREAT ISLAND |  | 52.3195 | -6.8864
109113 | MV/LV Substation WE***113 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.199 | 0.38 |  | --> | 0.38 | 0 | 0 | 0.359 | 0 |  | --> | C17 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7118 | -8.8886
118591Y | MV/LV Substation PA***591Y |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =182 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | E18 ex CREAGH | Creagh [T421,T422] | ATHLONE |  | 53.4746 | -8.5006
069741 | MV/LV Substation CH***741 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.391 | 4.47 |  | --> | 0.598 | 0 | 0.037 | 0.5 | 0 |  | --> | C13 ex TEMPLEOGUE | Templeogue [T41,T42] | MILLTOWN (DR) |  | 53.2962 | -6.2934
157207X | MV/LV Substation WI***207X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.357 | 2.03 |  | --> | 0.38 | 0 | 0.024 | 0 | 0 | Constrained, otherwise capacity available =356 kW | --> | E15 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 54.0504 | -7.7919
067256 | MV/LV Substation RO***256 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =377 kW | --> | E16 ex CRATLOE | Cratloe [T421,T422] | ARDNACRUSHA |  | 52.687 | -8.7202
068497 | MV/LV Substation GL***497 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =392 kVA | --> | 0.598 | 0 | 0.016 | 0.5 | 0 |  | --> | C12 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3867 | -6.246
255250X | MV/LV Substation WA***250X |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | E18 ex KILLYBEGS | Killybegs [T422] | BINBANE |  | 54.6293 | -8.4455
162595 | MV/LV Substation CL***595 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.026 | 0.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C12 ex ROSSGEIR | Rossgeir [T41,T42] | LETTERKENNY |  | 54.794 | -7.5533
109137 | MV/LV Substation FA***137 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 0.38 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | C14 ex RINEANNA | Rineanna [T41,T42] | DRUMLINE |  | 52.7688 | -8.9066
0684418 | MV/LV Substation SP***4418 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C22 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3484 | -6.2355
0014236 | MV/LV Substation BE***4236 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.16 |  | --> | 0.38 | 0 | 0 | 0.38 | 0 |  | --> | C21 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2633 | -6.1818
0494498 | MV/LV Substation IR***4498 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.389 | 1.31 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =378 kW | --> | C17 ex ROOSKY | Roosky [T41] | RICHMOND |  | 53.7767 | -8.0983
0154096 | MV/LV Substation KC***4096 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =77 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | E13 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1386 | -6.6276
021220 | MV/LV Substation BL***220 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =367 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9287 | -8.5692
042037Y | MV/LV Substation EL***037Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8046 | -9.128
176103 | MV/LV Substation MI***103 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 18.78 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | E13 ex HARTNETTS CROSS | Hartnetts Cross [T121,T422] | HARTNETTS CROSS |  | 51.8665 | -9.0365
066683X | MV/LV Substation WE***683X |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =342 kVA | --> | 0.598 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =559 kW | --> | E21 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5286 | -6.303
0684656 | MV/LV Substation TH***4656 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 14.34 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C41 ex NORTH QUAYS | North Quays [T101,T102,T103] | POOLBEG |  | 53.3519 | -6.2322
001237 | MV/LV Substation AL***237 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.276 | 1.23 |  | --> | 0.38 | 0 | 0.053 | 0.323 | 0 |  | --> | C16 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2825 | -6.1189
0654267 | MV/LV Substation RA***4267 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C11 ex LOUGHSHINNY | Loughshinny [T41,T42] | GLASMORE |  | 53.5295 | -6.1539
281563X | MV/LV Substation SH***563X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex KILMONEY | Kilmoney [T41,T42] | TRABEG |  | 51.8083 | -8.4248
256116X | MV/LV Substation BR***116X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.047 | 1.28 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C22 ex CASTLEREA | Castlerea [T41,T42] | CARRICK ON SHANNON |  | 53.787 | -8.2394
066757Z | MV/LV Substation ST***757Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =355 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C13 ex MALAHIDE | Malahide [T41,T42] | GLASMORE |  | 53.4255 | -6.1758
066393Z | MV/LV Substation TH***393Z |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =174 kVA | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | E13 ex GLASMORE | Glasmore [T421,T422] | GLASMORE |  | 53.4738 | -6.2336
093032 | MV/LV Substation SH***032 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =370 kVA | --> | 0.598 | 0 | 0.088 | 0.497 | 0 |  | --> | C11 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3901 | -6.2428
050654Y | MV/LV Substation PR***654Y |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =332 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C17 ex ATHLONE | Athlone [T41,T42] | ATHLONE |  | 53.424 | -7.9386
074398X | MV/LV Substation TH***398X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.179 | 2.03 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =176 kW | --> | E16 ex MOHILL | Mohill [T421,T422] | CARRICK ON SHANNON |  | 53.9296 | -8.0025
365768X | MV/LV Substation ES***768X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =84 kVA | --> | 0.095 | 0 | 0 | 0.093 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2455 | -6.4761
011573Y | MV/LV Substation CA***573Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.037 | 0.04 | Constrained, otherwise capacity available =71 kVA | --> | 0.095 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =87 kW | --> | C11 ex CALLAN | Callan [T41,T42] | KILKENNY |  | 52.554 | -7.3788
0814018 | MV/LV Substation HA***4018 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =606 kVA | --> | 0.598 | 0 | 0.011 | 0 | 0 | Constrained, otherwise capacity available =587 kW | --> | C18 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.3333 | -6.5333
0664519 | MV/LV Substation ED***4519 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.82 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex COOLOCK | Coolock [T41,T42] | FINGLAS |  | 53.389 | -6.1823
233110X | MV/LV Substation AH***110X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =311 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | C23 ex CASTLEISLAND | Castleisland [T41,T42] | TRALEE |  | 52.2647 | -9.4523
042860 | MV/LV Substation KE***860 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.031 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8462 | -9.169
029410 | MV/LV Substation CA***410 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =64 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | E12 ex CARRIGSHANE | Carrigshane [T422] | MIDLETON |  | 51.9034 | -8.0411
027569X | MV/LV Substation DU***569X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.198 | 7.79 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C13 ex DUNMANWAY | Dunmanway [T422,T43] | DUNMANWAY |  | 51.722 | -9.2119
066911 | MV/LV Substation RA***911 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =196 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | E12 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5012 | -6.4273
0684200 | MV/LV Substation RO***4200 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =523 kVA | --> | 0.598 | 0 | 0.049 | 0.5 | 0 |  | --> | C16 ex WHITEHALL | Whitehall [T41] | FINGLAS |  | 53.3717 | -6.2446
0934311 | MV/LV Substation WI***4311 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C14 ex SANTRY | Santry [T41,T42] | FINGLAS |  | 53.3935 | -6.2396
066449Z | MV/LV Substation BR***449Z |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =304 kVA | --> | 0.38 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | E16 ex ASHBOURNE | Ashbourne [T421,T422] | FINGLAS |  | 53.5159 | -6.4108
007067X | MV/LV Substation CA***067X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.143 | 0.14 | Constrained, otherwise capacity available =358 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =374 kW | --> | C12 ex CARRIGLAWN | Carriglawn [T41,T42] | WEXFORD |  | 52.3455 | -6.4529
184014 | MV/LV Substation ST***014 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.149 | 3.38 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =183 kW | --> | C13 ex CASTLEBLAYNEY | Castleblayney [T41,T42] | DUNDALK |  | 54.1203 | -6.7459
099579X | MV/LV Substation GO***579X |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 5.45 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =594 kW | --> | C13 ex GORTLEE | Gortlee [T41,T42] | LETTERKENNY |  | 54.971 | -7.7353
064361 | MV/LV Substation SE***361 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0.009 | 0 | 0 | Constrained, otherwise capacity available =39 kW | --> | C21 ex TERMONFECKIN ROAD | Termonfeckin Road [T41,T42] | DRYBRIDGE |  | 53.7598 | -6.2495
0074435 | MV/LV Substation BA***4435 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.4 | 1.4 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2662 | -6.3868
093338X | MV/LV Substation HI***338X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =376 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | C17 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.386 | -6.1746
019761 | MV/LV Substation BA***761 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.54 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =596 kW | --> | C20 ex BALLYARD | Ballyard [T41,T42] | TRALEE |  | 52.262 | -9.6981
015870X | MV/LV Substation TH***870X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =44 kVA | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =42 kW | --> | E14 ex BLESSINGTON | Blessington [T421,T422] | KILTEEL |  | 53.1181 | -6.5845
019647 | MV/LV Substation LI***647 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.047 | 0.05 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C12 ex BALLYBEGGAN | Ballybeggan [T43,T44] | TRALEE |  | 52.2704 | -9.6161
081025Y | MV/LV Substation WH***025Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =93 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C20 ex CELBRIDGE | Celbridge [T41,T42] | GRIFFINRATH |  | 53.2998 | -6.5759
009001 | MV/LV Substation RO***001 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.262 | 3.82 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =358 kW | --> | C20 ex WATERFORD | Waterford [T41,T42] | WATERFORD |  | 52.2626 | -7.124
062311X | MV/LV Substation AR***311X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.072 | 1.03 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =91 kW | --> | C18 ex LITTLE MILLS | Little Mills [T41] | DUNDALK |  | 53.9227 | -6.4019
216033X | MV/LV Substation DC***033X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =94 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =94 kW | --> | C26 ex GLENTIES | Glenties [T41,T42] | BINBANE |  | 54.7936 | -8.3045
007499X | MV/LV Substation BA***499X |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.089 | 1.4 |  | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =85 kW | --> | E13 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2247 | -6.3544
180975X | MV/LV Substation CL***975X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.2 | 3.27 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex LLOYD | Lloyd [T41,T42] | NAVAN |  | 53.7406 | -6.9162
281468 | MV/LV Substation NO***468 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 7.88 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C23 ex LIBERTY STREET | Liberty Street [T101,T102] | LIBERTY STREET |  | 51.8981 | -8.4685
011639Z | MV/LV Substation HI***639Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.16 | 2.8 |  | --> | 0.19 | 0 | 0.019 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C12 ex PURCELLS INCH | Purcells Inch [T41,T42] | KILKENNY |  | 52.591 | -7.1759
0424007 | MV/LV Substation BO***4007 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.034 | 1.93 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | C18 ex TURLOUGH ROAD | Turlough Road [T41,T42] | CASTLEBAR |  | 53.8498 | -9.157
0584207 | MV/LV Substation AS***4207 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | C17 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.925 | -8.1694
0144197 | MV/LV Substation WH***4197 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =302 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =366 kW | --> | C15 ex MORRISTOWN | Morristown [T41,T42] | NEWBRIDGE |  | 53.1892 | -6.8112
024679X | MV/LV Substation BR***679X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.255 | 2.14 |  | --> | 0.38 | 0 | 0.053 | 0 | 0 | Constrained, otherwise capacity available =320 kW | --> | C14 ex BUTTEVANT | Buttevant [T41,T42] | MALLOW |  | 52.2707 | -8.732
0234035 | MV/LV Substation LO***4035 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =78 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =92 kW | --> | C16 ex COOLCARRON | Coolcarron [T41,T42] | BARRYMORE |  | 52.134 | -8.2754
033469X | MV/LV Substation HU***469X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =3 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =37 kW | --> | C18 ex BALLYHALE | Ballyhale [T42,T421] | KILKENNY |  | 52.4524 | -7.2503
0814366 | MV/LV Substation PA***4366 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =375 kVA | --> | 0.38 | 0 | 0 | 0.377 | 0 |  | --> | E54 ex GRANGE CASTLE | Grange Castle [T124] | INCHICORE 220KV |  | 53.3309 | -6.4094
363162 | MV/LV Substation TU***162 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.046 | 3.25 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BALLYBUNION | Ballybunion [T421,T422] | TRIEN |  | 52.5407 | -9.6102
119776X | MV/LV Substation CU***776X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =180 kVA | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =184 kW | --> | C16 ex KANTURK | Kanturk [T41,T42] | GLENLARA |  | 52.1881 | -8.9132
033005 | MV/LV Substation BA***005 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =236 kVA | --> | 0.38 | 0 | 0.014 | 0.059 | 0 | Constrained, otherwise capacity available =346 kW | --> | C16 ex CREGG ROAD | Cregg Road [T41,T42] | BALLYDINE |  | 52.3487 | -7.3949
0684177 | MV/LV Substation HA***4177 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 7.2 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C25 ex TRINITY | Trinity [T101,T102] | POOLBEG |  | 53.3451 | -6.2454
007460Y | MV/LV Substation SA***460Y |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.5 | 1.4 |  | --> | 0.598 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =582 kW | --> | E18 ex KILLINICK | Killinick [T421,T422] | WEXFORD |  | 52.2741 | -6.3875
099431X | MV/LV Substation ES***431X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 2.96 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9567 | -7.7138
052115Z | MV/LV Substation LI***115Z |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =120 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =179 kW | --> | E18 ex BALLINDERRY | Ballinderry [T41,T422] | MULLINGAR |  | 53.5193 | -7.2873
137282X | MV/LV Substation TO***282X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.178 | 2 |  | --> | 0.19 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C19 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.396 | -9.8306
0214366 | MV/LV Substation EV***4366 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 6.78 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C13 ex CASTLEVIEW | Castleview [T101,T102] | CASTLEVIEW |  | 51.8978 | -8.3595
001005X | MV/LV Substation HE***005X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.352 | 1.23 |  | --> | 0.38 | 0 | 0 | 0.373 | 0 |  | --> | C23 ex SALLYNOGGIN ROAD | Sallynoggin Road [T41,T42] | CHERRYWOOD |  | 53.2783 | -6.1057
209665 | MV/LV Substation MI***665 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =319 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C19 ex MILFORD (NR) | Milford (nr) [T41,T42] | LETTERKENNY |  | 55.077 | -7.6809
017017 | MV/LV Substation KI***017 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.279 | 1.05 |  | --> | 0.38 | 0 | 0.053 | 0 | 0 | Constrained, otherwise capacity available =324 kW | --> | C15 ex NEWCASTLEWEST | Newcastlewest [T41,T42] | RATHKEALE |  | 52.4447 | -9.0471
075111 | MV/LV Substation BU***111 |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.157 | 1.13 |  | --> | 0.19 | 0 | 0.053 | 0 | 0 | Constrained, otherwise capacity available =145 kW | --> | E12 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.656 | -6.6449
3654158 | MV/LV Substation MO***4158 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =49 kVA | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C12 ex SAGGART | Saggart [T41,T42] | GRANGE CASTLE |  | 53.2806 | -6.5022
0754064 | MV/LV Substation BA***4064 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 4.38 |  | --> | 0.048 | 0 | 0 | 0.048 | 0 |  | --> | E18 ex CRANE | Crane [T122] | CRANE |  | 52.4783 | -6.3008
137536 | MV/LV Substation BA***536 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.143 | 2 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =182 kW | --> | C19 ex CAUSEWAY | Causeway [T41,T42] | TRALEE |  | 52.3906 | -9.8269
081445Y | MV/LV Substation BE***445Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =230 kVA | --> | 0.38 | 0 | 0.04 | 0 | 0 | Constrained, otherwise capacity available =326 kW | --> | C20 ex MONEYCOOLEY | Moneycooley [T41,T42,T44] | GRIFFINRATH |  | 53.3744 | -6.6004
069478 | MV/LV Substation LA***478 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 3 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C31 ex INCHICORE CENTRAL | Inchicore Central [T43,T45] | INCHICORE 220KV |  | 53.3279 | -6.3333
050217X | MV/LV Substation RO***217X |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.364 | 7.61 |  | --> | 0.38 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C14 ex GARRYCASTLE | Garrycastle [T41,T42] | ATHLONE |  | 53.4269 | -7.9337
244795X | MV/LV Substation AR***795X |  | 20 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =558 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =589 kW | --> | E16 ex MILLTOWN (SR) | Milltown (sr) [T421,T422] | OUGHTRAGH |  | 52.1408 | -9.7215
093303Z | MV/LV Substation SA***303Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =396 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =380 kW | --> | C31 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.4025 | -6.2214
099317 | MV/LV Substation TA***317 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.131 | 2.96 |  | --> | 0.19 | 0 | 0.015 | 0 | 0 | Constrained, otherwise capacity available =169 kW | --> | C21 ex BALLYRAINE | Ballyraine [T41,T42] | LETTERKENNY |  | 54.9597 | -7.694
210478Y | MV/LV Substation DR***478Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =100 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =95 kW | --> | C20 ex CARRICKMACROSS | Carrickmacross [T41,T42] | MEATH HILL |  | 53.9887 | -6.7851
075041 | MV/LV Substation SW***041 |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.05 | 1.13 |  | --> | 0.095 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =79 kW | --> | E12 ex BUNCLODY | Bunclody [T421,T422] | CRANE |  | 52.6562 | -6.6645
013910Y | MV/LV Substation TH***910Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.121 | 0.12 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.029 | 0.344 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9824 | -6.9753
005015Y | MV/LV Substation CL***015Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =379 kVA | --> | 0.38 | 0 | 0.012 | 0 | 0 | Constrained, otherwise capacity available =368 kW | --> | C11 ex GARDEN CITY | Garden City [T41,T42] | ARKLOW |  | 52.6769 | -6.2749
150125X | MV/LV Substation CA***125X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8024 | -7.8096
011902Z | MV/LV Substation RO***902Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C11 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.6429 | -7.2635
156826Y | MV/LV Substation CR***826Y |  | 20 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.362 | 2.47 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =375 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2664 | -6.989
0594131 | MV/LV Substation ID***4131 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C20 ex CAVAN | Cavan [T42,T421] | SHANKILL |  | 53.9898 | -7.322
1364130 | MV/LV Substation FL***4130 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =47 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C20 ex ROSCOMMON | Roscommon [T41,T42] | LANESBORO |  | 53.7783 | -8.2519
039877X | MV/LV Substation CA***877X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =338 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C15 ex ORANMORE | Oranmore [T41,T44] | GALWAY 110KV |  | 53.2676 | -8.9308
250116X | MV/LV Substation PO***116X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.048 | 1.26 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E16 ex BALLYCROSSAUN | Ballycrossaun [T421,T422] | SOMERSET |  | 53.0916 | -8.1961
093003Z | MV/LV Substation QU***003Z |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =143 kW | --> | C17 ex BALLYCOOLIN | Ballycoolin [T41,T42,T43] | FINGLAS |  | 53.4028 | -6.3329
012416Y | MV/LV Substation WE***416Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.38 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =369 kW | --> | C20 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.8214 | -6.8946
207185 | MV/LV Substation FO***185 |  | 10 kV | _ | LV | 33 kVA :Pole Substation | 0.033 | --> | 0.033 | 0.023 | 3.38 |  | --> | 0.031 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =30 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7527 | -7.5621
026531Y | MV/LV Substation LA***531Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.324 | 8.66 |  | --> | 0.38 | 0 | 0.072 | 0 | 0 | Constrained, otherwise capacity available =316 kW | --> | C17 ex BANDON | Bandon [T101,T42] | BANDON |  | 51.7677 | -8.6605
008293Z | MV/LV Substation BE***293Z |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0.239 | 0.24 | Constrained, otherwise capacity available =373 kVA | --> | 0.38 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =372 kW | --> | C15 ex ROSBERCON | Rosbercon [T41,T42] | WATERFORD |  | 52.3977 | -6.9562
2814484 | MV/LV Substation CA***4484 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C18 ex DOUGLAS | Douglas [T41,T42] | TRABEG |  | 51.8657 | -8.4246
001008X | MV/LV Substation BE***008X |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.315 | 1.16 |  | --> | 0.38 | 0 | 0 | 0.368 | 0 |  | --> | C14 ex DEANSGRANGE | Deansgrange [T41,T42] | CARRICKMINES |  | 53.2794 | -6.1855
006907X | MV/LV Substation CH***907X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.027 | 3.12 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =44 kW | --> | C11 ex BELLFIELD | Bellfield [T41,T42] | CRANE |  | 52.5091 | -6.5887
032046 | MV/LV Substation LI***046 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =43 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex KILCARRAGH | Kilcarragh [T421,T422] | BUTLERSTOWN |  | 52.1661 | -7.0066
0934016 | MV/LV Substation BT***4016 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =350 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =373 kW | --> | C22 ex CLONSHAUGH | Clonshaugh [T41,T42] | FINGLAS |  | 53.4062 | -6.2204
013809Y | MV/LV Substation LA***809Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.047 | 0 |  | --> | C23 ex ATHY | Athy [T101,T102] | ATHY |  | 52.946 | -7.0193
207180 | MV/LV Substation CA***180 |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.161 | 3.38 |  | --> | 0.19 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =181 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.749 | -7.5603
059599Y | MV/LV Substation CO***599Y |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =326 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =370 kW | --> | C15 ex DERRYCRAMPH | Derrycramph [T41,T42] | SHANKILL |  | 53.9878 | -7.362
288814 | MV/LV Substation BA***814 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.028 | 0.04 |  | --> | 0.048 | 0 | 0.005 | 0.041 | 0 |  | --> | C21 ex LITTLE BRAY | Little Bray [T41,T42] | FASSAROE |  | 53.2061 | -6.1492
062763X | MV/LV Substation LA***763X |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.046 | 3.47 |  | --> | 0.19 | 0 | 0.2 | 0 | 0 | Constrained, otherwise capacity available =20 kW | --> | E15 ex BUSH | Bush [T421,T422] | DUNDALK |  | 54.027 | -6.1353
156409X | MV/LV Substation TU***409X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.05 | 2.47 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E13 ex TELAYDON | Telaydon [T42,T421] | LISDRUM |  | 54.2556 | -7.0132
150608 | MV/LV Substation GO***608 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.033 | 3.96 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =45 kW | --> | E19 ex STRANORLAR | Stranorlar [T421,T422] | LETTERKENNY |  | 54.8092 | -7.7598
044810 | MV/LV Substation CO***810 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 2.33 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E13 ex MOY | Moy [T421,T422] | MOY |  | 54.0203 | -9.1747
031108 | MV/LV Substation GO***108 |  | 20 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =106 kVA | --> | 0.19 | 0 | 0.004 | 0 | 0 | Constrained, otherwise capacity available =174 kW | --> | E17 ex SPRINGS | Springs [T421,T422] | DUNGARVAN |  | 52.0853 | -7.5701
066234 | MV/LV Substation FO***234 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =499 kVA | --> | 0.598 | 0 | 0.091 | 0.5 | 0 |  | --> | C22 ex HOWTH JUNCTION | Howth Junction [T41,T42] | GRANGE (DR) |  | 53.3843 | -6.1656
047082X | MV/LV Substation CA***082X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.039 | 1.04 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C16 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 54.0274 | -8.3361
238669 | MV/LV Substation PA***669 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E13 ex BALLINROBE | Ballinrobe [T421,T422] | DALTON |  | 53.6981 | -9.2843
066263Z | MV/LV Substation TH***263Z |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =405 kVA | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C15 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4624 | -6.2171
136045Y | MV/LV Substation BO***045Y |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =38 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | C12 ex AGHAMORE | Aghamore [T41,T42] | LANESBORO |  | 53.7005 | -8.0207
022824X | MV/LV Substation KE***824X |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =63 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =170 kW | --> | C11 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1458 | -8.6568
012128 | MV/LV Substation ST***128 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =285 kVA | --> | 0.38 | 0 | 0.029 | 0 | 0 | Constrained, otherwise capacity available =343 kW | --> | C17 ex POLLERTON | Pollerton [T41,T42] | CARLOW |  | 52.841 | -6.9256
365867 | MV/LV Substation ST***867 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =487 kVA | --> | 0.598 | 0 | 0.008 | 0.5 | 0 |  | --> | C22 ex TYMON | Tymon [T41,T42] | COOKSTOWN |  | 53.2972 | -6.3431
281039X | MV/LV Substation GA***039X |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.165 | 5.49 |  | --> | 0.19 | 0 | 0.015 | 0.174 | 0 |  | --> | C18 ex TRABEG | Trabeg [T101,T102] | TRABEG |  | 51.875 | -8.4428
042413 | MV/LV Substation LU***413 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =46 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E17 ex WINDSOR | Windsor [T421,T422] | CASTLEBAR |  | 53.8658 | -9.2028
022496 | MV/LV Substation FI***496 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0.01 | 0 | 0 | Constrained, otherwise capacity available =38 kW | --> | C18 ex SCARTEEN | Scarteen [T41,T42] | MALLOW |  | 52.1372 | -8.6887
161750 | MV/LV Substation CE***750 |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.074 | 6.53 |  | --> | 0.095 | 0 | 0 | 0.091 | 0 |  | --> | C17 ex OUGHTERARD | Oughterard [T41,T42] | SCREEB |  | 53.4259 | -9.3346
011116 | MV/LV Substation LA***116 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =348 kVA | --> | 0.38 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | C19 ex ROSEHILL | Rosehill [T41,T42] | KILKENNY |  | 52.645 | -7.2433
013538X | MV/LV Substation DO***538X |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.053 | 0.12 |  | --> | 0.095 | 0 | 0 | 0.088 | 0 |  | --> | C20 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9991 | -6.9964
061449 | MV/LV Substation M.***449 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 2.04 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C17 ex BALLYBAY | Ballybay [T41,T42] | LISDRUM |  | 54.1208 | -6.8981
127642X | MV/LV Substation CA***642X |  | 10 kV | _ | LV | 100 kVA :Kiosk Substation | 0.1 | --> | 0.1 | 0.064 | 5.89 |  | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =90 kW | --> | C17 ex CASHEL | Cashel [T41,T42] | CAHIR |  | 52.5163 | -7.9035
052419Z | MV/LV Substation SP***419Z |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.444 | 10.9 |  | --> | 0.598 | 0 | 0.015 | 0.5 | 0 |  | --> | C19 ex MULLINGAR | Mullingar [T101,T102] | MULLINGAR |  | 53.5273 | -7.3319
004008Y | MV/LV Substation AV***008Y |  | 10 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =172 kVA | --> | 0.19 | 0 | 0.008 | 0 | 0 | Constrained, otherwise capacity available =180 kW | --> | C24 ex TINAHASK | Tinahask [T41,T42] | ARKLOW |  | 52.7864 | -6.1635
067247 | MV/LV Substation RE***247 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =280 kVA | --> | 0.38 | 0 | 0.08 | 0.304 | 0 |  | --> | C19 ex RAHEEN | Raheen [T41,T42] | LIMERICK |  | 52.6263 | -8.6552
111415Z | MV/LV Substation CO***415Z |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E15 ex BALLYDEHOB | Ballydehob [T421] | DUNMANWAY |  | 51.5825 | -9.4643
013991Y | MV/LV Substation CA***991Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.121 | 0.12 | Constrained, otherwise capacity available =607 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C19 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9937 | -6.9822
058329X | MV/LV Substation CO***329X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =30 kVA | --> | 0.048 | 0 | 0.005 | 0 | 0 | Constrained, otherwise capacity available =41 kW | --> | C11 ex KYLEERAGH | Kyleeragh [T41,T42] | NENAGH |  | 52.8699 | -8.2091
0544167 | MV/LV Substation GL***4167 |  | 20 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =488 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =579 kW | --> | E19 ex PORTLAOISE | Portlaoise [T423,T424] | PORTLAOISE |  | 53.0312 | -7.2452
093013 | MV/LV Substation WI***013 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0.482 | 2.86 |  | --> | 0.598 | 0 | 0.03 | 0.5 | 0 |  | --> | C17 ex BALLYMUN | Ballymun [T41,T42] | FINGLAS |  | 53.3903 | -6.2695
116254Y | MV/LV Substation HA***254Y |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.191 | 8.1 |  | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =189 kW | --> | E15 ex WESTPORT | Westport [T421,T422] | CASTLEBAR |  | 53.8024 | -9.4716
0684437 | MV/LV Substation TH***4437 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =589 kVA | --> | 0.598 | 0 | 0.01 | 0.5 | 0 |  | --> | C15 ex DRUMCONDRA | Drumcondra [T41,T42] | MCDERMOTT |  | 53.3592 | -6.2563
139693Y | MV/LV Substation KI***693Y |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0.122 | 4 |  | --> | 0.19 | 0 | 0.003 | 0 | 0 | Constrained, otherwise capacity available =177 kW | --> | C18 ex BALLYJAMESDUFF | Ballyjamesduff [T41,T42] | SHANKILL |  | 53.8644 | -7.1927
252878X | MV/LV Substation BA***878X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.042 | 1.32 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C15 ex CLIFDEN | Clifden [T41,T42] | SCREEB |  | 53.4211 | -10.0649
013022 | MV/LV Substation MI***022 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.043 | 0.12 |  | --> | 0.048 | 0 | 0 | 0.046 | 0 |  | --> | C12 ex ATHY | Athy [T101,T102] | ATHY |  | 52.9385 | -6.9045
049494 | MV/LV Substation DR***494 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.03 | 0.21 |  | --> | 0.048 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =40 kW | --> | E12 ex LONGFORD | Longford [T421,T422] | RICHMOND |  | 53.8166 | -7.7738
032048 | MV/LV Substation CH***048 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =295 kVA | --> | 0.38 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =342 kW | --> | C25 ex TRAMORE | Tramore [T41,T42] | BUTLERSTOWN |  | 52.1596 | -7.1536
152720X | MV/LV Substation KN***720X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =37 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =46 kW | --> | E31 ex CAPPAMORE | Cappamore [T41,T42] | ARDNACRUSHA |  | 52.6893 | -8.1104
082807Y | MV/LV Substation KI***807Y |  | 20 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0.083 | 0.64 |  | --> | 0.095 | 0 | 0.025 | 0 | 0 | Constrained, otherwise capacity available =74 kW | --> | E14 ex RANDALSTOWN | Randalstown [T422] | NAVAN |  | 53.6983 | -6.6746
047285 | MV/LV Substation GR***285 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 1.04 |  | --> | 0.95 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =950 kW | --> | C11 ex BOYLE | Boyle [T41,T42] | CARRICK ON SHANNON |  | 53.967 | -8.3025
067374 | MV/LV Substation CA***374 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.035 | 13.8 |  | --> | 0.048 | 0 | 0 | 0.045 | 0 |  | --> | C14 ex SINGLAND | Singland [T101,T102] | SINGLAND |  | 52.5965 | -8.4941
288349X | MV/LV Substation BA***349X |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.036 | 2.36 |  | --> | 0.048 | 0 | 0.031 | 0.022 | 0 |  | --> | C11 ex BRAY | Bray [T41,T42] | FASSAROE |  | 53.1874 | -6.2326
366012X | MV/LV Substation IN***012X |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.018 | 0.45 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | C16 ex CARRAROE | Carraroe [T42] | SCREEB |  | 53.0606 | -9.521
038896 | MV/LV Substation BA***896 |  | 20 kV | _ | LV | 45 kVA :Pole Substation | 0.045 | --> | 0.045 | 0 | 0 | Constrained, otherwise capacity available =45 kVA | --> | 0.043 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =43 kW | --> | E15 ex GORT | Gort [T41,T42] | ENNIS |  | 53.1259 | -8.795
021243 | MV/LV Substation SU***243 |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =180 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =187 kW | --> | E15 ex WHITECHURCH | Whitechurch [T421,T422] | KILBARRY |  | 51.9339 | -8.5692
007253Z | MV/LV Substation SN***253Z |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0.393 | 0.9 |  | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =379 kW | --> | C16 ex CLONARD | Clonard [T41,T42] | WEXFORD |  | 52.3271 | -6.489
207206 | MV/LV Substation JO***206 |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0.044 | 3.38 |  | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | C15 ex GLENGOOLE | Glengoole [T41] | THURLES |  | 52.7458 | -7.5453
025752Y | MV/LV Substation DU***752Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.334 | 2.96 |  | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =557 kW | --> | E17 ex CHARLEVILLE | Charleville [T421,T422] | CHARLEVILLE |  | 52.3536 | -8.6792
001168X | MV/LV Substation RO***168X |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0.5 | 0.86 |  | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex BELFIELD | Belfield [T41,T42] | BLACKROCK |  | 53.3013 | -6.2199
082237Z | MV/LV Substation TU***237Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =121 kVA | --> | 0.19 | 0 | 0.032 | 0 | 0 | Constrained, otherwise capacity available =155 kW | --> | C30 ex ACADEMY STREET | Academy Street [T421,T422,T44] | NAVAN |  | 53.6529 | -6.6582
0814330 | MV/LV Substation AR***4330 |  | 10 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =325 kVA | --> | 0.38 | 0 | 0.034 | 0.344 | 0 |  | --> | C12 ex LUCAN EAST | Lucan East [T41,T42] | GRANGE CASTLE |  | 53.3529 | -6.4548
035421X | MV/LV Substation AR***421X |  | 20 kV | _ | LV | 200 kVA :Pole Substation | 0.2 | --> | 0.2 | 0.112 | 0.49 |  | --> | 0.19 | 0 | 0.006 | 0 | 0 | Constrained, otherwise capacity available =173 kW | --> | E15 ex ARDFINNAN | Ardfinnan [T421] | CAHIR |  | 52.3091 | -7.8832
1544199 | MV/LV Substation ST***4199 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =630 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =598 kW | --> | C14 ex COOLMINE | Coolmine [T41,T42] | FINGLAS |  | 53.3852 | -6.4306
011540Z | MV/LV Substation TH***540Z |  | 10 kV | _ | LV | 200 kVA :Kiosk Substation | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =169 kVA | --> | 0.19 | 0 | 0.014 | 0 | 0 | Constrained, otherwise capacity available =175 kW | --> | C24 ex GORESBRIDGE | Goresbridge [T41,T42] | KILKENNY |  | 52.6302 | -7.0718
001004 | MV/LV Substation PA***004 |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.457 | 4.37 |  | --> | 0.95 | 0 | 0.021 | 0.5 | 0 |  | --> | C17 ex DUN LAOGHAIRE | Dun Laoghaire [T41,T42] | BLACKROCK |  | 53.2926 | -6.1375
0144133 | MV/LV Substation PR***4133 |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =551 kVA | --> | 0.598 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =588 kW | --> | C18 ex KILDARE | Kildare [T41,T42] | NEWBRIDGE |  | 53.1537 | -6.9022
1674065 | MV/LV Substation HO***4065 |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E17 ex WHITECHURCH |  |  |  | 51.9834 | -8.5104
066274 | MV/LV Substation TE***274 |  | 10 kV | _ | LV | 630 kVA :Kiosk Substation | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =213 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C15 ex MOUNTGORRY | Mountgorry [T41,T42] | GRANGE (DR) |  | 53.4559 | -6.209
1534142 | MV/LV Substation AL***4142 |  | 20 kV | _ | LV | 400 kVA :Kiosk Substation | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =335 kVA | --> | 0.38 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =371 kW | --> | E12 ex BIRDHILL | Birdhill [T421,T422] | ARDNACRUSHA |  | 52.8048 | -8.4413
093084Y | MV/LV Substation MA***084Y |  | 10 kV | _ | LV | 630 kVA :Building Structure | 0.63 | --> | 0.63 | 0 | 0 | Constrained, otherwise capacity available =385 kVA | --> | 0.598 | 0 | 0 | 0.5 | 0 |  | --> | C21 ex POPPINTREE | Poppintree [T101,T102] | FINGLAS |  | 53.403 | -6.288
288223X | MV/LV Substation TO***223X |  | 10 kV | _ | LV | 1000 kVA :Building Structure | 1 | --> | 1 | 0.5 | 19.52 |  | --> | 0.95 | 0 | 0 | 0.5 | 0 |  | --> | C18 ex TANEY | Taney [T101,T102] | CARRICKMINES |  | 53.2863 | -6.2405
160077Y | MV/LV Substation KY***077Y |  | 10 kV | _ | LV | 100 kVA :Pole Substation | 0.1 | --> | 0.1 | 0 | 0 | Constrained, otherwise capacity available =86 kVA | --> | 0.095 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =93 kW | --> | C20 ex MOUNTMELLICK | Mountmellick [T41,T42] | PORTLAOISE |  | 53.0712 | -7.3254
082566Y | MV/LV Substation SE***566Y |  | 20 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =48 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =47 kW | --> | E21 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.6687 | -6.5644
214605 | MV/LV Substation CA***605 |  | 10 kV | _ | LV | 200 kVA :Building Structure | 0.2 | --> | 0.2 | 0 | 0 | Constrained, otherwise capacity available =200 kVA | --> | 0.19 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =190 kW | --> | C15 ex DRUMQUIN | Drumquin [T42] | ENNIS |  | 52.6412 | -9.1353
066239 | MV/LV Substation DU***239 |  | 10 kV | _ | LV | 400 kVA :Building Structure | 0.4 | --> | 0.4 | 0 | 0 | Constrained, otherwise capacity available =372 kVA | --> | 0.38 | 0 | 0 | 0.376 | 0 |  | --> | C20 ex COLLINSTOWN | Collinstown [T41,T42] | GRANGE (DR) |  | 53.4396 | -6.2573
064403Z | MV/LV Substation OR***403Z |  | 10 kV | _ | LV | 50 kVA :Pole Substation | 0.05 | --> | 0.05 | 0 | 0 | Constrained, otherwise capacity available =50 kVA | --> | 0.048 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =48 kW | --> | E11 ex SLANE | Slane [T421] | DRYBRIDGE |  | 53.7852 | -6.5084
Dunleer [T41,T42] | DUNLEER (237000) 38 kV STATION | Dunleer [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.72 MVA | --> | 6.2 | 2.375 | 7.4 | 0 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.8337 | -6.4092
Milltown (sr) [T421,T422] | MILLTOWN (SR) (244000) 38 kV STATION | Milltown (sr) [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.83 MVA | --> | 12.4 | 4.75 | 8.7 | 0 | 0 | Constrained, otherwise capacity available =0.62 MW | --> |  | Oughtragh [T141] | OUGHTRAGH |  | 52.1327 | -9.7024
Grange Castle [T101,T102] | GRANGE CASTLE (734000) 110 kV STATION | Grange Castle [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 |  | --> | 24.7 | 9.5 | 0.7 | 9.2 | 10.354 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.329 | -6.4495
Saggart [T41,T42] | SAGGART (172000) 38 kV STATION | Saggart [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.2 | 2 | 2.444 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.2731 | -6.4548
Dingle [T421,T422] | DINGLE (426000) 38 kV STATION | Dingle [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.2 MVA | --> | 6.2 | 2.375 | 3 | 0 | 0 | Constrained, otherwise capacity available =1.38 MW | --> |  | Oughtragh [T141] | OUGHTRAGH |  | 52.1541 | -10.2483
Duleek [T421,T422] | DULEEK (546000) 38 kV STATION | Duleek [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 8.2 | 0 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.6673 | -6.4145
Bruff [T42,T421] | BRUFF (151000) 38 kV STATION | Bruff [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.51 MVA | --> | 6.2 | 2.375 | 2.5 | 3.2 | 2.379 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.5072 | -8.5227
Ballymount [T41,T42] | BALLYMOUNT (436000) 38 kV STATION | Ballymount [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 1.4 | 8 | 4.827 |  | --> |  | Inchicore 220kv [T144,T145] | INCHICORE 220KV |  | 53.3128 | -6.3502
Gurranebane [T421,T422] | GURRANEBANE (377000) 38 kV STATION | Gurranebane [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =0.02 MW | --> |  | Oughtragh [T141] | OUGHTRAGH |  | 51.9397 | -10.2237
Ballinrobe [T421,T422] | BALLINROBE (238000) 38 kV STATION | Ballinrobe [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.21 MVA | --> | 12.4 | 4.75 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =7.13 MW | --> |  | Dalton [T142] | DALTON |  | 53.6351 | -9.1986
Grange Castle [T141] | GRANGE CASTLE (734000) 110 kV STATION | Grange Castle [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 0 | 0 |  | --> | 59.8 | 0 | 9.2 | 36.6 | 0 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.329 | -6.4495
Drumcondra [T41,T42] | DRUMCONDRA (344000) 38 kV STATION | Drumcondra [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.15 MVA | --> | 12.4 | 4.75 | 0.5 | 9.6 | 4.796 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | MCDERMOTT |  | 53.3609 | -6.2538
Grange Castle [T124] | GRANGE CASTLE (734000) 110 kV STATION | Grange Castle [T124] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 0 | 0 | Constrained, otherwise capacity available =14.65 MVA | --> | 19 | 0 | 0 | 18.8 | 0 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.329 | -6.4495
Roches Street [T41,T42] | ROCHES STREET (356000) 38 kV STATION | Roches Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =3.45 MVA | --> | 12.4 | 4.75 | 0.4 | 8.8 | 4.835 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.659 | -8.6305
Riverstown [T41,T42] | RIVERSTOWN (129000) 38 kV STATION | Riverstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 3 | 1 | 1.323 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.9341 | -8.3652
Drumquin [T42] | DRUMQUIN (214000) 38 kV STATION | Drumquin [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 2.2 | 0 | 0 | Constrained, otherwise capacity available =1.73 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.7509 | -9.028
Portarlington [T41,T42] | PORTARLINGTON (160000) 38 kV STATION | Portarlington [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 4.9 | 0 | 0 |  | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.1553 | -7.1994
Dock Road [T41,T42] | DOCK ROAD (635000) 38 kV STATION | Dock Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 6.1 | 0 | 2.424 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.6509 | -8.6534
Bishopstown [T41,T42] | BISHOPSTOWN (254000) 38 kV STATION | Bishopstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.1 | 1.3 | 1.323 | Constrained, otherwise capacity available =4.82 MW | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8918 | -8.5522
Ennis North [T41,T42] | ENNIS NORTH (413000) 38 kV STATION | Ennis North [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =1.95 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.8587 | -8.9872
Mornington Road [T41,T42] | MORNINGTON ROAD (168000) 38 kV STATION | Mornington Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =2.46 MVA | --> | 12.4 | 4.75 | 3 | 0 | 0 | Constrained, otherwise capacity available =6.36 MW | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7118 | -6.342
Kinsale [T423] | KINSALE (225000) 38 kV STATION | Kinsale [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =7.71 MVA | --> | 9.5 | 0 | 0.5 | 0 | 0 | Constrained, otherwise capacity available =8.74 MW | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.7193 | -8.5569
Garryowen [T41,T42] | GARRYOWEN (067000) 38 kV STATION | Garryowen [T41,T42] | 38 kV | _ | MV | 2x15 MVA @ 10 kV | 30 | --> | 22.5 | 0 | 0 | Constrained, otherwise capacity available =4.37 MVA | --> | 18.5 | 7.125 | 2.7 | 12.7 | 7.187 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.6631 | -8.6174
Gillogue [T41,T42] | GILLOGUE (458000) 38 kV STATION | Gillogue [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.12 MVA | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =2.51 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.689 | -8.5794
Glasmore [T141,T142] | GLASMORE (322000) 110 kV STATION | Glasmore [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 0 | Constrained, otherwise capacity available =11.16 MVA | --> | 77.8 | 0 | 63.5 | 0 | 0 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.463 | -6.2548
Naas [T41,T42] | NAAS (015000) 38 kV STATION | Naas [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.9 | 0 | 0 | Constrained, otherwise capacity available =2.47 MW | --> |  | Kilteel [T141,T142] | KILTEEL |  | 53.1987 | -6.6602
Ballyboden [T41,T42] | BALLYBODEN (198000) 38 kV STATION | Ballyboden [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 6.1 | 3 | 4.844 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2821 | -6.2837
Granby Row [T41] | GRANBY ROW (102000) 38 kV STATION | Granby Row [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 0 | 0 | Constrained, otherwise capacity available =3.06 MVA | --> | 14.2 | 0 | 0.3 | 11.8 | 0 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | MCDERMOTT |  | 53.3547 | -6.2691
Birdhill [T421,T422] | BIRDHILL (153000) 38 kV STATION | Birdhill [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.28 MVA | --> | 12.4 | 4.75 | 5.9 | 0 | 0 | Constrained, otherwise capacity available =3.5 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.7758 | -8.4167
Fosterstown [T121] | FOSTERSTOWN (893000) 110 kV STATION | Fosterstown [T121] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 0 | 0 | Constrained, otherwise capacity available =18 MVA | --> | 19 | 0 | 0 | 19 | 0 |  | --> |  | Transmission Source | FOSTERSTOWN
Glasnevin [T41] | GLASNEVIN (114000) 38 kV STATION | Glasnevin [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 |  | --> | 9.5 | 0 | 1.1 | 6.9 | 0 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3705 | -6.2755
Kilsaran [T42] | KILSARAN (561000) 38 kV STATION | Kilsaran [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =1.62 MVA | --> | 4.8 | 0 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =3.2 MW | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.874 | -6.379
Gloucester Place [T41,T42] | GLOUCESTER PLACE (115000) 38 kV STATION | Gloucester Place [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 0.3 | 7.8 | 4.905 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | MCDERMOTT |  | 53.3519 | -6.2485
Moylish [T41,T42] | MOYLISH (402000) 38 kV STATION | Moylish [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.64 MVA | --> | 6.2 | 2.375 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =4.52 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6812 | -8.6481
Morristown [T41,T42] | MORRISTOWN (121000) 38 kV STATION | Morristown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.6 | 0 | 0 | Constrained, otherwise capacity available =1.18 MW | --> |  | Newbridge [T141,T142] | NEWBRIDGE |  | 53.185 | -6.8285
Blake [T41,T42] | BLAKE (120000) 110 kV STATION | Blake [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 7 | 0 | 0 |  | --> |  | Blake [T142] | BLAKE |  | 53.2952 | -6.8636
Gort [T41,T42] | GORT (038000) 38 kV STATION | Gort [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 3 | 0 | 0 | Constrained, otherwise capacity available =1.49 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 53.0628 | -8.837
Mountrath [T41,T42] | MOUNTRATH (388000) 38 kV STATION | Mountrath [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =2.63 MW | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 52.9827 | -7.4771
Mountmellick [T41,T42] | MOUNTMELLICK (387000) 38 kV STATION | Mountmellick [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =2.43 MW | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.0963 | -7.2946
Glasmore [T421,T422] | GLASMORE (322000) 110 kV STATION | Glasmore [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 8.5 | 0 | 0 | Constrained, otherwise capacity available =2.78 MW | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.463 | -6.2548
Fermoy North [T41,T42] | FERMOY NORTH (562000) 38 kV STATION | Fermoy North [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 1.8 | 0 | 0 |  | --> |  | Barrymore [T141] | BARRYMORE |  | 52.151 | -8.2886
Scariff [T42] | SCARIFF (229000) 38 kV STATION | Scariff [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 1.8 | 0 | 0 | Constrained, otherwise capacity available =2.18 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.9016 | -8.5292
Poppintree [T101,T102] | POPPINTREE (983000) 110 kV STATION | Poppintree [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 |  | --> | 24.7 | 9.5 | 6.8 | 10.4 | 9.746 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.4081 | -6.2756
Ennistymon [T41,T42] | ENNISTYMON (158000) 38 kV STATION | Ennistymon [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 8.1 | 0 | 0 |  | --> |  | Ennis [T141,T142] | ENNIS |  | 52.9213 | -9.2768
Phibsboro [T41,T42] | PHIBSBORO (307000) 38 kV STATION | Phibsboro [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 1.9 | 4.8 | 5.007 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3564 | -6.2768
Fairhill [T42] | FAIRHILL (486000) 38 kV STATION | Fairhill [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =1.29 MVA | --> | 9.5 | 0 | 0.5 | 1.3 | 0 | Constrained, otherwise capacity available =7.35 MW | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8958 | -8.4647
Ballinacurra [T41,T42] | BALLINACURRA (126000) 38 kV STATION | Ballinacurra [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 0 | 0 | Constrained, otherwise capacity available =2.65 MVA | --> | 6.2 | 4.75 | 1.3 | 2.2 | 4.938 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.6525 | -8.6293
Patrickswell [T421,T422] | PATRICKSWELL (077000) 38 kV STATION | Patrickswell [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 4.6 | 0 | 2.49 |  | --> |  | Limerick [T141,T142] | LIMERICK |  | 52.5919 | -8.7527
Parkmore [T41,T42] | PARKMORE (551000) 38 kV STATION | Parkmore [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 0.6 | 0 | 0 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.3021 | -8.9846
Foxhole [T421,T422] | FOXHOLE (621000) 38 kV STATION | Foxhole [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 10.1 | 0 | 0 |  | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 51.9759 | -7.855
Pallas [T41,T42] | PALLAS (559000) 38 kV STATION | Pallas [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.2 | 0 | 0 | Constrained, otherwise capacity available =1.66 MW | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 53.0378 | -7.3205
Portarlington [T43] | PORTARLINGTON (160000) 38 kV STATION | Portarlington [T43] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =2.15 MW | --> |  | Blake [T142] | BLAKE |  | 53.1553 | -7.1994
Ballincollig [T41,T42] | BALLINCOLLIG (341000) 38 kV STATION | Ballincollig [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =7.51 MVA | --> | 12.4 | 4.75 | 3.1 | 1.3 | 1.323 | Constrained, otherwise capacity available =7.78 MW | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8753 | -8.6135
Oranmore [T41,T44] | ORANMORE (487000) 38 kV STATION | Oranmore [T41,T44] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.6 | 0 | 0 | Constrained, otherwise capacity available =2.38 MW | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2884 | -8.9245
Finglas [T143,T144] | FINGLAS (318000) 220 kV STATION | Finglas [T143,T144] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 0 |  | --> | 77.8 | 0 | 55.6 | 0 | 0 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.4075 | -6.3161
Oldbawn [T41,T42] | OLDBAWN (365000) 38 kV STATION | Oldbawn [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =0.06 MVA | --> | 12.4 | 4.75 | 4.1 | 5.6 | 4.813 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2762 | -6.3517
Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS (318000) 220 kV STATION | Finglas Rural TSO 220/110 kV [T2101,T2106] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 0 | 0 |  | --> | 308.8 | 0 | 163.2 | 28.3 | 0 |  | --> |  | Transmission Source | FINGLAS |  | 53.4075 | -6.3161
Ballincollig [T421] | BALLINCOLLIG (341000) 38 kV STATION | Ballincollig [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 1.3 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8753 | -8.6135
Grange (dr) [T141,T142] | GRANGE (DR) (087000) 110 kV STATION | Grange (dr) [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 0 | Constrained, otherwise capacity available =21.28 MVA | --> | 77.8 | 0 | 58.6 | 1.5 | 0 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.3954 | -6.164
Ballincollig [T422] | BALLINCOLLIG (341000) 38 kV STATION | Ballincollig [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 1.3 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.8753 | -8.6135
Fortunestown [T101,T102] | FORTUNESTOWN (892000) 110 kV STATION | Fortunestown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 | Constrained, otherwise capacity available =10.71 MVA | --> | 24.7 | 9.5 | 2.4 | 17.5 | 9.607 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.2803 | -6.4085
Palmerstown [T41,T42] | PALMERSTOWN (302000) 38 kV STATION | Palmerstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =2.62 MVA | --> | 12.4 | 4.75 | 2.4 | 0 | 0 | Constrained, otherwise capacity available =7.04 MW | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.3595 | -6.3721
Adamstown [T121,T122] | ADAMSTOWN (497000) 110 kV STATION | Adamstown [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 0 | 0 | Constrained, otherwise capacity available =16.39 MVA | --> | 24.7 | 9.5 | 4.1 | 16 | 9.595 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.3485 | -6.4623
Clarkstown [T41] | CLARKSTOWN (620000) 38 kV STATION | Clarkstown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =4.47 MVA | --> | 4.8 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =4.74 MW | --> |  | Griffinrath [T141,T142] | GRIFFINRATH |  | 53.4525 | -6.6902
Tulla [T41,T42] | TULLA (182000) 38 kV STATION | Tulla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 0 |  | --> | 3.1 | 1.1875 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =0.11 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.8543 | -8.7626
Kilcarragh [T421,T422] | KILCARRAGH (978000) 38 kV STATION | Kilcarragh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 6.8 | 0 | 0 |  | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.2071 | -7.0736
Kilcloher [T41,T42] | KILCLOHER (249000) 38 kV STATION | Kilcloher [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 0 |  | --> | 1.2 | 1.1875 | 1.9 | 0 | 0 |  | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.1308 | -7.7957
Kilcock [T421,T422] | KILCOCK (248000) 38 kV STATION | Kilcock [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 6.3 | 0 | 0 | Constrained, otherwise capacity available =2.37 MW | --> |  | Griffinrath [T141,T142] | GRIFFINRATH |  | 53.3973 | -6.6413
Abbeyleix [T422] | ABBEYLEIX (565000) 38 kV STATION | Abbeyleix [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =1.1 MVA | --> | 4.8 | 0 | 2.7 | 0 | 0 | Constrained, otherwise capacity available =1.36 MW | --> |  | Portlaoise [T141,T142] | PORTLAOISE |  | 52.8889 | -7.2961
Cahircalla [T41,T42] | CAHIRCALLA (186000) 38 kV STATION | Cahircalla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 3 | 0 | 0 | Constrained, otherwise capacity available =1.28 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.8271 | -8.9999
Clondalkin [T41,T42,T44] | CLONDALKIN (072000) 38 kV STATION | Clondalkin [T41,T42,T44] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 | Constrained, otherwise capacity available =1.25 MVA | --> | 28.5 | 4.75 | 5.3 | 17.5 | 4.816 |  | --> |  | Inchicore 220kv [T144,T145] | INCHICORE 220KV |  | 53.3206 | -6.3859
Kilmeaden [T42] | KILMEADEN (576000) 38 kV STATION | Kilmeaden [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =2.42 MVA | --> | 4.8 | 0 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =3.53 MW | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.2376 | -7.2529
Clonshaugh [T41,T42] | CLONSHAUGH (411000) 38 kV STATION | Clonshaugh [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =7.12 MVA | --> | 12.4 | 4.75 | 0.2 | 0 | 0 | Constrained, otherwise capacity available =10.42 MW | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.4072 | -6.2262
Inchicore 220kv [T144,T145] | INCHICORE 220KV (964000) 220 kV STATION | Inchicore 220kv [T144,T145] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 0 | Constrained, otherwise capacity available =23.74 MVA | --> | 77.8 | 0 | 8.9 | 41.2 | 0 | Constrained, otherwise capacity available =50.75 MW | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.3313 | -6.3371
Kilcolgan [T42,T421] | KILCOLGAN (084000) 38 kV STATION | Kilcolgan [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 5 | 0 | 0 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2019 | -8.8562
Cloonlough [T41,T42] | CLOONLOUGH (369000) 38 kV STATION | Cloonlough [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.12 MVA | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =1.9 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.2556 | -8.2695
Tramore [T41,T42] | TRAMORE (032000) 38 kV STATION | Tramore [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =0.84 MVA | --> | 12.4 | 4.75 | 13.4 | 0 | 0 |  | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.1603 | -7.1467
Cloyne [T41] | CLOYNE (232000) 38 kV STATION | Cloyne [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 |  | --> | 4.8 | 0 | 6.9 | 0 | 0 |  | --> |  | Midleton [T141] | MIDLETON |  | 51.8695 | -8.1197
Cloyne [T421] | CLOYNE (232000) 38 kV STATION | Cloyne [T421] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 0 | 0 | Constrained, otherwise capacity available =13.5 MVA | --> | 14.2 | 0 | 5.5 | 0 | 0 | Constrained, otherwise capacity available =8.79 MW | --> |  | Midleton [T141] | MIDLETON |  | 51.8695 | -8.1197
Inch [T421,T422] | INCH (243000) 38 kV STATION | Inch [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =4.7 MVA | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =4.13 MW | --> |  | Oughtragh [T141] | OUGHTRAGH |  | 52.173 | -9.9883
Kilmoney [T41,T42] | KILMONEY (482000) 38 kV STATION | Kilmoney [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 0 | 0 | Constrained, otherwise capacity available =0.29 MVA | --> | 6.2 | 4.75 | 8.2 | 0 | 0 |  | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.8215 | -8.4054
Togher [T41,T42] | TOGHER (336000) 38 kV STATION | Togher [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =3.24 MVA | --> | 12.4 | 4.75 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =6.69 MW | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.8827 | -8.5056
Caherdavin [T41,T42] | CAHERDAVIN (098000) 38 kV STATION | Caherdavin [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =2.71 MVA | --> | 12.4 | 4.75 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =7.62 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6639 | -8.6494
Castletroy [T41,T42] | CASTLETROY (558000) 38 kV STATION | Castletroy [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =1.05 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6786 | -8.5636
Carrigshane [T41] | CARRIGSHANE (459000) 38 kV STATION | Carrigshane [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =5.99 MVA | --> | 9.5 | 0 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =8.03 MW | --> |  | Midleton [T141] | MIDLETON |  | 51.9116 | -8.1493
Julianstown [T423] | JULIANSTOWN (312000) 38 kV STATION | Julianstown [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.6503 | -6.3227
Whitestown [T41,T42] | WHITESTOWN (423000) 38 kV STATION | Whitestown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.25 MVA | --> | 12.4 | 4.75 | 1.2 | 9.7 | 4.769 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2802 | -6.3801
Whitehall [T41] | WHITEHALL (183000) 38 kV STATION | Whitehall [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =1.68 MVA | --> | 9.5 | 0 | 1.9 | 6 | 0 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3782 | -6.2569
Whitechurch [T421,T422] | WHITECHURCH (167000) 38 kV STATION | Whitechurch [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.09 MVA | --> | 12.4 | 4.75 | 9.1 | 0 | 1.323 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.9901 | -8.4998
Castleknock [T41,T42] | CASTLEKNOCK (154000) 38 kV STATION | Castleknock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =3.42 MVA | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =3.01 MW | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.3624 | -6.3628
Castlelyons [T421,T422] | CASTLELYONS (455000) 38 kV STATION | Castlelyons [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.45 MVA | --> | 6.2 | 2.375 | 1.8 | 0 | 0 | Constrained, otherwise capacity available =3.18 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.0798 | -8.2327
Carrigshane [T422] | CARRIGSHANE (459000) 38 kV STATION | Carrigshane [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =4.26 MVA | --> | 9.5 | 0 | 4.4 | 0 | 0 | Constrained, otherwise capacity available =3.2 MW | --> |  | Midleton [T141] | MIDLETON |  | 51.9116 | -8.1493
Claregalway [T42,T421] | CLAREGALWAY (251000) 38 kV STATION | Claregalway [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 5.5 | 0 | 0 |  | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.3678 | -8.9067
Waterford Ind Est [T41,T42,T44] | WATERFORD IND EST (348000) 38 kV STATION | Waterford Ind Est [T41,T42,T44] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 | Constrained, otherwise capacity available =12.9 MVA | --> | 28.5 | 4.75 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =22.03 MW | --> |  | Butlerstown [T141,T142] | BUTLERSTOWN |  | 52.2426 | -7.1558
Citywest [T101,T102] | CITYWEST (454000) 110 kV STATION | Citywest [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 |  | --> | 24.7 | 9.5 | 1.4 | 13 | 9.939 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.2916 | -6.4214
Douglas [T41,T42] | DOUGLAS (281000) 38 kV STATION | Douglas [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.1 | 0 | 0 | Constrained, otherwise capacity available =4.76 MW | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.8706 | -8.4246
Celbridge [T41,T42] | CELBRIDGE (016000) 38 kV STATION | Celbridge [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 4.6 | 0 | 0 | Constrained, otherwise capacity available =4.4 MW | --> |  | Griffinrath [T141,T142] | GRIFFINRATH |  | 53.3409 | -6.5446
Unidare [T41,T42] | UNIDARE (245000) 38 kV STATION | Unidare [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 0.9 | 8.9 | 4.808 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3995 | -6.3031
Tymon [T41,T42] | TYMON (424000) 38 kV STATION | Tymon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.42 MVA | --> | 12.4 | 4.75 | 2.9 | 6.3 | 4.835 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2972 | -6.3369
Belgard [T41,T42] | BELGARD (331000) 38 kV STATION | Belgard [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 0.7 | 8.6 | 4.834 |  | --> |  | Cookstown [T141,T142] | COOKSTOWN |  | 53.2941 | -6.3721
Cappamore [T424] | CAPPAMORE (152000) 38 kV STATION | Cappamore [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =8.91 MVA | --> | 9.5 | 0 | 7.5 | 0 | 0 | Constrained, otherwise capacity available =2.3 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6179 | -8.3228
Cappamore [T41,T42] | CAPPAMORE (152000) 38 kV STATION | Cappamore [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 6.6 | 0 | 0 |  | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6179 | -8.3228
Inchicore North [T41] | INCHICORE NORTH (083000) 38 kV STATION | Inchicore North [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =1.8 MVA | --> | 9.5 | 0 | 0.6 | 7.6 | 0 |  | --> |  | Inchicore 220kv [T144,T145] | INCHICORE 220KV |  | 53.3372 | -6.343
Ashbourne [T421,T422] | ASHBOURNE (335000) 38 kV STATION | Ashbourne [T421,T422] | 38 kV | _ | MV | 1x10,1x15 MVA @ 20 kV | 25 | --> | 18.75 | 0 | 0 |  | --> | 12.4 | 7.125 | 13.2 | 0 | 0 |  | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.4828 | -6.3871
Johnstown [T41,T42] | JOHNSTOWN (506000) 38 kV STATION | Johnstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 3.3 | 0 | 0 | Constrained, otherwise capacity available =3.79 MW | --> |  | Kilteel [T141,T142] | KILTEEL |  | 53.2374 | -6.6141
Slane [T42] | SLANE (208000) 38 kV STATION | Slane [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =4.5 MVA | --> | 4.8 | 0 | 3.9 | 0 | 0 | Constrained, otherwise capacity available =0.86 MW | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7558 | -6.5442
Balbriggan [T41] | BALBRIGGAN (065000) 38 kV STATION | Balbriggan [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =8.84 MVA | --> | 9.5 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =9.38 MW | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.6076 | -6.1858
Colligan [T41,T42] | COLLIGAN (516000) 38 kV STATION | Colligan [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =4.69 MVA | --> | 12.4 | 4.75 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =7.83 MW | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.0906 | -7.6179
Balbriggan [T42] | BALBRIGGAN (065000) 38 kV STATION | Balbriggan [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =5.96 MVA | --> | 9.5 | 0 | 0.2 | 0 | 0 | Constrained, otherwise capacity available =8.59 MW | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.6076 | -6.1858
Howth Junction [T41,T42] | HOWTH JUNCTION (334000) 38 kV STATION | Howth Junction [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =5.03 MVA | --> | 12.4 | 4.75 | 2.9 | 1.5 | 1.472 | Constrained, otherwise capacity available =7.05 MW | --> |  | Grange (dr) [T141,T142] | GRANGE (DR) |  | 53.3856 | -6.1573
Cranny [T41] | CRANNY (582000) 38 kV STATION | Cranny [T41] | 38 kV | _ | MV | 1x2 MVA @ 10 kV | 2 | --> | 1.8 | 0 | 0 | Constrained, otherwise capacity available =0.6 MVA | --> | 1.9 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =1.3 MW | --> |  | Ennis [T141,T142] | ENNIS |  | 52.6971 | -9.2202
Balgaddy [T41,T42] | BALGADDY (623000) 38 kV STATION | Balgaddy [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =2.54 MVA | --> | 12.4 | 4.75 | 2.5 | 6.9 | 4.825 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.328 | -6.4495
Cratloe [T421,T422] | CRATLOE (273000) 38 kV STATION | Cratloe [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.54 MVA | --> | 6.2 | 2.375 | 2.8 | 0 | 0 | Constrained, otherwise capacity available =1.56 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.7015 | -8.7607
Killacloyne [T41,T42] | KILLACLOYNE (536000) 38 kV STATION | Killacloyne [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 |  | --> |  | Midleton [T141] | MIDLETON |  | 51.9137 | -8.2708
Collinstown [T41,T42] | COLLINSTOWN (267000) 38 kV STATION | Collinstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =5.21 MVA | --> | 6.2 | 2.375 | 0 | 1.5 | 1.472 | Constrained, otherwise capacity available =5.18 MW | --> |  | Grange (dr) [T141,T142] | GRANGE (DR) |  | 53.4222 | -6.2216
Slane [T421] | SLANE (208000) 38 kV STATION | Slane [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =1.51 MVA | --> | 9.5 | 0 | 9.2 | 0 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7558 | -6.5442
Springs [T421,T422] | SPRINGS (585000) 38 kV STATION | Springs [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =8.09 MVA | --> | 12.4 | 4.75 | 11.5 | 0 | 0 |  | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.0866 | -7.6482
Curraleigh [T421,T422] | CURRALEIGH (450000) 38 kV STATION | Curraleigh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 7.6 | 0 | 1.323 |  | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.912 | -8.6593
Killacloyne [T43] | KILLACLOYNE (536000) 38 kV STATION | Killacloyne [T43] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 0 |  | --> | 9.5 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =4.76 MW | --> |  | Midleton [T141] | MIDLETON |  | 51.9137 | -8.2708
Malahide [T41,T42] | MALAHIDE (212000) 38 kV STATION | Malahide [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 6.6 | 0 | 0 | Constrained, otherwise capacity available =1.51 MW | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.4477 | -6.1508
Lucan East [T41,T42] | LUCAN EAST (359000) 38 kV STATION | Lucan East [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.4 | 1.7 | 2.451 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.3647 | -6.4272
Dalton [T421,T422] | DALTON (909000) 110 kV STATION | Dalton [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =4.01 MVA | --> | 12.4 | 4.75 | 11.9 | 0 | 0 |  | --> |  | Dalton [T142] | DALTON |  | 53.7163 | -8.9756
Ballycoolin [T41,T42,T43] | BALLYCOOLIN (514000) 38 kV STATION | Ballycoolin [T41,T42,T43] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 |  | --> | 28.5 | 4.75 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =17.61 MW | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.4024 | -6.3597
Semperit [T41,T42,T43] | SEMPERIT (360000) 38 kV STATION | Semperit [T41,T42,T43] | 38 kV | _ | MV | 3x10 MVA @ 10 kV | 30 | --> | 27 | 0 | 0 |  | --> | 28.5 | 4.75 | 2.1 | 19.7 | 4.837 |  | --> |  | Grange Castle [T141] | GRANGE CASTLE |  | 53.3359 | -6.3539
Headford Road [T41,T42] | HEADFORD ROAD (262000) 38 kV STATION | Headford Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.51 MVA | --> | 12.4 | 4.75 | 1 | 0 | 0 | Constrained, otherwise capacity available =8.31 MW | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2759 | -9.0548
Dennehys Cross [T41,T42] | DENNEHYS CROSS (311000) 38 kV STATION | Dennehys Cross [T41,T42] | 38 kV | _ | MV | 2x15 MVA @ 10 kV | 30 | --> | 22.5 | 0 | 0 | Constrained, otherwise capacity available =2.74 MVA | --> | 18.5 | 7.125 | 2 | 0 | 0 | Constrained, otherwise capacity available =8.48 MW | --> |  | Trabeg [T141,T142] | TRABEG |  | 51.8918 | -8.4967
Curraglass [T41] | CURRAGLASS (586000) 38 kV STATION | Curraglass [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 0 | Constrained, otherwise capacity available =2.18 MVA | --> | 4.8 | 0 | 0.5 | 0 | 0 | Constrained, otherwise capacity available =3.86 MW | --> |  | Barrymore [T141] | BARRYMORE |  | 52.0896 | -8.0562
Kildare [T422] | KILDARE (014000) 38 kV STATION | Kildare [T422] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 0 | 0 | Constrained, otherwise capacity available =13.5 MVA | --> | 14.2 | 0 | 1.5 | 0 | 0 | Constrained, otherwise capacity available =12.77 MW | --> |  | Newbridge [T141,T142] | NEWBRIDGE |  | 53.1584 | -6.9295
Kildare [T41,T42] | KILDARE (014000) 38 kV STATION | Kildare [T41,T42] | 38 kV | _ | MV | 2x15 MVA @ 10 kV | 30 | --> | 22.5 | 0 | 0 | Constrained, otherwise capacity available =0.73 MVA | --> | 18.5 | 7.125 | 6.2 | 0 | 0 | Constrained, otherwise capacity available =8.11 MW | --> |  | Newbridge [T141,T142] | NEWBRIDGE |  | 53.1584 | -6.9295
Cookstown [T141,T142] | COOKSTOWN (672000) 110 kV STATION | Cookstown [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 0 | Constrained, otherwise capacity available =20.1 MVA | --> | 77.8 | 0 | 24 | 37.2 | 0 |  | --> |  | Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV |  | 53.2947 | -6.3826
Athenry [T41,T42] | ATHENRY (142000) 38 kV STATION | Athenry [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 2.4 | 0 | 0 | Constrained, otherwise capacity available =2.14 MW | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2785 | -8.719
Termonfeckin Road [T41,T42] | TERMONFECKIN ROAD (263000) 38 kV STATION | Termonfeckin Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 |  | --> | 6.2 | 2.375 | 6.6 | 0 | 0 |  | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.7295 | -6.3184
Coolcarron [T41,T42] | COOLCARRON (234000) 38 kV STATION | Coolcarron [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 0 |  | --> | 1.2 | 1.1875 | 1.2 | 0 | 0 |  | --> |  | Barrymore [T141] | BARRYMORE |  | 52.133 | -8.2814
Templemore [T41,T42] | TEMPLEMORE (057000) 38 kV STATION | Templemore [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =7.06 MVA | --> | 12.4 | 4.75 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =8.41 MW | --> |  | Ikerrin [T141] | IKERRIN |  | 52.7898 | -7.8383
Athenry [T423] | ATHENRY (142000) 38 kV STATION | Athenry [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 0 | Constrained, otherwise capacity available =2.4 MVA | --> | 9.5 | 0 | 3.3 | 0 | 0 | Constrained, otherwise capacity available =4.8 MW | --> |  | Galway 110kv [T141,T142] | GALWAY 110KV |  | 53.2785 | -8.719
Athgarvan [T41,T44] | ATHGARVAN (394000) 38 kV STATION | Athgarvan [T41,T44] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 7.4 | 0 | 0 |  | --> |  | Newbridge [T141,T142] | NEWBRIDGE |  | 53.1648 | -6.7899
Mayfield [T41,T42] | MAYFIELD (300000) 38 kV STATION | Mayfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =4.39 MVA | --> | 12.4 | 4.75 | 2.3 | 1.3 | 1.323 | Constrained, otherwise capacity available =7.76 MW | --> |  | Kilbarry [T142,T143] | KILBARRY |  | 51.922 | -8.4109
Kilmacthomas [T421,T422] | KILMACTHOMAS (296000) 38 kV STATION | Kilmacthomas [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.59 MVA | --> | 6.2 | 2.375 | 6 | 0 | 0 |  | --> |  | Dungarvan [T141,T142] | DUNGARVAN |  | 52.2032 | -7.403
Swords [T41,T42] | SWORDS (066000) 38 kV STATION | Swords [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.29 MVA | --> | 12.4 | 4.75 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =3.03 MW | --> |  | Glasmore [T141,T142] | GLASMORE |  | 53.4613 | -6.2256
Coolmine [T41,T42] | COOLMINE (407000) 38 kV STATION | Coolmine [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 |  | --> | 12.4 | 4.75 | 5.4 | 0 | 0 | Constrained, otherwise capacity available =2.12 MW | --> |  | Finglas [T143,T144] | FINGLAS |  | 53.3768 | -6.4167
Sutton [T41,T42] | SUTTON (333000) 38 kV STATION | Sutton [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =1.63 MVA | --> | 12.4 | 4.75 | 4 | 1.5 | 1.472 | Constrained, otherwise capacity available =5.83 MW | --> |  | Grange (dr) [T141,T142] | GRANGE (DR) |  | 53.3875 | -6.1215
Corbally [T41,T42] | CORBALLY (195000) 38 kV STATION | Corbally [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =0.99 MVA | --> | 6.2 | 2.375 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =3.42 MW | --> |  | Ardnacrusha [T141,T142] | ARDNACRUSHA |  | 52.6735 | -8.6203
Merville [T41,T42] | MERVILLE (200000) 38 kV STATION | Merville [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0 | Constrained, otherwise capacity available =0.92 MVA | --> | 12.4 | 4.75 | 0.9 | 9.6 | 4.785 |  | --> |  | Mesh: Orange [FingT142,McDrT142] | FINGLAS |  | 53.3848 | -6.2951
Stickillen [T41,T42] | STICKILLEN (063000) 38 kV STATION | Stickillen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 0 | Constrained, otherwise capacity available =1.03 MVA | --> | 6.2 | 2.375 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =1.65 MW | --> |  | Drybridge [T141,T142] | DRYBRIDGE |  | 53.8627 | -6.533
Stephenstown [T101,T102] | STEPHENSTOWN (730000) 110 kV STATION | Stephenstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | 0 | Constrained, otherwise capacity available =13.21 MVA | --> | 24.7 | 9.5 | 15 | 6 | 9.562 |  | --> |  | Finglas Rural TSO 220/110 kV [T2101,T2106] | FINGLAS |  | 53.6057 | -6.1974
Rineanna [T41,T42] | RINEANNA (109000) 38 kV STATION | Rineanna [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.4 | 0.4 | Constrained, otherwise capacity available =1.05 MVA | --> | 12.4 | 4.75 | 1.6 | 4.9 | 4.879 | Constrained, otherwise capacity available =6.92 MW | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.7096 | -8.8866
Drumline [T421,T422] | DRUMLINE (629000) 110 kV STATION | Drumline [T421,T422] | 110 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0.4 |  | --> | 6.2 | 2.375 | 2.6 | 0 | 2.81 |  | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.7309 | -8.8496
Shannon [T41,T42] | SHANNON (325000) 38 kV STATION | Shannon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0.4 |  | --> | 12.4 | 4.75 | 0.4 | 4.9 | 4.876 | Constrained, otherwise capacity available =8.07 MW | --> |  | Drumline [T141,T142] | DRUMLINE |  | 52.698 | -8.8964
Baltinglass [T421,T422] | BALTINGLASS (294000) 38 kV STATION | Baltinglass [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 0.6 |  | --> | 6.2 | 2.375 | 5.8 | 0 | 0 |  | --> |  | Stratford [T141] | STRATFORD |  | 52.9404 | -6.6817
Kilcullen [T41,T42,T424] | KILCULLEN (323000) 38 kV STATION | Kilcullen [T41,T42,T424] | 38 kV | _ | MV | 2x5,1x10 MVA @ 10 kV | 20 | --> | 18 | 0.6 | 0.6 | Constrained, otherwise capacity available =4.13 MVA | --> | 19 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =14.53 MW | --> |  | Stratford [T141] | STRATFORD |  | 53.1216 | -6.7474
Kilgarvan [T421] | KILGARVAN (110000) 38 kV STATION | Kilgarvan [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.38 MVA | --> | 4.8 | 0 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =2.47 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 51.9092 | -9.4416
Kenmare [T421] | KENMARE (414000) 38 kV STATION | Kenmare [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.04 MVA | --> | 4.8 | 0 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =2.75 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 51.8856 | -9.5643
Rathmore [T42,T421] | RATHMORE (221000) 38 kV STATION | Rathmore [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.63 MVA | --> | 6.2 | 2.375 | 1.8 | 0 | 0 | Constrained, otherwise capacity available =3.55 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0803 | -9.1908
Woodford [T41,T42] | WOODFORD (276000) 38 kV STATION | Woodford [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.8 | 0.8 | Constrained, otherwise capacity available =2.99 MVA | --> | 12.4 | 4.75 | 3.5 | 0 | 0 | Constrained, otherwise capacity available =5.56 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0537 | -9.4547
Kenmare [T42] | KENMARE (414000) 38 kV STATION | Kenmare [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.8 | 0.8 | Constrained, otherwise capacity available =1.96 MVA | --> | 4.8 | 0 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =3.31 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 51.8856 | -9.5643
Coolcorcoran [T41,T42] | COOLCORCORAN (020000) 38 kV STATION | Coolcorcoran [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 0.8 |  | --> | 12.4 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =2.9 MW | --> |  | Knockearagh [T141,T142] | KNOCKEARAGH |  | 52.0758 | -9.5109
Deansgrange [T41,T42] | DEANSGRANGE (001000) 38 kV STATION | Deansgrange [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 1.2 | Constrained, otherwise capacity available =5.35 MVA | --> | 12.4 | 4.75 | 3.3 | 7.1 | 4.785 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2716 | -6.1525
Carrickmines [T41,T42] | CARRICKMINES (649000) 220 kV STATION | Carrickmines [T41,T42] | 220 kV | _ | MV | 1x10,1x15 MVA @ 10 kV | 25 | --> | 18.75 | 0 | 1.2 |  | --> | 12.4 | 7.125 | 7 | 1.2 | 7.315 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2549 | -6.1921
Brewery Road [T41,T42] | BREWERY ROAD (773000) 38 kV STATION | Brewery Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 1.2 | Constrained, otherwise capacity available =2.9 MVA | --> | 12.4 | 4.75 | 2.4 | 6.4 | 4.861 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.283 | -6.1924
Sandyford [T41,T42] | SANDYFORD (288000) 38 kV STATION | Sandyford [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 1.2 |  | --> | 12.4 | 4.75 | 4.5 | 4.6 | 4.841 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2665 | -6.2258
Mount Merrion [T41,T42] | MOUNT MERRION (101000) 38 kV STATION | Mount Merrion [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 1.2 | Constrained, otherwise capacity available =2.51 MVA | --> | 12.4 | 4.75 | 3.3 | 6.6 | 4.806 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2994 | -6.2114
Loughlinstown [T41,T42] | LOUGHLINSTOWN (199000) 38 kV STATION | Loughlinstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 1.2 |  | --> | 12.4 | 4.75 | 2.9 | 5.7 | 4.87 |  | --> |  | Carrickmines [T141,T142] | CARRICKMINES |  | 53.2528 | -6.1374
Bundoran [T41,T42] | BUNDORAN (350000) 38 kV STATION | Bundoran [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 1.6 | Constrained, otherwise capacity available =2.7 MVA | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =3.42 MW | --> |  | Cathaleens Fall [T141] | CATHALEENS FALL |  | 54.4694 | -8.2598
Ballyshannon [T41,T42] | BALLYSHANNON (108000) 38 kV STATION | Ballyshannon [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 1.6 | Constrained, otherwise capacity available =2.23 MVA | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =2.69 MW | --> |  | Cathaleens Fall [T141] | CATHALEENS FALL |  | 54.499 | -8.2003
Donegal [T41,T42] | DONEGAL (149000) 38 kV STATION | Donegal [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 1.6 |  | --> | 6.2 | 2.375 | 34.6 | 0 | 0 |  | --> |  | Cathaleens Fall [T141] | CATHALEENS FALL |  | 54.6538 | -8.0773
Ballyconra [T423] | BALLYCONRA (479000) 38 kV STATION | Ballyconra [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 8.7 | 10.3 |  | --> | 9.5 | 0 | 9.2 | 0 | 0 | Constrained, otherwise capacity available =0.6 MW | --> |  | Ballyragget [T141] | BALLYRAGGET |  | 52.7979 | -7.3452
Ballyragget [T421,T422] | BALLYRAGGET (329000) 38 kV STATION | Ballyragget [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 2.8 | 10.3 |  | --> | 6.2 | 2.375 | 1.8 | 0 | 0 | Constrained, otherwise capacity available =3.3 MW | --> |  | Ballyragget [T141] | BALLYRAGGET |  | 52.7962 | -7.3349
Castlecomer [T41,T42] | CASTLECOMER (144000) 38 kV STATION | Castlecomer [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.3 |  | --> | 6.2 | 2.375 | 6.2 | 0 | 0 |  | --> |  | Ballyragget [T141] | BALLYRAGGET |  | 52.8442 | -7.1771
Callan [T41,T42] | CALLAN (460000) 38 kV STATION | Callan [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 6 | 0 | 0 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.5351 | -7.3914
Ballyhale [T42,T421] | BALLYHALE (010000) 38 kV STATION | Ballyhale [T42,T421] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 3.2 | 0 | 0 | Constrained, otherwise capacity available =1.05 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.4755 | -7.181
Mcdonagh [T41,T42] | MCDONAGH (390000) 38 kV STATION | Mcdonagh [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5 | 10.4 |  | --> | 12.4 | 4.75 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =6.89 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6596 | -7.2484
Talbots Inch [T41,T42] | TALBOTS INCH (508000) 38 kV STATION | Talbots Inch [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 8.2 | 0 | 0 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6758 | -7.2636
Graiguenamanagh [T41,T42] | GRAIGUENAMANAGH (382000) 38 kV STATION | Graiguenamanagh [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0 | 10.4 |  | --> | 2.5 | 0.95 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =0.17 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.5297 | -6.9767
Ballyhale [T422] | BALLYHALE (010000) 38 kV STATION | Ballyhale [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 10.4 |  | --> | 9.5 | 0 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =6.38 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.4755 | -7.181
Purcells Inch [T41,T42] | PURCELLS INCH (485000) 38 kV STATION | Purcells Inch [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 7.5 | 2.8 | 10.4 |  | --> | 3.1 | 2.375 | 2.1 | 0 | 0 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.647 | -7.214
Goresbridge [T41,T42] | GORESBRIDGE (247000) 38 kV STATION | Goresbridge [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.4 |  | --> | 6.2 | 2.375 | 5 | 0 | 0 |  | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6397 | -6.9995
Rosehill [T41,T42] | ROSEHILL (193000) 38 kV STATION | Rosehill [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 10.4 |  | --> | 12.4 | 4.75 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =5.2 MW | --> |  | Kilkenny [T141,T142] | KILKENNY |  | 52.6399 | -7.2705
Tuam South [T42] | TUAM SOUTH (040000) 38 kV STATION | Tuam South [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 10.8 |  | --> | 4.8 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =2.25 MW | --> |  | Cloon [T141,T142] | CLOON |  | 53.516 | -8.8665
Tuam North [T41,T42] | TUAM NORTH (253000) 38 kV STATION | Tuam North [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 10.8 |  | --> | 6.2 | 2.375 | 3 | 0 | 0 | Constrained, otherwise capacity available =0.71 MW | --> |  | Cloon [T141,T142] | CLOON |  | 53.5329 | -8.8772
Cloon [T42,T421] | CLOON (907000) 110 kV STATION | Cloon [T42,T421] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 10.7 | 10.8 |  | --> | 12.4 | 4.75 | 13.1 | 0 | 0 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.4879 | -8.8539
Cong [T421,T422] | CONG (590000) 38 kV STATION | Cong [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 1.4 | 10.8 |  | --> | 6.2 | 2.375 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =4.35 MW | --> |  | Cloon [T141,T142] | CLOON |  | 53.544 | -9.2569
Headford [T41,T42] | HEADFORD (527000) 38 kV STATION | Headford [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 10.8 |  | --> | 1.2 | 1.1875 | 3.3 | 0 | 0 |  | --> |  | Cloon [T141,T142] | CLOON |  | 53.4969 | -9.1181
Boyle [T41,T42] | BOYLE (047000) 38 kV STATION | Boyle [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1 | 11.5 |  | --> | 6.2 | 2.375 | 9.3 | 0 | 0 |  | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9561 | -8.3176
Castlerea [T41,T42] | CASTLEREA (256000) 38 kV STATION | Castlerea [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.3 | 11.5 |  | --> | 6.2 | 2.375 | 4.4 | 0 | 0 | Constrained, otherwise capacity available =0.24 MW | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.7675 | -8.4446
Castlerea [T421] | CASTLEREA (256000) 38 kV STATION | Castlerea [T421] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 9 | 11.5 |  | --> | 9.5 | 4.75 | 0 | 0 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.7675 | -8.4446
Carrigallen [T421] | CARRIGALLEN (157000) 38 kV STATION | Carrigallen [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.6 | 11.5 |  | --> | 4.8 | 0 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =3.18 MW | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9723 | -7.6967
Mohill [T421,T422] | MOHILL (048000) 38 kV STATION | Mohill [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 2 | 11.5 |  | --> | 6.2 | 2.375 | 1.8 | 0 | 0 | Constrained, otherwise capacity available =3.01 MW | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9048 | -7.8689
Carrick On Shannon [T41,T42] | CARRICK ON SHANNON (074000) 110 kV STATION | Carrick On Shannon [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 11.5 |  | --> | 6.2 | 2.375 | 2.2 | 0 | 0 | Constrained, otherwise capacity available =0.72 MW | --> |  | Carrick On Shannon [T141,T142] | CARRICK ON SHANNON |  | 53.9295 | -8.1261
Spa Road [T41,T42] | SPA ROAD (205000) 38 kV STATION | Spa Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9 | 11.6 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =2.31 MW | --> |  | Doon [T141,T142] | DOON |  | 52.3529 | -7.6775
Lawlesstown [T42,T421] | LAWLESSTOWN (542000) 38 kV STATION | Lawlesstown [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.6 | 11.6 |  | --> | 12.4 | 4.75 | 3.5 | 0 | 0 | Constrained, otherwise capacity available =4.38 MW | --> |  | Doon [T141,T142] | DOON |  | 52.3763 | -7.7249
Ardgeeha [T41,T42] | ARDGEEHA (034000) 38 kV STATION | Ardgeeha [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.9 | 11.6 |  | --> | 12.4 | 4.75 | 8.3 | 0 | 0 | Constrained, otherwise capacity available =1.65 MW | --> |  | Doon [T141,T142] | DOON |  | 52.3777 | -7.6967
Gweedore [T421] | GWEEDORE (192000) 38 kV STATION | Gweedore [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.7 | 11.8 |  | --> | 4.8 | 0 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =2.81 MW | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 55.0328 | -8.2027
Derrybeg [T41,T42] | DERRYBEG (399000) 38 kV STATION | Derrybeg [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 11.8 |  | --> | 6.2 | 2.375 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =3.44 MW | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 55.0668 | -8.2661
Dungloe [T41,T42] | DUNGLOE (340000) 38 kV STATION | Dungloe [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 11.8 |  | --> | 1.2 | 1.1875 | 2.3 | 0 | 0 |  | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 54.9422 | -8.3626
Creeslough [T421] | CREESLOUGH (258000) 38 kV STATION | Creeslough [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.9 | 11.8 |  | --> | 4.8 | 0 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =3.08 MW | --> |  | Ardnagappary [T141] | ARDNAGAPPARY |  | 55.1166 | -7.9019
Milltown (dr) [T101,T102] | MILLTOWN (DR) (069000) 110 kV STATION | Milltown (dr) [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.8 | 113 |  | --> | 24.7 | 9.5 | 3.2 | 15.8 | 9.645 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.3176 | -6.2456
Heuston Square [T101,T102] | HEUSTON SQUARE (504000) 110 kV STATION | Heuston Square [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 20.8 | 113 |  | --> | 24.7 | 9.5 | 0.2 | 20.5 | 9.574 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.347 | -6.3042
Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) (069000) 110 kV STATION | Mesh: Green [MiltT142,InciT143] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 29.5 | 113 |  | --> | 77.8 | 0 | 26.8 | 33.3 | 0 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.3176 | -6.2456
Mesh: Red [InciT141,FranT142] | INCHICORE 220KV (964000) 220 kV STATION | Mesh: Red [InciT141,FranT142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 14.7 | 113 |  | --> | 77.8 | 0 | 9.9 | 51.7 | 0 |  | --> |  | Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV |  | 53.3313 | -6.3371
Rathkeale [T421,T422] | RATHKEALE (712000) 110 kV STATION | Rathkeale [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2 | 12.7 |  | --> | 12.4 | 4.75 | 3.2 | 0 | 0 | Constrained, otherwise capacity available =6.06 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.5406 | -8.9745
Newcastlewest [T41,T42] | NEWCASTLEWEST (185000) 38 kV STATION | Newcastlewest [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.1 | 12.7 |  | --> | 6.2 | 2.375 | 2.8 | 0 | 0 | Constrained, otherwise capacity available =1.44 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4479 | -9.0462
Churchtown [T422] | CHURCHTOWN (971000) 38 kV STATION | Churchtown [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 7.5 | 12.7 |  | --> | 9.5 | 0 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =8.28 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4634 | -9.0494
Churchtown [T41] | CHURCHTOWN (971000) 38 kV STATION | Churchtown [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4.2 | 12.7 |  | --> | 9.5 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =8.38 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.4634 | -9.0494
Foynes [T41,T42] | FOYNES (314000) 38 kV STATION | Foynes [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.6 | 12.7 |  | --> | 6.2 | 2.375 | 4.8 | 0 | 0 | Constrained, otherwise capacity available =0.14 MW | --> |  | Rathkeale [T141,T142] | RATHKEALE |  | 52.6067 | -9.0798
Lloyd [T41,T42] | LLOYD (711000) 38 kV STATION | Lloyd [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.3 | 12.8 |  | --> | 6.2 | 2.375 | 0.6 | 0 | 0 | Constrained, otherwise capacity available =4.77 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.7333 | -6.9117
Randalstown [T422] | RANDALSTOWN (463000) 38 kV STATION | Randalstown [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.6 | 12.8 |  | --> | 4.8 | 0 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =3.45 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.6705 | -6.7238
Trim [T41,T42] | TRIM (196000) 38 kV STATION | Trim [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 12.8 |  | --> | 6.2 | 2.375 | 7.9 | 0 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.5544 | -6.7864
Trim [T421] | TRIM (196000) 38 kV STATION | Trim [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.3 | 12.8 |  | --> | 4.8 | 0 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =2.44 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.5544 | -6.7864
Abbeyland [T41,T42] | ABBEYLAND (270000) 38 kV STATION | Abbeyland [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2 | 12.8 |  | --> | 12.4 | 4.75 | 3.5 | 0 | 0 | Constrained, otherwise capacity available =6.47 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.671 | -6.6874
Athboy [T42] | ATHBOY (177000) 38 kV STATION | Athboy [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 12.8 |  | --> | 4.8 | 0 | 5.7 | 0 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6447 | -6.9298
Academy Street [T421,T422,T44] | ACADEMY STREET (617000) 38 kV STATION | Academy Street [T421,T422,T44] | 38 kV | _ | MV | 2x5,1x10 MVA @ 20 kV | 20 | --> | 18 | 0 | 12.8 |  | --> | 19 | 4.75 | 8.3 | 0 | 0 | Constrained, otherwise capacity available =5.62 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.6496 | -6.6735
Randalstown [T41] | RANDALSTOWN (463000) 38 kV STATION | Randalstown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.8 | 12.8 |  | --> | 4.8 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =3.98 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.6705 | -6.7238
Kells [T41,T42] | KELLS (180000) 38 kV STATION | Kells [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.4 | 12.8 |  | --> | 6.2 | 2.375 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =3.3 MW | --> |  | Navan [T141,T142] | NAVAN |  | 53.716 | -6.8746
Athboy [T423] | ATHBOY (177000) 38 kV STATION | Athboy [T423] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.3 | 12.8 |  | --> | 4.8 | 0 | 5.2 | 0 | 0 |  | --> |  | Navan [T141,T142] | NAVAN |  | 53.6447 | -6.9298
Moy [T421,T422] | MOY (774000) 110 kV STATION | Moy [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.3 | 13 |  | --> | 12.4 | 4.75 | 7.9 | 0 | 0 | Constrained, otherwise capacity available =0.42 MW | --> |  | Moy [T141,T142] | MOY |  | 54.1315 | -9.1748
Crossmolina [T41,T42] | CROSSMOLINA (220000) 38 kV STATION | Crossmolina [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 5.25 | 1.4 | 13 |  | --> | 2.5 | 2.375 | 1.3 | 0 | 0 |  | --> |  | Moy [T141,T142] | MOY |  | 54.1164 | -9.3359
Ardnaree [T42,T421] | ARDNAREE (089000) 38 kV STATION | Ardnaree [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 9.1 | 13 |  | --> | 12.4 | 4.75 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =9.3 MW | --> |  | Moy [T141,T142] | MOY |  | 54.1178 | -9.1521
Enniscrone [T421,T422] | ENNISCRONE (492000) 38 kV STATION | Enniscrone [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3.6 | 13 |  | --> | 6.2 | 2.375 | 7.5 | 0 | 0 |  | --> |  | Moy [T141,T142] | MOY |  | 54.2051 | -9.0628
Rahans [T41] | RAHANS (461000) 38 kV STATION | Rahans [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.7 | 13 |  | --> | 4.8 | 0 | 0.5 | 0 | 0 | Constrained, otherwise capacity available =2.75 MW | --> |  | Moy [T141,T142] | MOY |  | 54.1078 | -9.1659
Cullion [T41,T42] | CULLION (099000) 38 kV STATION | Cullion [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.2 |  | --> | 6.2 | 2.375 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =0.77 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.939 | -7.7183
Convoy [T41,T42] | CONVOY (162000) 38 kV STATION | Convoy [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 7.2 | 13.2 |  | --> | 6.2 | 4.75 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =4.52 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.8604 | -7.6599
Gortlee [T41,T42] | GORTLEE (646000) 38 kV STATION | Gortlee [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.5 | 13.2 |  | --> | 12.4 | 4.75 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =8.49 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.9707 | -7.7144
Newtowncunningham [T41,T42] | NEWTOWNCUNNINGHAM (503000) 38 kV STATION | Newtowncunningham [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.7 | 13.2 |  | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =3.19 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 55.008 | -7.4657
Ballyraine [T41,T42] | BALLYRAINE (442000) 38 kV STATION | Ballyraine [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 3 | 13.2 |  | --> | 6.2 | 4.75 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =1.44 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.9515 | -7.7105
Milford (nr) [T41,T42] | MILFORD (NR) (209000) 38 kV STATION | Milford (nr) [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.2 |  | --> | 6.2 | 2.375 | 7.9 | 0 | 0 |  | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 55.075 | -7.6985
Stranorlar [T421,T422] | STRANORLAR (150000) 38 kV STATION | Stranorlar [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 4 | 13.2 |  | --> | 12.4 | 4.75 | 11.1 | 0 | 0 |  | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.808 | -7.7617
Rossgeir [T41,T42] | ROSSGEIR (489000) 38 kV STATION | Rossgeir [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.2 | 13.2 |  | --> | 6.2 | 2.375 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =2.52 MW | --> |  | Letterkenny [T141,T142] | LETTERKENNY |  | 54.8614 | -7.5172
Glengoole [T42] | GLENGOOLE (207000) 38 kV STATION | Glengoole [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.9 | 13.7 |  | --> | 4.8 | 0 | 0.5 | 0 | 0 | Constrained, otherwise capacity available =4.03 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6084 | -7.6267
Loughtagalla [T41,T42] | LOUGHTAGALLA (127000) 38 kV STATION | Loughtagalla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.7 |  | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =2.48 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.693 | -7.7696
Glengoole [T41] | GLENGOOLE (207000) 38 kV STATION | Glengoole [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 3.4 | 13.7 |  | --> | 9.5 | 0 | 8 | 0 | 0 |  | --> |  | Thurles [T141,T142] | THURLES |  | 52.6084 | -7.6267
Blanchfield [T422] | BLANCHFIELD (432000) 38 kV STATION | Blanchfield [T422] | 38 kV | _ | MV | 1x31.5 MVA @ 20 kV | 31.5 | --> | 28.35 | 13.7 | 13.7 | Constrained, otherwise capacity available =28.13 MVA | --> | 29.9 | 0 | 23.4 | 0 | 0 | Constrained, otherwise capacity available =6.79 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6547 | -7.5021
Urlingford [T421] | URLINGFORD (910000) 38 kV STATION | Urlingford [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 13.7 |  | --> | 9.5 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.705 | -7.5965
Blanchfield [T421] | BLANCHFIELD (432000) 38 kV STATION | Blanchfield [T421] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.2 | 13.7 |  | --> | 14.2 | 0 | 11.5 | 0 | 0 | Constrained, otherwise capacity available =3.05 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6547 | -7.5021
Holycross Road [T41,T42] | HOLYCROSS ROAD (328000) 38 kV STATION | Holycross Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.7 |  | --> | 6.2 | 2.375 | 3.5 | 0 | 0 | Constrained, otherwise capacity available =0.05 MW | --> |  | Thurles [T141,T142] | THURLES |  | 52.6664 | -7.8399
Cavan [T42,T421] | CAVAN (059000) 38 kV STATION | Cavan [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 13.8 |  | --> | 12.4 | 4.75 | 4.2 | 0 | 0 | Constrained, otherwise capacity available =2.79 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.0066 | -7.3417
Errigal [T41,T422] | ERRIGAL (517000) 38 kV STATION | Errigal [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.6 | 13.8 |  | --> | 12.4 | 4.75 | 5.8 | 0 | 0 | Constrained, otherwise capacity available =3.76 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.0567 | -7.0805
Derrycramph [T41,T42] | DERRYCRAMPH (545000) 38 kV STATION | Derrycramph [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.8 |  | --> | 6.2 | 2.375 | 1.5 | 0 | 0 | Constrained, otherwise capacity available =2.85 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 53.9752 | -7.378
Errigal [T421] | ERRIGAL (517000) 38 kV STATION | Errigal [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 13.8 |  | --> | 9.5 | 0 | 5.5 | 0 | 0 | Constrained, otherwise capacity available =4.04 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.0567 | -7.0805
Finea [T421,T422] | FINEA (587000) 38 kV STATION | Finea [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 13.8 |  | --> | 6.2 | 2.375 | 5 | 0 | 0 |  | --> |  | Shankill [T141,T142] | SHANKILL |  | 53.7997 | -7.3943
Clones [T41,T42] | CLONES (246000) 38 kV STATION | Clones [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 13.8 |  | --> | 6.2 | 2.375 | 1.5 | 0 | 0 | Constrained, otherwise capacity available =2.09 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 54.1892 | -7.2291
Ballyjamesduff [T41,T42] | BALLYJAMESDUFF (139000) 38 kV STATION | Ballyjamesduff [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4 | 13.8 |  | --> | 12.4 | 4.75 | 6.1 | 0 | 0 | Constrained, otherwise capacity available =4.51 MW | --> |  | Shankill [T141,T142] | SHANKILL |  | 53.8459 | -7.202
Kilrush [T41,T42] | KILRUSH (095000) 38 kV STATION | Kilrush [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.7 | 14.4 |  | --> | 6.2 | 2.375 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =2.77 MW | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.655 | -9.4708
Milltown Malbay [T42] | MILLTOWN MALBAY (439000) 38 kV STATION | Milltown Malbay [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.8 | 14.4 |  | --> | 4.8 | 0 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =2.26 MW | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.8439 | -9.4124
Kilkee [T41] | KILKEE (275000) 38 kV STATION | Kilkee [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.1 | 14.4 |  | --> | 4.8 | 0 | 5.7 | 0 | 0 |  | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.6854 | -9.6296
Tullabrack [T421,T422] | TULLABRACK (722000) 110 kV STATION | Tullabrack [T421,T422] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 14.4 | 14.4 | Constrained, otherwise capacity available =15 MVA | --> | 12.4 | 4.75 | 0 | 0 | 0 | Constrained, otherwise capacity available =12.35 MW | --> |  | Tullabrack [T141] | TULLABRACK |  | 52.6666 | -9.462
Watling Street [T41,T42] | WATLING STREET (361000) 38 kV STATION | Watling Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 14.7 |  | --> | 12.4 | 4.75 | 8.3 | 1.8 | 4.793 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3469 | -6.2808
Camden Row [T41] | CAMDEN ROW (103000) 38 kV STATION | Camden Row [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 0 | 14.7 |  | --> | 14.2 | 0 | 0.2 | 10.2 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3344 | -6.2628
Newmarket (dr) [T41] | NEWMARKET (DR) (217000) 38 kV STATION | Newmarket (dr) [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 14.7 |  | --> | 9.5 | 0 | 0.5 | 6.6 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | FRANCIS STREET |  | 53.3347 | -6.2819
Marrowbone Lane [T42] | MARROWBONE LANE (128000) 38 kV STATION | Marrowbone Lane [T42] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 1.5 | 14.7 |  | --> | 14.2 | 0 | 0.3 | 10.6 | 0 |  | --> |  | Mesh: Red [InciT141,FranT142] | INCHICORE 220KV |  | 53.3353 | -6.2922
Inchicore Central [T43,T45] | INCHICORE CENTRAL (081000) 110 kV STATION | Inchicore Central [T43,T45] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3 | 14.7 |  | --> | 12.4 | 4.75 | 1.4 | 8.2 | 4.819 |  | --> |  | Mesh: Red [InciT141,FranT142] | INCHICORE 220KV |  | 53.3333 | -6.3419
Kingsbridge [T41,T42] | KINGSBRIDGE (107000) 38 kV STATION | Kingsbridge [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.6 | 14.7 |  | --> | 12.4 | 4.75 | 0.2 | 7.4 | 4.939 |  | --> |  | Mesh: Red [InciT141,FranT142] | INCHICORE 220KV |  | 53.343 | -6.2973
Smearla [T41,T42] | SMEARLA (018000) 38 kV STATION | Smearla [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.8 | 14.8 |  | --> | 12.4 | 4.75 | 4.4 | 0 | 0 | Constrained, otherwise capacity available =5.58 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.4372 | -9.446
Ballybunion [T424] | BALLYBUNION (363000) 38 kV STATION | Ballybunion [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 8.4 | 14.8 |  | --> | 9.5 | 0 | 10 | 0 | 0 |  | --> |  | Trien [T141,T142] | TRIEN |  | 52.4988 | -9.6482
Abbeyfeale [T42] | ABBEYFEALE (429000) 38 kV STATION | Abbeyfeale [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.3 | 14.8 |  | --> | 4.8 | 0 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =2.68 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.387 | -9.2926
Ballybunion [T421,T422] | BALLYBUNION (363000) 38 kV STATION | Ballybunion [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3.3 | 14.8 |  | --> | 6.2 | 2.375 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =3.21 MW | --> |  | Trien [T141,T142] | TRIEN |  | 52.4988 | -9.6482
Abbeyfeale [T421] | ABBEYFEALE (429000) 38 kV STATION | Abbeyfeale [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 5.8 | 14.8 |  | --> | 9.5 | 0 | 9.8 | 0 | 0 |  | --> |  | Trien [T141,T142] | TRIEN |  | 52.387 | -9.2926
Macroom [T422] | MACROOM (630000) 110 kV STATION | Macroom [T422] | 110 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 3.75 | 0 | 16.1 |  | --> | 3.3 | 0 | 12.5 | 0 | 0 |  | --> |  | Macroom [T142] | MACROOM |  | 51.8936 | -8.8878
Lee Bridge [T41,T42] | LEE BRIDGE (176000) 38 kV STATION | Lee Bridge [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 7.6 | 16.1 |  | --> | 6.2 | 4.75 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =3.19 MW | --> |  | Macroom [T142] | MACROOM |  | 51.8978 | -8.9379
Cregg Road [T41,T42] | CREGG ROAD (181000) 38 kV STATION | Cregg Road [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0 | 16.9 |  | --> | 2.5 | 0.95 | 1.3 | 0.1 | 1.001 |  | --> |  | Ballydine [T141] | BALLYDINE |  | 52.354 | -7.4099
Deerpark [T41,T42] | DEERPARK (033000) 38 kV STATION | Deerpark [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 16.9 |  | --> | 6.2 | 2.375 | 6.9 | 0 | 2.43 |  | --> |  | Ballydine [T141] | BALLYDINE |  | 52.3507 | -7.4248
Castletownroche [T41] | CASTLETOWNROCHE (080000) 38 kV STATION | Castletownroche [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.2 | 18.1 |  | --> | 4.8 | 0 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =3.47 MW | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1709 | -8.465
Scarteen [T41,T42] | SCARTEEN (211000) 38 kV STATION | Scarteen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 18.1 |  | --> | 6.2 | 2.375 | 5.5 | 0 | 0 |  | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1463 | -8.6725
Buttevant [T41,T42] | BUTTEVANT (024000) 38 kV STATION | Buttevant [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.1 | 18.1 |  | --> | 6.2 | 2.375 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =3.18 MW | --> |  | Mallow [T141,T142] | MALLOW |  | 52.2276 | -8.6577
Mallow [T41,T42] | MALLOW (689000) 110 kV STATION | Mallow [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.6 | 18.1 |  | --> | 12.4 | 4.75 | 2.6 | 0 | 0 | Constrained, otherwise capacity available =7.38 MW | --> |  | Mallow [T141,T142] | MALLOW |  | 52.1463 | -8.6155
Ardfinnan [T424] | ARDFINNAN (386000) 38 kV STATION | Ardfinnan [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 18.2 |  | --> | 9.5 | 0 | 6.2 | 0 | 0 | Constrained, otherwise capacity available =3.26 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3019 | -7.8809
Ardfinnan [T421] | ARDFINNAN (386000) 38 kV STATION | Ardfinnan [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.5 | 18.2 |  | --> | 4.8 | 0 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =1.92 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3019 | -7.8809
Ardfinnan [T42] | ARDFINNAN (386000) 38 kV STATION | Ardfinnan [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 3.9 | 18.2 |  | --> | 4.8 | 0 | 3 | 0 | 0 | Constrained, otherwise capacity available =1.69 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3019 | -7.8809
Cashel [T41,T42] | CASHEL (169000) 38 kV STATION | Cashel [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.9 | 18.2 |  | --> | 12.4 | 4.75 | 3 | 0 | 0 | Constrained, otherwise capacity available =7.34 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.5019 | -7.8903
Cahir [T41,T42] | CAHIR (668000) 110 kV STATION | Cahir [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 6.2 | 18.2 |  | --> | 12.4 | 4.75 | 6.1 | 0 | 0 | Constrained, otherwise capacity available =3.43 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.3824 | -7.8857
Kilshanny [T41,T42] | KILSHANNY (125000) 38 kV STATION | Kilshanny [T41,T42] | 38 kV | _ | MV | 2x2 MVA @ 10 kV | 4 | --> | 3 | 0.2 | 18.2 |  | --> | 2.5 | 0.95 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =0.23 MW | --> |  | Cahir [T141,T142] | CAHIR |  | 52.2627 | -8.2479
Bray [T41,T42] | BRAY (002000) 38 kV STATION | Bray [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.4 | 19.8 |  | --> | 12.4 | 4.75 | 3.9 | 5.2 | 4.843 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.195 | -6.1243
Boghall Road [T41,T42] | BOGHALL ROAD (969000) 38 kV STATION | Boghall Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.5 | 19.8 |  | --> | 12.4 | 4.75 | 1.9 | 7.2 | 4.845 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.1834 | -6.1028
Little Bray [T41,T42] | LITTLE BRAY (223000) 38 kV STATION | Little Bray [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 19.8 |  | --> | 12.4 | 4.75 | 3.7 | 4.4 | 4.899 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.2051 | -6.1369
Greystones [T41,T42] | GREYSTONES (071000) 38 kV STATION | Greystones [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 19.8 |  | --> | 12.4 | 4.75 | 7.1 | 0.6 | 4.929 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.1386 | -6.0918
Kilcoole [T41,T42] | KILCOOLE (498000) 38 kV STATION | Kilcoole [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.6 | 19.8 |  | --> | 12.4 | 4.75 | 3.3 | 7 | 4.788 |  | --> |  | Fassaroe [T141,T142] | FASSAROE |  | 53.0942 | -6.0848
Cookstown [T101,T102] | COOKSTOWN (672000) 110 kV STATION | Cookstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.9 | 198.6 |  | --> | 24.7 | 9.5 | 1.2 | 17.2 | 9.676 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2947 | -6.3826
Cherrywood [T101,T102] | CHERRYWOOD (499000) 110 kV STATION | Cherrywood [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 30 | 198.6 |  | --> | 24.7 | 9.5 | 0 | 24.7 | 9.5 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2412 | -6.1614
Pottery Road [T101,T102] | POTTERY ROAD (317000) 110 kV STATION | Pottery Road [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.4 | 198.6 |  | --> | 24.7 | 9.5 | 2.9 | 15.5 | 9.674 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2765 | -6.1586
Cherrywood [T141,T142] | CHERRYWOOD (499000) 110 kV STATION | Cherrywood [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 70.4 | 198.6 |  | --> | 77.8 | 0 | 8.1 | 66.1 | 0 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2412 | -6.1614
Central Park [T101,T102] | CENTRAL PARK (993000) 110 kV STATION | Central Park [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 15.2 | 198.6 |  | --> | 24.7 | 9.5 | 0.6 | 19.6 | 9.593 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2678 | -6.2094
Carrickmines [T141,T142] | CARRICKMINES (649000) 220 kV STATION | Carrickmines [T141,T142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 1.2 | 198.6 |  | --> | 77.8 | 0 | 35.6 | 18.6 | 0 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2549 | -6.1921
Taney [T101,T102] | TANEY (953000) 110 kV STATION | Taney [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 19.5 | 198.6 |  | --> | 24.7 | 9.5 | 0.8 | 21.9 | 9.52 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.2846 | -6.2385
Fassaroe [T141,T142] | FASSAROE (678000) 110 kV STATION | Fassaroe [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 19.8 | 198.6 |  | --> | 77.8 | 0 | 19.9 | 42 | 0 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 53.191 | -6.1672
Ballybeg [T101,T102] | BALLYBEG (781000) 110 kV STATION | Ballybeg [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 11.6 | 198.6 |  | --> | 24.7 | 9.5 | 24.5 | 0 | 9.573 |  | --> |  | Carrickmines [T2101,T2103,T2104] | CARRICKMINES |  | 52.9969 | -6.1046
Curra [T41] | CURRA (528000) 38 kV STATION | Curra [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.6 | 2 |  | --> | 4.8 | 0 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =2.9 MW | --> |  | Somerset [T142] | SOMERSET |  | 53.1308 | -8.4456
Ballycrossaun [T421,T422] | BALLYCROSSAUN (250000) 38 kV STATION | Ballycrossaun [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 1.3 | 2 |  | --> | 6.2 | 2.375 | 4.7 | 0 | 0 | Constrained, otherwise capacity available =0.65 MW | --> |  | Somerset [T142] | SOMERSET |  | 53.161 | -8.1805
Loughrea [T41,T42] | LOUGHREA (132000) 38 kV STATION | Loughrea [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 2 |  | --> | 6.2 | 2.375 | 7.8 | 0 | 0 |  | --> |  | Somerset [T142] | SOMERSET |  | 53.2119 | -8.5846
Ballinasloe [T41,T42] | BALLINASLOE (118000) 38 kV STATION | Ballinasloe [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2 | 2 | Constrained, otherwise capacity available =2.73 MVA | --> | 6.2 | 2.375 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =3.72 MW | --> |  | Somerset [T142] | SOMERSET |  | 53.3136 | -8.1996
Longford [T421,T422] | LONGFORD (049000) 38 kV STATION | Longford [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0.2 | 2.8 |  | --> | 12.4 | 4.75 | 9.7 | 0 | 0 |  | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.745 | -7.8022
Roosky [T41] | ROOSKY (434000) 38 kV STATION | Roosky [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.3 | 2.8 |  | --> | 4.8 | 0 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =2.9 MW | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.8405 | -7.9198
Garranacanty [T421,T422] | GARRANACANTY (036000) 38 kV STATION | Garranacanty [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 2.8 |  | --> | 12.4 | 4.75 | 4.2 | 0 | 0 | Constrained, otherwise capacity available =1.73 MW | --> |  | Tipperary [T141] | TIPPERARY |  | 52.4853 | -8.1521
Kilross Road [T421] | KILROSS ROAD (213000) 38 kV STATION | Kilross Road [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.4 | 2.8 |  | --> | 4.8 | 0 | 4.4 | 0 | 0 |  | --> |  | Tipperary [T141] | TIPPERARY |  | 52.4642 | -8.1856
Garryspillane [T41] | GARRYSPILLANE (292000) 38 kV STATION | Garryspillane [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 2.8 |  | --> | 4.8 | 0 | 6.1 | 0 | 0 |  | --> |  | Tipperary [T141] | TIPPERARY |  | 52.3983 | -8.3769
Glebe [T41,T42] | GLEBE (416000) 38 kV STATION | Glebe [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.8 | 2.8 | Constrained, otherwise capacity available =2.97 MVA | --> | 12.4 | 4.75 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =6.61 MW | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.7374 | -7.793
Edgeworthstown [T421,T422] | EDGEWORTHSTOWN (130000) 38 kV STATION | Edgeworthstown [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.5 | 2.8 |  | --> | 12.4 | 4.75 | 4.5 | 0 | 0 | Constrained, otherwise capacity available =6.05 MW | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.7144 | -7.6198
Kilross Road [T42] | KILROSS ROAD (213000) 38 kV STATION | Kilross Road [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.8 | 2.8 | Constrained, otherwise capacity available =3.11 MVA | --> | 4.8 | 0 | 0.3 | 0 | 0 | Constrained, otherwise capacity available =4.2 MW | --> |  | Tipperary [T141] | TIPPERARY |  | 52.4642 | -8.1856
Carrigaline [T41,T42] | CARRIGALINE (166000) 38 kV STATION | Carrigaline [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 20.5 |  | --> | 6.2 | 2.375 | 4.7 | 0 | 2.446 |  | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8185 | -8.3894
Ringaskiddy 110kv [T42] | RINGASKIDDY 110KV (603000) 110 kV STATION | Ringaskiddy 110kv [T42] | 110 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4.3 | 20.5 |  | --> | 9.5 | 0 | 1.3 | 6.1 | 0 | Constrained, otherwise capacity available =7.4 MW | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8315 | -8.3406
Factory Cross [T41,T42] | FACTORY CROSS (370000) 38 kV STATION | Factory Cross [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 10.8 | 20.5 |  | --> | 12.4 | 4.75 | 0.2 | 6.1 | 4.767 | Constrained, otherwise capacity available =10.83 MW | --> |  | Barnahely [T141,T142] | BARNAHELY |  | 51.8186 | -8.3341
Marshes [T423] | MARSHES (358000) 38 kV STATION | Marshes [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 21 |  | --> | 9.5 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =9.5 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9768 | -6.3937
Castleblayney [T41,T42] | CASTLEBLAYNEY (184000) 38 kV STATION | Castleblayney [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.4 | 21 |  | --> | 12.4 | 4.75 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =7.78 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.1291 | -6.7624
Ballybailie [T41,T42] | BALLYBAILIE (269000) 38 kV STATION | Ballybailie [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 21 |  | --> | 1.2 | 1.1875 | 1.8 | 0 | 0 |  | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.8666 | -6.5464
Jenkinstown [T421,T422] | JENKINSTOWN (264000) 38 kV STATION | Jenkinstown [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 4.2 | 21 |  | --> | 6.2 | 2.375 | 2 | 0 | 0 | Constrained, otherwise capacity available =2.89 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0241 | -6.2867
Marshes [T41,T42] | MARSHES (358000) 38 kV STATION | Marshes [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.1 | 21 |  | --> | 12.4 | 4.75 | 5.3 | 0 | 0 | Constrained, otherwise capacity available =4.34 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9768 | -6.3937
Bush [T421,T422] | BUSH (488000) 38 kV STATION | Bush [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3.5 | 21 |  | --> | 6.2 | 2.375 | 5.6 | 0 | 0 |  | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0011 | -6.1682
Coes Road [T41,T42] | COES ROAD (367000) 38 kV STATION | Coes Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.7 | 21 |  | --> | 6.2 | 2.375 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =3.06 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9951 | -6.3872
Little Mills [T41] | LITTLE MILLS (316000) 38 kV STATION | Little Mills [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1 | 21 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =2.39 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 53.9887 | -6.4426
Ramparts [T41,T42] | RAMPARTS (175000) 38 kV STATION | Ramparts [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.7 | 21 |  | --> | 12.4 | 4.75 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =8.99 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0064 | -6.4047
Dundalk [T41,T42] | DUNDALK (062000) 110 kV STATION | Dundalk [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.3 | 21 |  | --> | 12.4 | 4.75 | 2.9 | 0 | 0 | Constrained, otherwise capacity available =6.64 MW | --> |  | Dundalk [T141,T142] | DUNDALK |  | 54.0085 | -6.4194
Leeson Street [T41,T42] | LEESON STREET (342000) 38 kV STATION | Leeson Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1 | 21.3 |  | --> | 12.4 | 4.75 | 0.3 | 8.1 | 4.881 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | MILLTOWN (DR) |  | 53.3276 | -6.2585
Pembroke [T41,T42,T43,T44] | PEMBROKE (094000) 38 kV STATION | Pembroke [T41,T42,T43,T44] | 38 kV | _ | MV | 4x10 MVA @ 10 kV | 40 | --> | 36 | 9.3 | 21.3 |  | --> | 38 | 4.75 | 1.6 | 30 | 4.799 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | RINGSEND |  | 53.3428 | -6.2348
Merrion Square [T41,T42] | MERRION SQUARE (105000) 38 kV STATION | Merrion Square [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.4 | 21.3 |  | --> | 12.4 | 4.75 | 0.1 | 9.2 | 4.834 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | RINGSEND |  | 53.3348 | -6.2424
Donnybrook [T41,T42] | DONNYBROOK (308000) 38 kV STATION | Donnybrook [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 21.3 |  | --> | 12.4 | 4.75 | 0.8 | 7.3 | 4.901 |  | --> |  | Mesh: Blue [RingT141,MiltT141] | MILLTOWN (DR) |  | 53.3177 | -6.226
Knockmullen [T42,T421] | KNOCKMULLEN (957000) 38 kV STATION | Knockmullen [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 21.5 |  | --> | 12.4 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =4.62 MW | --> |  | Great Island [T141,T142] | GREAT ISLAND |  | 52.3846 | -6.944
Bealistown [T421,T422] | BEALISTOWN (375000) 38 kV STATION | Bealistown [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0.2 | 21.5 |  | --> | 6.2 | 2.375 | 8.5 | 0 | 0 |  | --> |  | Great Island [T141,T142] | GREAT ISLAND |  | 52.263 | -6.8747
Shillelagh [T421,T422] | SHILLELAGH (708000) 38 kV STATION | Shillelagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 22 |  | --> | 6.2 | 2.375 | 6.6 | 0 | 0 |  | --> |  | Carlow [T141,T142] | CARLOW |  | 52.7481 | -6.5265
Tullow [T421,T422] | TULLOW (293000) 38 kV STATION | Tullow [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0.4 | 22 |  | --> | 12.4 | 4.75 | 13.7 | 0 | 0 |  | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8003 | -6.7211
Pollerton [T41,T42] | POLLERTON (242000) 38 kV STATION | Pollerton [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 22 |  | --> | 12.4 | 4.75 | 4.8 | 0 | 0 | Constrained, otherwise capacity available =2.64 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8431 | -6.9178
Tullow [T424] | TULLOW (293000) 38 kV STATION | Tullow [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 22 |  | --> | 9.5 | 0 | 7.3 | 0 | 0 | Constrained, otherwise capacity available =2.25 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8003 | -6.7211
Graigue [T41,T42] | GRAIGUE (012000) 38 kV STATION | Graigue [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2 | 22 |  | --> | 12.4 | 4.75 | 3 | 0 | 0 | Constrained, otherwise capacity available =6.27 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.8391 | -6.9503
Bagenalstown [T421,T422] | BAGENALSTOWN (389000) 38 kV STATION | Bagenalstown [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.8 | 22 |  | --> | 12.4 | 4.75 | 7.9 | 0 | 0 | Constrained, otherwise capacity available =1.48 MW | --> |  | Carlow [T141,T142] | CARLOW |  | 52.7094 | -6.9462
Clontarf [T42] | CLONTARF (283000) 38 kV STATION | Clontarf [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0 | 22.3 |  | --> | 9.5 | 0 | 2.9 | 4.6 | 0 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3668 | -6.2009
Santry [T41,T42] | SANTRY (315000) 38 kV STATION | Santry [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 22.3 |  | --> | 12.4 | 4.75 | 1.6 | 7.6 | 4.836 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3928 | -6.2492
Coolock [T41,T42] | COOLOCK (277000) 38 kV STATION | Coolock [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.8 | 22.3 |  | --> | 12.4 | 4.75 | 1.2 | 8.7 | 4.804 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.4 | -6.2054
East Wall Road [T41,T42] | EAST WALL ROAD (112000) 38 kV STATION | East Wall Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 6.6 | 22.3 |  | --> | 12.4 | 4.75 | 0.4 | 8.5 | 4.853 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | MCDERMOTT |  | 53.3506 | -6.2282
Ballymun [T41,T42] | BALLYMUN (093000) 38 kV STATION | Ballymun [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.9 | 22.3 |  | --> | 12.4 | 4.75 | 1.9 | 8.4 | 4.789 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | FINGLAS |  | 53.3839 | -6.2803
Fairview [T41] | FAIRVIEW (113000) 38 kV STATION | Fairview [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 1.9 | 22.3 |  | --> | 14.2 | 0 | 1.9 | 9.5 | 0 |  | --> |  | Mesh: Purple [FingT141,McDrT141] | MCDERMOTT |  | 53.3678 | -6.2215
Turlough Road [T41,T42] | TURLOUGH ROAD (042000) 38 kV STATION | Turlough Road [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.9 | 25 |  | --> | 6.2 | 2.375 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =3.74 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8678 | -9.2871
Swinford [T41,T42] | SWINFORD (043000) 38 kV STATION | Swinford [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.4 | 25 |  | --> | 6.2 | 2.375 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =2.69 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.9394 | -8.9569
Turlough Road [T43] | TURLOUGH ROAD (042000) 38 kV STATION | Turlough Road [T43] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.5 | 25 |  | --> | 4.8 | 0 | 0.3 | 0 | 0 | Constrained, otherwise capacity available =3.6 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8678 | -9.2871
Westport [T421,T422] | WESTPORT (116000) 38 kV STATION | Westport [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 8.1 | 25 |  | --> | 12.4 | 4.75 | 3.2 | 0 | 0 | Constrained, otherwise capacity available =7.15 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.7963 | -9.4872
Kiltimagh [T41] | KILTIMAGH (349000) 38 kV STATION | Kiltimagh [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.4 | 25 |  | --> | 4.8 | 0 | 5.6 | 0 | 0 |  | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8517 | -9.0045
Windsor [T421,T422] | WINDSOR (608000) 38 kV STATION | Windsor [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 25 |  | --> | 6.2 | 2.375 | 6 | 0 | 0 |  | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8745 | -9.2555
Knockaphunta [T41,T42] | KNOCKAPHUNTA (979000) 38 kV STATION | Knockaphunta [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 25 |  | --> | 6.2 | 2.375 | 2.4 | 0 | 0 | Constrained, otherwise capacity available =1.71 MW | --> |  | Castlebar [T141,T142] | CASTLEBAR |  | 53.8352 | -9.3173
Manor Street [T41,T42] | MANOR STREET (346000) 38 kV STATION | Manor Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.5 | 25.2 |  | --> | 12.4 | 4.75 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =6.23 MW | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2516 | -7.1197
Waterford [T41,T42] | WATERFORD (808000) 110 kV STATION | Waterford [T41,T42] | 110 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.8 | 25.2 |  | --> | 6.2 | 2.375 | 0.3 | 0 | 0 | Constrained, otherwise capacity available =5 MW | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2685 | -7.1278
Tycor [T41,T42] | TYCOR (286000) 38 kV STATION | Tycor [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1 | 25.2 |  | --> | 6.2 | 2.375 | 1.1 | 0 | 0 | Constrained, otherwise capacity available =3.54 MW | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2539 | -7.1345
Rosbercon [T41,T42] | ROSBERCON (179000) 38 kV STATION | Rosbercon [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0.2 | 25.2 |  | --> | 1.2 | 1.1875 | 6 | 0 | 0 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.3977 | -6.9486
Granagh [T41,T42] | GRANAGH (226000) 38 kV STATION | Granagh [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 25.2 |  | --> | 6.2 | 2.375 | 6.1 | 0 | 0 |  | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2752 | -7.1748
Mount Misery [T41,T42] | MOUNT MISERY (009000) 38 kV STATION | Mount Misery [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 8.2 | 25.2 |  | --> | 12.4 | 4.75 | 7.6 | 0 | 0 | Constrained, otherwise capacity available =1.81 MW | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2659 | -7.1183
Belview [T421,T422] | BELVIEW (605000) 38 kV STATION | Belview [T421,T422] | 38 kV | _ | MV | 2x15 MVA @ 20 kV | 30 | --> | 22.5 | 3.8 | 25.2 |  | --> | 18.5 | 7.125 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =11.4 MW | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.2631 | -7.0386
Rosbercon [T424] | ROSBERCON (179000) 38 kV STATION | Rosbercon [T424] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.2 | 25.2 |  | --> | 14.2 | 0 | 14.3 | 0 | 0 | Constrained, otherwise capacity available =0.27 MW | --> |  | Waterford [T141,T142] | WATERFORD |  | 52.3977 | -6.9486
Carrickmacross [T41,T42] | CARRICKMACROSS (210000) 38 kV STATION | Carrickmacross [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 26.4 |  | --> | 12.4 | 4.75 | 4.2 | 0 | 0 | Constrained, otherwise capacity available =4.16 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9862 | -6.7454
Mullagh [T41,T42] | MULLAGH (428000) 38 kV STATION | Mullagh [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.1 | 26.4 |  | --> | 6.2 | 2.375 | 0 | 0 | 0 | Constrained, otherwise capacity available =6.06 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8021 | -6.9384
Tullynamalra [T41,T42] | TULLYNAMALRA (466000) 38 kV STATION | Tullynamalra [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.1 | 26.4 |  | --> | 6.2 | 2.375 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =1.55 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 54.0666 | -6.8262
Bailieboro [T423] | BAILIEBORO (138000) 38 kV STATION | Bailieboro [T423] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13 | 26.4 |  | --> | 14.2 | 0 | 13.5 | 0 | 0 | Constrained, otherwise capacity available =0.86 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9033 | -6.9569
Virginia [T41,T42] | VIRGINIA (452000) 38 kV STATION | Virginia [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 26.4 |  | --> | 6.2 | 2.375 | 1 | 0 | 0 | Constrained, otherwise capacity available =1.92 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8085 | -7.0378
Mullagh [T44] | MULLAGH (428000) 38 kV STATION | Mullagh [T44] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.7 | 26.4 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =2.72 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8021 | -6.9384
Kingscourt [T423] | KINGSCOURT (122000) 38 kV STATION | Kingscourt [T423] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13 | 26.4 |  | --> | 14.2 | 0 | 11.5 | 0 | 0 | Constrained, otherwise capacity available =3.05 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8796 | -6.7932
Bailieboro [T41,T42] | BAILIEBORO (138000) 38 kV STATION | Bailieboro [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.2 | 26.4 |  | --> | 6.2 | 2.375 | 7.2 | 0 | 0 |  | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9033 | -6.9569
Kingscourt [T41,T42] | KINGSCOURT (122000) 38 kV STATION | Kingscourt [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.2 | 26.4 |  | --> | 12.4 | 4.75 | 2.6 | 0 | 0 | Constrained, otherwise capacity available =7.96 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.8796 | -6.7932
Shercock [T41,T42] | SHERCOCK (539000) 38 kV STATION | Shercock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.5 | 26.4 |  | --> | 6.2 | 2.375 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =2.56 MW | --> |  | Meath Hill [T141,T142] | MEATH HILL |  | 53.9961 | -6.9203
Ballytivnan [T41,T42] | BALLYTIVNAN (445000) 38 kV STATION | Ballytivnan [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.5 | 27.1 |  | --> | 12.4 | 4.75 | 2.5 | 5.9 | 4.883 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2887 | -8.4701
Oakfield [T41,T42] | OAKFIELD (240000) 38 kV STATION | Oakfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 5.8 | 27.1 |  | --> | 12.4 | 4.75 | 3.8 | 6.7 | 4.78 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2573 | -8.505
Finisklin [T41,T42] | FINISKLIN (511000) 38 kV STATION | Finisklin [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 27.1 |  | --> | 6.2 | 2.375 | 0.1 | 2.9 | 2.54 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.2766 | -8.4905
Aghagad [T41,T42] | AGHAGAD (645000) 38 kV STATION | Aghagad [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.1 | 27.1 |  | --> | 6.2 | 2.375 | 1.9 | 3.6 | 2.386 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.3731 | -8.524
Ballymote [T41] | BALLYMOTE (496000) 38 kV STATION | Ballymote [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.3 | 27.1 |  | --> | 4.8 | 0 | 5.1 | 0 | 0 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.0922 | -8.5182
Collooney [T421,T422] | COLLOONEY (117000) 38 kV STATION | Collooney [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 3.75 | 0 | 27.1 |  | --> | 3.1 | 1.1875 | 5.9 | 0 | 1.369 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.1747 | -8.4924
Manorhamilton [T422] | MANORHAMILTON (345000) 38 kV STATION | Manorhamilton [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 27.1 |  | --> | 4.8 | 0 | 1.7 | 1.4 | 0 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.299 | -8.1601
Manorhamilton [T424] | MANORHAMILTON (345000) 38 kV STATION | Manorhamilton [T424] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13 | 27.1 |  | --> | 14.2 | 0 | 13.6 | 0.7 | 0 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.299 | -8.1601
Cranmore [T41,T42] | CRANMORE (046000) 38 kV STATION | Cranmore [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 27.1 |  | --> | 6.2 | 2.375 | 0.9 | 2.2 | 2.529 |  | --> |  | Sligo [T141,T142] | SLIGO |  | 54.272 | -8.4578
Kilflynn [T41,T42] | KILFLYNN (137000) 38 kV STATION | Kilflynn [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.7 | 28.6 |  | --> | 6.2 | 2.375 | 5.1 | 0 | 0 | Constrained, otherwise capacity available =0.61 MW | --> |  | Tralee [T141,T142] | TRALEE |  | 52.342 | -9.6307
Castleisland [T41,T42] | CASTLEISLAND (233000) 38 kV STATION | Castleisland [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 28.6 |  | --> | 6.2 | 2.375 | 9.4 | 0 | 0 |  | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2368 | -9.4809
Causeway [T41,T42] | CAUSEWAY (483000) 38 kV STATION | Causeway [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2 | 28.6 |  | --> | 6.2 | 2.375 | 6.7 | 0 | 0 |  | --> |  | Tralee [T141,T142] | TRALEE |  | 52.4138 | -9.7472
Ballyrickard [T41,T42] | BALLYRICKARD (173000) 38 kV STATION | Ballyrickard [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.2 | 28.6 |  | --> | 12.4 | 4.75 | 3 | 0 | 0 | Constrained, otherwise capacity available =6.3 MW | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2743 | -9.7183
Ballyard [T41,T42] | BALLYARD (278000) 38 kV STATION | Ballyard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.5 | 28.6 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =2.26 MW | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2539 | -9.7005
Ballybeggan [T43,T44] | BALLYBEGGAN (462000) 38 kV STATION | Ballybeggan [T43,T44] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 28.6 |  | --> | 12.4 | 4.75 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =5.78 MW | --> |  | Tralee [T141,T142] | TRALEE |  | 52.2752 | -9.6854
Greenhills [T42] | GREENHILLS (290000) 38 kV STATION | Greenhills [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 3.3 | 29.5 |  | --> | 9.5 | 0 | 1.4 | 6.8 | 0 |  | --> |  | Mesh: Green [MiltT142,InciT143] | INCHICORE 220KV |  | 53.3166 | -6.3254
Kimmage [T41,T42] | KIMMAGE (145000) 38 kV STATION | Kimmage [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.9 | 29.5 |  | --> | 12.4 | 4.75 | 3.6 | 5.5 | 4.842 |  | --> |  | Mesh: Green [MiltT142,InciT143] | INCHICORE 220KV |  | 53.3076 | -6.3089
Crumlin [T41,T42] | CRUMLIN (259000) 38 kV STATION | Crumlin [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.9 | 29.5 |  | --> | 12.4 | 4.75 | 1.5 | 8.5 | 4.801 |  | --> |  | Mesh: Green [MiltT142,InciT143] | INCHICORE 220KV |  | 53.3214 | -6.3094
Garville Avenue [T42] | GARVILLE AVENUE (230000) 38 kV STATION | Garville Avenue [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 0.9 | 29.5 |  | --> | 9.5 | 0 | 1.3 | 6.4 | 0 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3199 | -6.2755
Templeogue [T41,T42] | TEMPLEOGUE (146000) 38 kV STATION | Templeogue [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.5 | 29.5 |  | --> | 12.4 | 4.75 | 4.7 | 5.5 | 4.794 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3005 | -6.308
Dodder Road [T42] | DODDER ROAD (330000) 38 kV STATION | Dodder Road [T42] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 2.9 | 29.5 |  | --> | 9.5 | 0 | 2 | 6.1 | 0 |  | --> |  | Mesh: Green [MiltT142,InciT143] | MILLTOWN (DR) |  | 53.3014 | -6.2613
Bunclody [T424] | BUNCLODY (470000) 38 kV STATION | Bunclody [T424] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 3.1 | 3.1 | Constrained, otherwise capacity available =8.82 MVA | --> | 9.5 | 0 | 7.5 | 0 | 0 | Constrained, otherwise capacity available =2.29 MW | --> |  | Crane [T141] | CRANE |  | 52.6432 | -6.6311
Bunclody [T421,T422] | BUNCLODY (470000) 38 kV STATION | Bunclody [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 1.1 | 3.1 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =2.14 MW | --> |  | Crane [T141] | CRANE |  | 52.6432 | -6.6311
Ferns [T421] | FERNS (075000) 38 kV STATION | Ferns [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.6 | 3.1 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =2.47 MW | --> |  | Crane [T141] | CRANE |  | 52.5871 | -6.5101
Bellfield [T41,T42] | BELLFIELD (006000) 38 kV STATION | Bellfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.1 | 3.1 | Constrained, otherwise capacity available =5.19 MVA | --> | 12.4 | 4.75 | 2.7 | 0 | 0 | Constrained, otherwise capacity available =7.82 MW | --> |  | Crane [T141] | CRANE |  | 52.5084 | -6.5651
Ramstown [T41,T42] | RAMSTOWN (287000) 38 kV STATION | Ramstown [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3 | 3.1 |  | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =3.61 MW | --> |  | Crane [T141] | CRANE |  | 52.6637 | -6.3193
Enniskeane [T41,T42] | ENNISKEANE (090000) 38 kV STATION | Enniskeane [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 3.2 | 3.2 | Constrained, otherwise capacity available =5.59 MVA | --> | 6.2 | 2.375 | 7.9 | 0 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.744 | -8.9399
Bealnablath [T421] | BEALNABLATH (235000) 38 kV STATION | Bealnablath [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 0 | 3.2 |  | --> | 9.5 | 0 | 11.4 | 0 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.8282 | -8.8934
Timoleague [T41] | TIMOLEAGUE (163000) 38 kV STATION | Timoleague [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.2 |  | --> | 4.8 | 0 | 6.9 | 0 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.6825 | -8.7671
Bealnablath [T422] | BEALNABLATH (235000) 38 kV STATION | Bealnablath [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 3.2 | 3.2 | Constrained, otherwise capacity available =4.5 MVA | --> | 4.8 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =4.75 MW | --> |  | Bandon [T141,T142] | BANDON |  | 51.8282 | -8.8934
Kinsale [T41,T42] | KINSALE (225000) 38 kV STATION | Kinsale [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 3.2 |  | --> | 6.2 | 2.375 | 7.4 | 0 | 0 |  | --> |  | Bandon [T141,T142] | BANDON |  | 51.7193 | -8.5569
Delvin [T41,T42] | DELVIN (123000) 38 kV STATION | Delvin [T41,T42] | 38 kV | _ | MV | 1x3.2,1x5 MVA @ 10 kV | 8.2 | --> | 2.4 | 0 | 3.4 |  | --> | 2 | 1.1875 | 2 | 0 | 0 |  | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.6035 | -7.0789
Loughanalla [T41,T42] | LOUGHANALLA (613000) 38 kV STATION | Loughanalla [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.3 | 3.4 |  | --> | 6.2 | 2.375 | 4 | 0 | 0 | Constrained, otherwise capacity available =1.11 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.6761 | -7.3044
Newbrook [T42] | NEWBROOK (465000) 38 kV STATION | Newbrook [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 3.4 |  | --> | 4.8 | 0 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =1.83 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.5214 | -7.3821
Ballinderry [T41,T422] | BALLINDERRY (383000) 38 kV STATION | Ballinderry [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 3.4 |  | --> | 12.4 | 4.75 | 9 | 0 | 0 |  | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.5134 | -7.3166
Oldcastle [T41,T422] | OLDCASTLE (538000) 38 kV STATION | Oldcastle [T41,T422] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.7 | 3.4 |  | --> | 6.2 | 2.375 | 5 | 0 | 0 | Constrained, otherwise capacity available =0.25 MW | --> |  | Mullingar [T141,T142] | MULLINGAR |  | 53.7816 | -7.1696
Killinick [T421,T422] | KILLINICK (298000) 38 kV STATION | Killinick [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 1.4 | 33.6 |  | --> | 12.4 | 4.75 | 12.3 | 0 | 0 |  | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.2534 | -6.4483
Mulgannon [T41,T42] | MULGANNON (174000) 38 kV STATION | Mulgannon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 33.6 |  | --> | 12.4 | 4.75 | 2.6 | 0 | 0 | Constrained, otherwise capacity available =2.81 MW | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.3204 | -6.4567
Monfin [T41,T42] | MONFIN (297000) 38 kV STATION | Monfin [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 5.25 | 1.3 | 33.6 |  | --> | 2.5 | 2.375 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =1.02 MW | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.4915 | -6.5881
Carriglawn [T41,T42] | CARRIGLAWN (188000) 38 kV STATION | Carriglawn [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.1 | 33.6 |  | --> | 6.2 | 2.375 | 1.6 | 0 | 0 | Constrained, otherwise capacity available =2.63 MW | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.3464 | -6.4809
Clonard [T41,T42] | CLONARD (547000) 38 kV STATION | Clonard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9 | 33.6 |  | --> | 6.2 | 2.375 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =2.82 MW | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.3265 | -6.4957
Clonroche [T421,T422] | CLONROCHE (515000) 38 kV STATION | Clonroche [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 33.6 |  | --> | 6.2 | 2.375 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =1.7 MW | --> |  | Wexford [T141,T142] | WEXFORD |  | 52.4438 | -6.6979
Monkstown [T41,T42] | MONKSTOWN (222000) 38 kV STATION | Monkstown [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.5 | 36.3 |  | --> | 12.4 | 4.75 | 3.8 | 5.5 | 4.831 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.292 | -6.1664
Belfield [T41,T42] | BELFIELD (310000) 38 kV STATION | Belfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.9 | 36.3 |  | --> | 12.4 | 4.75 | 2.4 | 5.1 | 4.948 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.31 | -6.2168
Dun Laoghaire [T41,T42] | DUN LAOGHAIRE (284000) 38 kV STATION | Dun Laoghaire [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 4.4 | 36.3 |  | --> | 12.4 | 4.75 | 1 | 9 | 4.801 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.2966 | -6.1497
Dundrum [T41,T42] | DUNDRUM (134000) 38 kV STATION | Dundrum [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 36.3 |  | --> | 12.4 | 4.75 | 5.6 | 3.5 | 4.844 |  | --> |  | Blackrock [T141,T142] | BLACKROCK |  | 53.2963 | -6.2488
Sheriff Street [T41,T42] | SHERIFF STREET (588000) 38 kV STATION | Sheriff Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 7.6 | 36.8 |  | --> | 12.4 | 4.75 | 0.3 | 10.7 | 4.769 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3488 | -6.2392
Bedford Row [T41,T42,T43,T44] | BEDFORD ROW (068000) 38 kV STATION | Bedford Row [T41,T42,T43,T44] | 38 kV | _ | MV | 4x15 MVA @ 10 kV | 60 | --> | 54 | 28.4 | 36.8 |  | --> | 57 | 7.125 | 1 | 48.3 | 7.173 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3437 | -6.2564
South King Street [T41,T42] | SOUTH KING STREET (241000) 38 kV STATION | South King Street [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.4 | 36.8 |  | --> | 12.4 | 4.75 | 0 | 8.7 | 4.86 |  | --> |  | Mesh: Brown [FranT141,RingT144] | FRANCIS STREET |  | 53.3423 | -6.269
Kanturk [T41,T42] | KANTURK (119000) 38 kV STATION | Kanturk [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 38.7 |  | --> | 6.2 | 2.375 | 7.4 | 0 | 0.221 |  | --> |  | Glenlara [T142] | GLENLARA |  | 52.165 | -8.917
Cloonbannin [T421] | CLOONBANNIN (070000) 38 kV STATION | Cloonbannin [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.2 | 38.7 |  | --> | 4.8 | 0 | 0.4 | 0.2 | 0 | Constrained, otherwise capacity available =3.98 MW | --> |  | Glenlara [T142] | GLENLARA |  | 52.1372 | -9.0556
Cloonbannin [T42] | CLOONBANNIN (070000) 38 kV STATION | Cloonbannin [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.6 | 38.7 |  | --> | 4.8 | 0 | 0.7 | 0.2 | 0 | Constrained, otherwise capacity available =3.61 MW | --> |  | Glenlara [T142] | GLENLARA |  | 52.1372 | -9.0556
Newmarket (sr) [T41,T42] | NEWMARKET (SR) (481000) 38 kV STATION | Newmarket (sr) [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 4.2 | 38.7 |  | --> | 6.2 | 2.375 | 1.2 | 0.2 | 0.221 | Constrained, otherwise capacity available =3.35 MW | --> |  | Glenlara [T142] | GLENLARA |  | 52.21 | -8.9982
Toomevara [T42] | TOOMEVARA (385000) 38 kV STATION | Toomevara [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.2 | 4.1 |  | --> | 4.8 | 0 | 6.9 | 0 | 0 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8734 | -8.0397
Nenagh [T422] | NENAGH (946000) 110 kV STATION | Nenagh [T422] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 4.1 | 4.1 | Constrained, otherwise capacity available =8.74 MVA | --> | 9.5 | 0 | 9.6 | 0 | 0 | Constrained, otherwise capacity available =0.21 MW | --> |  | Nenagh [T141] | NENAGH |  | 52.8664 | -8.1737
Kyleeragh [T41,T42] | KYLEERAGH (421000) 38 kV STATION | Kyleeragh [T41,T42] | 38 kV | _ | MV | 1x5,1x10 MVA @ 10 kV | 15 | --> | 11.25 | 0 | 4.1 |  | --> | 6.2 | 4.75 | 2.5 | 0 | 0 |  | --> |  | Nenagh [T141] | NENAGH |  | 52.8742 | -8.1818
Nenagh [T41,T42] | NENAGH (946000) 110 kV STATION | Nenagh [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3 | 4.1 |  | --> | 12.4 | 4.75 | 5.5 | 0 | 0 | Constrained, otherwise capacity available =4.22 MW | --> |  | Nenagh [T141] | NENAGH |  | 52.8664 | -8.1737
Ballymacarry [T421] | BALLYMACARRY (607000) 38 kV STATION | Ballymacarry [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2 | 4.9 |  | --> | 4.8 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =3.88 MW | --> |  | Trillick [T141] | TRILLICK |  | 55.1278 | -7.4459
Moville [T421,T422] | MOVILLE (405000) 38 kV STATION | Moville [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 3 | 4.9 |  | --> | 6.2 | 2.375 | 5.4 | 0 | 0 | Constrained, otherwise capacity available =0.01 MW | --> |  | Trillick [T141] | TRILLICK |  | 55.1994 | -7.0601
Buncrana [T421,T422] | BUNCRANA (204000) 38 kV STATION | Buncrana [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 4.9 |  | --> | 6.2 | 2.375 | 40.1 | 0 | 0 |  | --> |  | Trillick [T141] | TRILLICK |  | 55.1336 | -7.437
Carndonagh [T421,T422] | CARNDONAGH (266000) 38 kV STATION | Carndonagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 4.9 |  | --> | 6.2 | 2.375 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =2.07 MW | --> |  | Trillick [T141] | TRILLICK |  | 55.2526 | -7.26
Castletownbere [T42] | CASTLETOWNBERE (513000) 38 kV STATION | Castletownbere [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 3.6 | 42.2 |  | --> | 4.8 | 0 | 0.1 | 0 | 0 | Constrained, otherwise capacity available =4.35 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.6478 | -9.9112
Castletownbere [T421] | CASTLETOWNBERE (513000) 38 kV STATION | Castletownbere [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0.9 | 42.2 |  | --> | 4.8 | 0 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =1.96 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.6478 | -9.9112
Bantry [T41,T42] | BANTRY (111000) 38 kV STATION | Bantry [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 42.2 |  | --> | 6.2 | 2.375 | 5.8 | 0 | 0 |  | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.6828 | -9.4156
Ballylicky [T421] | BALLYLICKY (728000) 110 kV STATION | Ballylicky [T421] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 42.2 |  | --> | 9.5 | 0 | 5.8 | 0 | 0 | Constrained, otherwise capacity available =3.98 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.7191 | -9.4235
Glengarriff [T421] | GLENGARRIFF (384000) 38 kV STATION | Glengarriff [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 3.5 | 42.2 |  | --> | 4.8 | 0 | 0.4 | 0 | 0 | Constrained, otherwise capacity available =4.14 MW | --> |  | Ballylicky [T142] | BALLYLICKY |  | 51.7541 | -9.535
Dunmanway [T422,T43] | DUNMANWAY (676000) 110 kV STATION | Dunmanway [T422,T43] | 110 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 7.8 | 43.9 |  | --> | 12.4 | 4.75 | 8.4 | 0 | 0 | Constrained, otherwise capacity available =2.68 MW | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.7167 | -9.0773
Ross Carbery [T41,T42] | ROSS CARBERY (352000) 38 kV STATION | Ross Carbery [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.9 | 43.9 |  | --> | 6.2 | 2.375 | 6.3 | 0 | 0 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.6071 | -9.0157
Ballydehob [T421] | BALLYDEHOB (535000) 38 kV STATION | Ballydehob [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 43.9 |  | --> | 4.8 | 0 | 2.1 | 0 | 0 | Constrained, otherwise capacity available =1.78 MW | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.5611 | -9.485
Skibbereen [T41,T42] | SKIBBEREEN (164000) 38 kV STATION | Skibbereen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 43.9 |  | --> | 6.2 | 2.375 | 7.5 | 0 | 0 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.567 | -9.255
Clonakilty [T41,T42] | CLONAKILTY (165000) 38 kV STATION | Clonakilty [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 43.9 |  | --> | 6.2 | 2.375 | 3.7 | 0 | 0 |  | --> |  | Dunmanway [T141,T142] | DUNMANWAY |  | 51.6279 | -8.8884
Killeshandra [T41,T42] | KILLESHANDRA (265000) 38 kV STATION | Killeshandra [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.6 | 44.4 |  | --> | 6.2 | 2.375 | 0.9 | 2.6 | 2.494 |  | --> |  | Gortawee [T142] | GORTAWEE |  | 54.026 | -7.5458
Ballyconnell [T421,T422] | BALLYCONNELL (571000) 38 kV STATION | Ballyconnell [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0.1 | 44.4 |  | --> | 6.2 | 2.375 | 8.3 | 0 | 2.461 |  | --> |  | Gortawee [T142] | GORTAWEE |  | 54.1215 | -7.6071
Trimms Lane [T41,T42] | TRIMMS LANE (427000) 38 kV STATION | Trimms Lane [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 3.5 | 44.9 |  | --> | 12.4 | 4.75 | 1.4 | 6 | 4.824 | Constrained, otherwise capacity available =8.09 MW | --> |  | Salthill [T141] | SALTHILL |  | 53.2643 | -9.0739
Ballybay [T41,T42] | BALLYBAY (061000) 38 kV STATION | Ballybay [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2 | 5.9 |  | --> | 6.2 | 2.375 | 1.3 | 0 | 0 | Constrained, otherwise capacity available =3.34 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.1259 | -6.9173
Lisdrum [T422] | LISDRUM (624000) 110 kV STATION | Lisdrum [T422] | 110 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.1 | 5.9 |  | --> | 4.8 | 0 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =3.11 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2488 | -6.9279
Emyvale [T422] | EMYVALE (502000) 38 kV STATION | Emyvale [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 5.9 |  | --> | 4.8 | 0 | 1.4 | 0 | 0 | Constrained, otherwise capacity available =2.4 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.355 | -7.0362
Drumbear [T41,T42] | DRUMBEAR (156000) 38 kV STATION | Drumbear [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 5.9 |  | --> | 6.2 | 2.375 | 1.9 | 0 | 0 | Constrained, otherwise capacity available =2.25 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2263 | -6.9847
Telaydon [T42,T421] | TELAYDON (415000) 38 kV STATION | Telaydon [T42,T421] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 2.5 | 5.9 |  | --> | 12.4 | 4.75 | 3.7 | 0 | 0 | Constrained, otherwise capacity available =5.68 MW | --> |  | Lisdrum [T141,T142] | LISDRUM |  | 54.2688 | -6.9899
Belmullet [T421] | BELMULLET (500000) 38 kV STATION | Belmullet [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.6 | 51.8 |  | --> | 4.8 | 0 | 13.2 | 0 | 0 |  | --> |  | Bellacorick [T141] | BELLACORICK |  | 54.2057 | -9.9522
Belmullet [T422] | BELMULLET (500000) 38 kV STATION | Belmullet [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 51.8 |  | --> | 9.5 | 0 | 0 | 9.5 | 0 |  | --> |  | Bellacorick [T141] | BELLACORICK |  | 54.2057 | -9.9522
Bangor Erris [T421] | BANGOR ERRIS (206000) 38 kV STATION | Bangor Erris [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.8 | 51.8 |  | --> | 4.8 | 0 | 0.3 | 4.1 | 0 |  | --> |  | Bellacorick [T141] | BELLACORICK |  | 54.1568 | -9.7598
Kilmagig [T42] | KILMAGIG (301000) 38 kV STATION | Kilmagig [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.4 | 53.6 |  | --> | 4.8 | 0 | 0.8 | 0 | 0 | Constrained, otherwise capacity available =3.3 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.8551 | -6.2193
Kilmartin [T41] | KILMARTIN (332000) 38 kV STATION | Kilmartin [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.5 | 53.6 |  | --> | 4.8 | 0 | 1.7 | 0 | 0 | Constrained, otherwise capacity available =1.34 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 53.0421 | -6.0865
Tinahask [T41,T42] | TINAHASK (362000) 38 kV STATION | Tinahask [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 53.6 |  | --> | 6.2 | 2.375 | 2.8 | 0 | 0 | Constrained, otherwise capacity available =1.09 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.7921 | -6.1724
Garden City [T41,T42] | GARDEN CITY (005000) 38 kV STATION | Garden City [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 53.6 |  | --> | 6.2 | 2.375 | 2.3 | 0 | 0 | Constrained, otherwise capacity available =0.82 MW | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.6682 | -6.3057
Rathdrum [T42] | RATHDRUM (602000) 38 kV STATION | Rathdrum [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 53.6 |  | --> | 4.8 | 0 | 6.7 | 0 | 0 |  | --> |  | Arklow [T141,T142] | ARKLOW |  | 52.9421 | -6.2583
Multeen [T421] | MULTEEN (752000) 38 kV STATION | Multeen [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 8.4 | 54.7 |  | --> | 9.5 | 0 | 9.7 | 0 | 0 | Constrained, otherwise capacity available =0.13 MW | --> |  | Cauteen [T141] | CAUTEEN |  | 52.6482 | -8.1336
Booltiagh [T421] | BOOLTIAGH (887000) 110 kV STATION | Booltiagh [T421] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 12.6 | 56.4 |  | --> | 14.2 | 0 | 13.7 | 0 | 0 | Constrained, otherwise capacity available =0.77 MW | --> |  | Booltiagh [T143] | BOOLTIAGH |  | 52.7667 | -9.2556
Ringsend [T101,T102] | RINGSEND (998000) 110 kV STATION | Ringsend [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 17.8 | 57.1 |  | --> | 24.7 | 9.5 | 0.1 | 18.8 | 9.653 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3447 | -6.2005
North Quays [T101,T102,T103] | NORTH QUAYS (981000) 110 kV STATION | North Quays [T101,T102,T103] | 110 kV | _ | MV | 3x20 MVA @ 10 kV | 60 | --> | 54 | 14.3 | 57.1 |  | --> | 57 | 9.5 | 0.9 | 48.8 | 9.557 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3532 | -6.2311
Misery Hill [T101,T102] | MISERY HILL (980000) 110 kV STATION | Misery Hill [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 9 | 57.1 |  | --> | 24.7 | 9.5 | 0.2 | 18 | 9.688 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3412 | -6.2458
Mesh: Brown [FranT141,RingT144] | FRANCIS STREET (733000) 110 kV STATION | Mesh: Brown [FranT141,RingT144] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 36.8 | 57.1 |  | --> | 77.8 | 0 | 1.3 | 63.7 | 0 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3374 | -6.2793
Mesh: Blue [RingT141,MiltT141] | MILLTOWN (DR) (069000) 110 kV STATION | Mesh: Blue [RingT141,MiltT141] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 21.3 | 57.1 |  | --> | 77.8 | 0 | 2.8 | 56.9 | 0 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3176 | -6.2456
Harolds Cross [T101,T102] | HAROLDS CROSS (343000) 110 kV STATION | Harolds Cross [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 10 | 57.1 |  | --> | 24.7 | 9.5 | 1.7 | 16.8 | 9.673 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3321 | -6.2726
Blackrock [T141,T142] | BLACKROCK (338000) 110 kV STATION | Blackrock [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 36.3 | 57.1 |  | --> | 77.8 | 0 | 29.1 | 29.9 | 0 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.2934 | -6.1704
Trinity [T101,T102] | TRINITY (494000) 110 kV STATION | Trinity [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.2 | 57.1 |  | --> | 24.7 | 9.5 | 0.1 | 18.1 | 9.684 |  | --> |  | Poolbeg [TF3,TF4] | POOLBEG |  | 53.3456 | -6.2435
Charlestown [T41] | CHARLESTOWN (078000) 38 kV STATION | Charlestown [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0 | 6.1 |  | --> | 4.8 | 0 | 3.4 | 0 | 0 | Constrained, otherwise capacity available =0.84 MW | --> |  | Tonroe [T142] | TONROE |  | 53.9536 | -8.7931
Ballaghaderreen [T41,T42] | BALLAGHADERREEN (433000) 38 kV STATION | Ballaghaderreen [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0 | 6.1 |  | --> | 6.2 | 2.375 | 6 | 0 | 0 |  | --> |  | Tonroe [T142] | TONROE |  | 53.919 | -8.5832
Tubbercurry [T41,T42] | TUBBERCURRY (355000) 38 kV STATION | Tubbercurry [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0.1 | 6.1 |  | --> | 1.2 | 1.1875 | 1.3 | 0 | 0 |  | --> |  | Tonroe [T142] | TONROE |  | 54.0575 | -8.7418
Gurteen [T41] | GURTEEN (045000) 38 kV STATION | Gurteen [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.4 | 6.1 |  | --> | 4.8 | 0 | 1 | 0 | 0 | Constrained, otherwise capacity available =3.31 MW | --> |  | Tonroe [T142] | TONROE |  | 53.9883 | -8.5242
Banagher [T41,T42] | BANAGHER (305000) 38 kV STATION | Banagher [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0.3 | 6.4 |  | --> | 3.1 | 1.1875 | 0.9 | 0 | 0 | Constrained, otherwise capacity available =1.4 MW | --> |  | Dallow [T141] | DALLOW |  | 53.1941 | -8.0279
Birr [T41,T422] | BIRR (056000) 38 kV STATION | Birr [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0.9 | 6.4 |  | --> | 12.4 | 4.75 | 10.2 | 0 | 0 |  | --> |  | Dallow [T141] | DALLOW |  | 53.0789 | -7.8766
Lumcloon [T421,T422] | LUMCLOON (147000) 38 kV STATION | Lumcloon [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 9 | 4.6 | 6.4 |  | --> | 9.5 | 9.5 | 6.3 | 0 | 0 | Constrained, otherwise capacity available =2.68 MW | --> |  | Dallow [T141] | DALLOW |  | 53.2308 | -7.8337
Dallow [T421] | DALLOW (673000) 110 kV STATION | Dallow [T421] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 6.4 | 6.4 | Constrained, otherwise capacity available =8.81 MVA | --> | 9.5 | 0 | 10 | 0 | 0 |  | --> |  | Dallow [T141] | DALLOW |  | 53.1167 | -7.9381
Spiddal [T42] | SPIDDAL (443000) 38 kV STATION | Spiddal [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 4.5 | 6.9 |  | --> | 4.8 | 0 | 3.3 | 1.7 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.2582 | -9.3209
Spiddal [T423] | SPIDDAL (443000) 38 kV STATION | Spiddal [T423] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 6.9 | 6.9 | Constrained, otherwise capacity available =9 MVA | --> | 9.5 | 0 | 0 | 9.5 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.2582 | -9.3209
Carraroe [T42] | CARRAROE (475000) 38 kV STATION | Carraroe [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 0.4 | 6.9 |  | --> | 4.8 | 0 | 4.5 | 0 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.2748 | -9.5356
Screeb [T41] | SCREEB (366000) 110 kV STATION | Screeb [T41] | 110 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.5 | 6.9 |  | --> | 4.8 | 0 | 0.9 | 3 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.3894 | -9.5708
Clifden [T41,T42] | CLIFDEN (252000) 38 kV STATION | Clifden [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 1.3 | 6.9 |  | --> | 6.2 | 2.375 | 1.7 | 2.5 | 2.442 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4846 | -10.0109
Oughterard [T41,T42] | OUGHTERARD (444000) 38 kV STATION | Oughterard [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 6.5 | 6.9 |  | --> | 6.2 | 2.375 | 2.1 | 4.1 | 2.375 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4249 | -9.3117
Recess [T41] | RECESS (581000) 38 kV STATION | Recess [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.8 | 6.9 |  | --> | 4.8 | 0 | 0.7 | 3.6 | 0 |  | --> |  | Screeb [T142] | SCREEB |  | 53.4543 | -9.7555
Srah [T41,T42] | SRAH (484000) 38 kV STATION | Srah [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 2.4 | 65.1 |  | --> | 6.2 | 2.375 | 6.5 | 0 | 2.419 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2828 | -7.5199
Srah [T43] | SRAH (484000) 38 kV STATION | Srah [T43] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 3.3 | 65.1 |  | --> | 9.5 | 0 | 0.9 | 7.2 | 0 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2828 | -7.5199
Clonminch [T41,T422] | CLONMINCH (650000) 38 kV STATION | Clonminch [T41,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 0 | 65.1 |  | --> | 12.4 | 4.75 | 3.6 | 4.1 | 4.931 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2586 | -7.4934
Clara [T421,T422] | CLARA (051000) 38 kV STATION | Clara [T421,T422] | 38 kV | _ | MV | 2x10 MVA @ 20 kV | 20 | --> | 15 | 2.2 | 65.1 |  | --> | 12.4 | 4.75 | 6.6 | 2.9 | 4.821 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.3524 | -7.5884
Clonminch [T421] | CLONMINCH (650000) 38 kV STATION | Clonminch [T421] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 9 | 65.1 |  | --> | 9.5 | 4.75 | 9.9 | 0 | 4.75 |  | --> |  | Thornsberry [T141,T142] | THORNSBERRY |  | 53.2586 | -7.4934
Killybegs [T422] | KILLYBEGS (255000) 38 kV STATION | Killybegs [T422] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 0 | 66.6 |  | --> | 14.2 | 0 | 4.3 | 0 | 0 | Constrained, otherwise capacity available =7.63 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.6554 | -8.4439
Killybegs [T41] | KILLYBEGS (255000) 38 kV STATION | Killybegs [T41] | 38 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 13.5 | 66.6 |  | --> | 14.2 | 0 | 4.2 | 0 | 0 | Constrained, otherwise capacity available =10.35 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.6554 | -8.4439
Kilcar [T41] | KILCAR (501000) 38 kV STATION | Kilcar [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 2.1 | 66.6 |  | --> | 4.8 | 0 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =0.55 MW | --> |  | Binbane [T141,T142] | BINBANE |  | 54.6385 | -8.572
Glenties [T41,T42] | GLENTIES (216000) 38 kV STATION | Glenties [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 66.6 |  | --> | 1.2 | 1.1875 | 1.3 | 0 | 0 |  | --> |  | Binbane [T141,T142] | BINBANE |  | 54.7693 | -8.3082
Inchicore County 220/110 kV [T2101,T2106] | INCHICORE 220KV (964000) 220 kV STATION | Inchicore County 220/110 kV [T2101,T2106] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 0 | 67.1 |  | --> | 308.8 | 0 | 160.9 | 41.2 | 0 |  | --> |  | Transmission Source | INCHICORE 220KV |  | 53.3313 | -6.3371
Ballygar [T41,T42] | BALLYGAR (324000) 38 kV STATION | Ballygar [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 7.6 |  | --> | 3.1 | 1.1875 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =0.71 MW | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.5265 | -8.306
Moate [T41,T42] | MOATE (073000) 38 kV STATION | Moate [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 7.6 |  | --> | 3.1 | 1.1875 | 2.4 | 0 | 0 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.386 | -7.7209
Ballymahon [T41,T42] | BALLYMAHON (076000) 38 kV STATION | Ballymahon [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 7.5 | 0.1 | 7.6 |  | --> | 6.2 | 2.375 | 1.5 | 0 | 0 | Constrained, otherwise capacity available =3.01 MW | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.5965 | -7.804
Garrycastle [T41,T42] | GARRYCASTLE (976000) 38 kV STATION | Garrycastle [T41,T42] | 38 kV | _ | MV | 2x15 MVA @ 10 kV | 30 | --> | 22.5 | 7.6 | 7.6 | Constrained, otherwise capacity available =9.45 MVA | --> | 18.5 | 7.125 | 2.5 | 0 | 0 | Constrained, otherwise capacity available =12.25 MW | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.426 | -7.8904
Glenamaddy [T422] | GLENAMADDY (526000) 38 kV STATION | Glenamaddy [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 0 | 7.6 |  | --> | 4.8 | 0 | 6.1 | 0 | 0 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.6158 | -8.5908
Creagh [T421,T422] | CREAGH (519000) 38 kV STATION | Creagh [T421,T422] | 38 kV | _ | MV | 2x5 MVA @ 20 kV | 10 | --> | 7.5 | 0 | 7.6 |  | --> | 6.2 | 2.375 | 7.5 | 0 | 0 |  | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.3294 | -8.2061
Athlone [T41,T42] | ATHLONE (897000) 110 kV STATION | Athlone [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 7.6 |  | --> | 12.4 | 4.75 | 4.3 | 0 | 0 | Constrained, otherwise capacity available =1.35 MW | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.4256 | -7.9672
Bushfield [T41,T42] | BUSHFIELD (478000) 38 kV STATION | Bushfield [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 6.5 | 7.6 |  | --> | 12.4 | 4.75 | 3.1 | 0 | 0 | Constrained, otherwise capacity available =5.32 MW | --> |  | Athlone [T141,T142] | ATHLONE |  | 53.4341 | -7.9082
Milford (mwr) [T422] | MILFORD (MWR) (236000) 38 kV STATION | Milford (mwr) [T422] | 38 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 6.2 | 7.9 |  | --> | 9.5 | 0 | 10 | 0 | 0 |  | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.3333 | -8.8451
Newport [T421] | NEWPORT (260000) 38 kV STATION | Newport [T421] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.7 | 7.9 |  | --> | 4.8 | 0 | 1.8 | 2.3 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8858 | -9.5017
Charleville [T421,T422] | CHARLEVILLE (456000) 110 kV STATION | Charleville [T421,T422] | 110 kV | _ | MV | 1x10,1x15 MVA @ 20 kV | 25 | --> | 18.75 | 3 | 7.9 |  | --> | 12.4 | 7.125 | 16 | 0 | 0 |  | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.325 | -8.7025
Kilmallock [T41,T42] | KILMALLOCK (412000) 38 kV STATION | Kilmallock [T41,T42] | 38 kV | _ | MV | 2x5 MVA @ 10 kV | 10 | --> | 3.75 | 0 | 7.9 |  | --> | 3.1 | 1.1875 | 1.2 | 0 | 0 | Constrained, otherwise capacity available =0.9 MW | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.4131 | -8.5896
Milford (mwr) [T41] | MILFORD (MWR) (236000) 38 kV STATION | Milford (mwr) [T41] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.9 | 7.9 |  | --> | 4.8 | 0 | 0.7 | 0 | 0 | Constrained, otherwise capacity available =3.6 MW | --> |  | Charleville [T142] | CHARLEVILLE |  | 52.3333 | -8.8451
Achill [T422] | ACHILL (495000) 38 kV STATION | Achill [T422] | 38 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 1.5 | 7.9 |  | --> | 4.8 | 0 | 1.1 | 2.7 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.9495 | -9.9002
Carrowbeg [T421] | CARROWBEG (699000) 110 kV STATION | Carrowbeg [T421] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 3 | 7.9 |  | --> | 9.5 | 0 | 0 | 5.9 | 0 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8048 | -9.5016
Carrowbeg [T41,T42] | CARROWBEG (699000) 110 kV STATION | Carrowbeg [T41,T42] | 110 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 7.3 | 7.9 |  | --> | 12.4 | 4.75 | 1.8 | 8.6 | 4.785 |  | --> |  | Carrowbeg [T142] | CARROWBEG |  | 53.8048 | -9.5016
Ballinclea [T41] | BALLINCLEA (396000) 38 kV STATION | Ballinclea [T41] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 4 | 70.4 |  | --> | 9.5 | 0 | 2.2 | 6.3 | 0 |  | --> |  | Cherrywood [T141,T142] | CHERRYWOOD |  | 53.2683 | -6.1245
Sallynoggin Road [T41,T42] | SALLYNOGGIN ROAD (133000) 38 kV STATION | Sallynoggin Road [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 1.2 | 70.4 |  | --> | 12.4 | 4.75 | 5.9 | 3.8 | 4.815 |  | --> |  | Cherrywood [T141,T142] | CHERRYWOOD |  | 53.281 | -6.1416
Carrigtwohill [T42] | CARRIGTWOHILL (351000) 38 kV STATION | Carrigtwohill [T42] | 38 kV | _ | MV | 1x5 MVA @ 10 kV | 5 | --> | 4.5 | 1.3 | 8.8 |  | --> | 4.8 | 0 | 0 | 0 | 0 | Constrained, otherwise capacity available =2.86 MW | --> |  | Cow Cross [T142] | COW CROSS |  | 51.8928 | -8.2549
Carrigtwohill [T421] | CARRIGTWOHILL (351000) 38 kV STATION | Carrigtwohill [T421] | 38 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 8.8 | 8.8 | Constrained, otherwise capacity available =13.5 MVA | --> | 14.2 | 0 | 10 | 0 | 0 | Constrained, otherwise capacity available =4.25 MW | --> |  | Cow Cross [T142] | COW CROSS |  | 51.8928 | -8.2549
Mesh: Orange [FingT142,McDrT142] | FINGLAS (318000) 220 kV STATION | Mesh: Orange [FingT142,McDrT142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | 87.1 |  | --> | 77.8 | 0 | 7.9 | 48.4 | 0 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.4075 | -6.3161
Mesh: Purple [FingT141,McDrT141] | FINGLAS (318000) 220 kV STATION | Mesh: Purple [FingT141,McDrT141] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 22.3 | 87.1 |  | --> | 77.8 | 0 | 10 | 52 | 0 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.4075 | -6.3161
Artane [T101,T102] | ARTANE (966000) 110 kV STATION | Artane [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13 | 87.1 |  | --> | 24.7 | 9.5 | 4.1 | 17.7 | 9.54 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3903 | -6.1919
Cabra [T101,T102] | CABRA (231000) 110 kV STATION | Cabra [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 11.1 | 87.1 |  | --> | 24.7 | 9.5 | 3.3 | 16.8 | 9.599 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3695 | -6.294
Wolfe Tone Street [T101,T102] | WOLFE TONE STREET (769000) 110 kV STATION | Wolfe Tone Street [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 2.6 | 87.1 |  | --> | 24.7 | 9.5 | 0.4 | 16.7 | 9.751 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3519 | -6.2732
Pelletstown [T101,T102] | PELLETSTOWN (092000) 110 kV STATION | Pelletstown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.9 | 87.1 |  | --> | 24.7 | 9.5 | 4.9 | 15.7 | 9.579 |  | --> |  | Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS |  | 53.3788 | -6.3228
Aghamore [T41,T42] | AGHAMORE (124000) 38 kV STATION | Aghamore [T41,T42] | 38 kV | _ | MV | 1x2,1x5 MVA @ 10 kV | 7 | --> | 3.75 | 0 | 9.2 |  | --> | 1.2 | 1.1875 | 1.6 | 0 | 0 |  | --> |  | Lanesboro [T141] | LANESBORO |  | 53.6642 | -7.9855
Roscommon [T41,T42] | ROSCOMMON (136000) 38 kV STATION | Roscommon [T41,T42] | 38 kV | _ | MV | 2x10 MVA @ 10 kV | 20 | --> | 15 | 0 | 9.2 |  | --> | 12.4 | 4.75 | 11.7 | 0 | 0 |  | --> |  | Lanesboro [T141] | LANESBORO |  | 53.6305 | -8.1528
Roscommon [T423] | ROSCOMMON (136000) 38 kV STATION | Roscommon [T423] | 38 kV | _ | MV | 1x10 MVA @ 10 kV | 10 | --> | 9 | 9 | 9.2 |  | --> | 9.5 | 0 | 5 | 0 | 0 | Constrained, otherwise capacity available =4.85 MW | --> |  | Lanesboro [T141] | LANESBORO |  | 53.6305 | -8.1528
Navan [T141,T142] | NAVAN (694000) 110 kV STATION | Navan [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 12.8 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 68.1 | 0 | 0 |  | --> |  | Transmission Source | NAVAN |  | 53.705 | -6.7109
Baltrasna [T121,T122] | BALTRASNA (371000) 110 kV STATION | Baltrasna [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 26.5 | 0 | 9.604 |  | --> |  | Transmission Source | BALTRASNA |  | 53.5535 | -6.4343
Newbridge [T141,T142] | NEWBRIDGE (695000) 110 kV STATION | Newbridge [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 34.4 | 0 | 0 |  | --> |  | Transmission Source | NEWBRIDGE |  | 53.1981 | -6.8437
Nenagh [T141] | NENAGH (946000) 110 kV STATION | Nenagh [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 4.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 24.5 | 0 | 0 |  | --> |  | Transmission Source | NENAGH |  | 52.8664 | -8.1737
Oughtragh [T141] | OUGHTRAGH (696000) 110 kV STATION | Oughtragh [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 25.1 | 0 | 0 |  | --> |  | Transmission Source | OUGHTRAGH |  | 52.1418 | -9.7044
Bandon [T101,T42] | BANDON (729000) 110 kV STATION | Bandon [T101,T42] | 110 kV | _ | MV | 1x10,1x20 MVA @ 10 kV | 30 | --> | 22.5 | 8.7 | N/A, consult Eirgrid |  | --> | 20 | 0 | 19.3 | 0 | 0 |  | --> |  | Transmission Source | BANDON |  | 51.7661 | -8.722
Bandon [T141,T142] | BANDON (729000) 110 kV STATION | Bandon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 3.2 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 39.7 | 0 | 0 |  | --> |  | Transmission Source | BANDON |  | 51.7661 | -8.722
Moy [T141,T142] | MOY (774000) 110 kV STATION | Moy [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 13 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 28.4 | 0 | 0 |  | --> |  | Transmission Source | MOY |  | 54.1315 | -9.1748
Blake [T142] | BLAKE (120000) 110 kV STATION | Blake [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 20.1 | 0 | 0 |  | --> |  | Transmission Source | BLAKE |  | 53.2952 | -6.8636
Mullingar [T141,T142] | MULLINGAR (693000) 110 kV STATION | Mullingar [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 3.4 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 56.3 | 0 | 0 |  | --> |  | Transmission Source | MULLINGAR |  | 53.5365 | -7.3663
Binbane [T143] | BINBANE (666000) 110 kV STATION | Binbane [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.3 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 0 | 59.8 | 0 |  | --> |  | Transmission Source | BINBANE |  | 54.7253 | -8.2757
Mullingar [T101,T102] | MULLINGAR (693000) 110 kV STATION | Mullingar [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 10.9 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 3.3 | 17.5 | 9.571 |  | --> |  | Transmission Source | MULLINGAR |  | 53.5365 | -7.3663
Mullagharlin [T121,T122] | MULLAGHARLIN (817000) 110 kV STATION | Mullagharlin [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 19.8 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 0.8 | 20.3 | 9.562 |  | --> |  | Transmission Source | MULLAGHARLIN |  | 53.9808 | -6.4054
Monread [T101,T102] | MONREAD (902000) 110 kV STATION | Monread [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 12.6 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 10.8 | 9.8 | 9.578 |  | --> |  | Transmission Source | MONREAD |  | 53.2479 | -6.6529
Trien [T141,T142] | TRIEN (720000) 110 kV STATION | Trien [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 14.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 54 | 0 | 0 |  | --> |  | Transmission Source | TRIEN |  | 52.4203 | -9.4318
Salthill [T101,T102] | SALTHILL (161000) 110 kV STATION | Salthill [T101,T102] | 110 kV | _ | MV | 2x31.5 MVA @ 10 kV | 63 | --> | 47.25 | 11 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 9.5 | 20.4 | 15.191 |  | --> |  | Transmission Source | SALTHILL |  | 53.2718 | -9.073
Arklow [T143] | ARKLOW (917000) 220 kV STATION | Arklow [T143] | 220 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 57.2 | 2.9 | 0 |  | --> |  | Transmission Source | ARKLOW |  | 52.8171 | -6.1411
Arklow [T141,T142] | ARKLOW (917000) 220 kV STATION | Arklow [T141,T142] | 220 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 53.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 99.4 | 0 | 0 |  | --> |  | Transmission Source | ARKLOW |  | 52.8171 | -6.1411
Arklow [T101,T102] | ARKLOW (917000) 220 kV STATION | Arklow [T101,T102] | 220 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 18.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 15.9 | 6.7 | 9.521 |  | --> |  | Transmission Source | ARKLOW |  | 52.8171 | -6.1411
Arigna [T121] | ARIGNA (417000) 110 kV STATION | Arigna [T121] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 8.5 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 17.5 | 0 | 0 |  | --> |  | Transmission Source | ARIGNA |  | 54.0871 | -8.0882
Tonroe [T142] | TONROE (904000) 110 kV STATION | Tonroe [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 28.7 | 0 | 0 |  | --> |  | Transmission Source | TONROE |  | 53.9135 | -8.5866
Ardnagappary [T141] | ARDNAGAPPARY (819000) 110 kV STATION | Ardnagappary [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 11.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 42 | 0 | 0 |  | --> |  | Transmission Source | ARDNAGAPPARY |  | 55.0608 | -8.2543
Ardnacrusha [T141,T142] | ARDNACRUSHA (990000) 110 kV STATION | Ardnacrusha [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 65.7 | 0 | 0 |  | --> |  | Transmission Source | ARDNACRUSHA |  | 52.716 | -8.6233
Trabeg [T101,T102] | TRABEG (701000) 110 kV STATION | Trabeg [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 5.5 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 5.4 | 14.4 | 9.613 |  | --> |  | Transmission Source | TRABEG |  | 51.8856 | -8.4621
Thurles [T141,T142] | THURLES (718000) 110 kV STATION | Thurles [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 13.7 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 54.3 | 0 | 0 |  | --> |  | Transmission Source | THURLES |  | 52.6972 | -7.7687
Tralee [T141,T142] | TRALEE (719000) 110 kV STATION | Tralee [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 28.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 79.3 | 0 | 0 |  | --> |  | Transmission Source | TRALEE |  | 52.2874 | -9.6776
Thornsberry [T141,T142] | THORNSBERRY (717000) 110 kV STATION | Thornsberry [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 65.1 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 38.5 | 35.1 | 0 |  | --> |  | Transmission Source | THORNSBERRY |  | 53.2917 | -7.4657
Ahane [T102] | AHANE (900000) 110 kV STATION | Ahane [T102] | 110 kV | _ | MV | 1x15 MVA @ 10 kV | 15 | --> | 13.5 | 6.8 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 5.8 | 7.1 | 0 |  | --> |  | Transmission Source | AHANE |  | 52.668 | -8.4986
Trien [T143] | TRIEN (720000) 110 kV STATION | Trien [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.8 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 46.3 | 13.8 | 0 |  | --> |  | Transmission Source | TRIEN |  | 52.4203 | -9.4318
Aghada [T721] | AGHADA (631000) 220 kV STATION | Aghada [T721] | 220 kV | _ | MV | 1x5 MVA @ 20 kV | 5 | --> | 4.5 | 2.3 | N/A, consult Eirgrid |  | --> | 4.8 | 0 | 0.9 | 3.5 | 0 |  | --> |  |  | N/A |  | 51.8454 | -8.2168
Trillick [T141] | TRILLICK (721000) 110 kV STATION | Trillick [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 4.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 57.8 | 0 | 0 |  | --> |  | Transmission Source | TRILLICK |  | 55.1182 | -7.4248
Trillick [T142] | TRILLICK (721000) 110 kV STATION | Trillick [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 28 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 30.9 | 0 | 0 |  | --> |  | Transmission Source | TRILLICK |  | 55.1182 | -7.4248
Tullabrack [T141] | TULLABRACK (722000) 110 kV STATION | Tullabrack [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 14.4 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 43.7 | 0 | 0 |  | --> |  | Transmission Source | TULLABRACK |  | 52.6666 | -9.462
Waterford [T141,T142] | WATERFORD (808000) 110 kV STATION | Waterford [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 25.2 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 62.3 | 0 | 0 |  | --> |  | Transmission Source | WATERFORD |  | 52.2685 | -7.1278
Wexford [T121,T122] | WEXFORD (742000) 110 kV STATION | Wexford [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 16.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 6.1 | 15.5 | 9.546 |  | --> |  | Transmission Source | WEXFORD |  | 52.3425 | -6.5476
Wexford [T141,T142] | WEXFORD (742000) 110 kV STATION | Wexford [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 33.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 70.3 | 0 | 0 |  | --> |  | Transmission Source | WEXFORD |  | 52.3425 | -6.5476
Trabeg [T141,T142] | TRABEG (701000) 110 kV STATION | Trabeg [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 26.9 | 0 | 0 |  | --> |  | Transmission Source | TRABEG |  | 51.8856 | -8.4621
Screeb [T142] | SCREEB (366000) 110 kV STATION | Screeb [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 13.2 | 11.4 | 0 |  | --> |  | Transmission Source | SCREEB |  | 53.3894 | -9.5708
Portlaoise [T141,T142] | PORTLAOISE (201000) 110 kV STATION | Portlaoise [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 78.8 | 0 | 0 |  | --> |  | Transmission Source | PORTLAOISE |  | 53.022 | -7.3041
Rathkeale [T141,T142] | RATHKEALE (712000) 110 kV STATION | Rathkeale [T141,T142] | 110 kV | _ | 38 kV | 2x30 MVA @ 38 kV | 60 | --> | 42 | 12.7 | N/A, consult Eirgrid |  | --> | 37 | 0 | 71.5 | 0 | 0 |  | --> |  | Transmission Source | RATHKEALE |  | 52.5406 | -8.9745
Reamore [T141] | REAMORE (197000) 110 kV STATION | Reamore [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 45.1 | 14.5 | 0 |  | --> |  | Transmission Source | REAMORE |  | 52.2973 | -9.5504
Reamore [T142] | REAMORE (197000) 110 kV STATION | Reamore [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.5 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 44.4 | 15.8 | 0 |  | --> |  | Transmission Source | REAMORE |  | 52.2973 | -9.5504
Ballyragget [T142] | BALLYRAGGET (329000) 38 kV STATION | Ballyragget [T142] | 38 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 72.3 | 0 | 0 |  | --> |  | Transmission Source | BALLYRAGGET |  | 52.7962 | -7.3349
Ballyragget [T141] | BALLYRAGGET (329000) 38 kV STATION | Ballyragget [T141] | 38 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 10.3 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 27.4 | 0 | 0 |  | --> |  | Transmission Source | BALLYRAGGET |  | 52.7962 | -7.3349
Richmond [T141,T142] | RICHMOND (713000) 110 kV STATION | Richmond [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 2.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 43.2 | 0 | 0 |  | --> |  | Transmission Source | RICHMOND |  | 53.7492 | -7.8419
Richmond [T421] | RICHMOND (713000) 110 kV STATION | Richmond [T421] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.5 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 11.7 | 2.6 | 0 |  | --> |  | Richmond [T141,T142] | RICHMOND |  | 53.7492 | -7.8419
Ballylicky [T142] | BALLYLICKY (728000) 110 kV STATION | Ballylicky [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 42.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 76 | 0 | 0 |  | --> |  | Transmission Source | BALLYLICKY |  | 51.7191 | -9.4235
Tipperary [T141] | TIPPERARY (806000) 110 kV STATION | Tipperary [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 2.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 29.1 | 0 | 0 |  | --> |  | Transmission Source | TIPPERARY |  | 52.4802 | -8.0759
Ballydine [T141] | BALLYDINE (727000) 110 kV STATION | Ballydine [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 16.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 12.1 | 14.4 | 0 |  | --> |  | Transmission Source | BALLYDINE |  | 52.3562 | -7.5061
Poolbeg [TF3,TF4] | POOLBEG (799000) 220 kV STATION | Poolbeg [TF3,TF4] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 57.1 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 93.1 | 133.4 | 0 |  | --> |  | Transmission Source | POOLBEG |  | 53.3438 | -6.1967
Shankill [T141,T142] | SHANKILL (714000) 110 kV STATION | Shankill [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 13.8 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 84.7 | 0 | 0 |  | --> |  | Transmission Source | SHANKILL |  | 54.0044 | -7.3094
Singland [T101,T102] | SINGLAND (521000) 110 kV STATION | Singland [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.8 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 4 | 16.7 | 9.575 |  | --> |  | Transmission Source | SINGLAND |  | 52.6677 | -8.5792
Sligo [T141,T142] | SLIGO (715000) 110 kV STATION | Sligo [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 27.1 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 40.1 | 14.9 | 0 |  | --> |  | Transmission Source | SLIGO |  | 54.2379 | -8.4592
Somerset [T142] | SOMERSET (716000) 110 kV STATION | Somerset [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 2 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 29.8 | 0 | 0 |  | --> |  | Transmission Source | SOMERSET |  | 53.2595 | -8.2412
Sorne Hill [T122] | SORNE HILL (743000) 110 kV STATION | Sorne Hill [T122] | 110 kV | _ | MV | 1x31.5 MVA @ 20 kV | 31.5 | --> | 28.35 | 27.7 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 25.2 | 5 | 0 |  | --> |  | Transmission Source | SORNE HILL |  | 55.1231 | -7.361
Stratford [T141] | STRATFORD (913000) 110 kV STATION | Stratford [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0.6 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 37 | 0 | 0 |  | --> |  | Transmission Source | STRATFORD |  | 52.9896 | -6.6669
Athy [T101,T102] | ATHY (927000) 110 kV STATION | Athy [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 7.4 | 11.7 | 9.644 |  | --> |  | Transmission Source | ATHY |  | 52.9985 | -7.0167
Athlone [T141,T142] | ATHLONE (897000) 110 kV STATION | Athlone [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 7.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 83.4 | 0 | 0 |  | --> |  | Transmission Source | ATHLONE |  | 53.4256 | -7.9672
Tawnaghmore [T142] | TAWNAGHMORE (952000) 110 kV STATION | Tawnaghmore [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 26.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 30 | 0.1 | 0 |  | --> |  | Transmission Source | TAWNAGHMORE |  | 54.1991 | -9.229
Salthill [T141] | SALTHILL (161000) 110 kV STATION | Salthill [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 44.9 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 50.1 | 6 | 0 |  | --> |  | Transmission Source | SALTHILL |  | 53.2718 | -9.073
Dallow [T141] | DALLOW (673000) 110 kV STATION | Dallow [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 6.4 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 32.1 | 0 | 0 |  | --> |  | Transmission Source | DALLOW |  | 53.1167 | -7.9381
Meath Hill [T141,T142] | MEATH HILL (691000) 110 kV STATION | Meath Hill [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 26.4 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 95.4 | 0 | 0 |  | --> |  | Transmission Source | MEATH HILL |  | 53.8968 | -6.7244
Corderry [T122] | CORDERRY (972000) 110 kV STATION | Corderry [T122] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 55.6 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 61.1 | 0 | 0 |  | --> |  | Transmission Source | CORDERRY |  | 54.204 | -8.1807
Corduff [T121,T122] | CORDUFF (932000) 220 kV STATION | Corduff [T121,T122] | 220 kV | _ | MV | 2x31.5 MVA @ 20 kV | 63 | --> | 47.25 | 41.3 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 0.2 | 38.7 | 14.963 |  | --> |  | Transmission Source | CORDUFF |  | 53.4174 | -6.369
Cow Cross [T102,T41] | COW CROSS (908000) 110 kV STATION | Cow Cross [T102,T41] | 110 kV | _ | MV | 1x15,1x20 MVA @ 10 kV | 35 | --> | 26.25 | 19.7 | N/A, consult Eirgrid |  | --> | 18.5 | 9.5 | 6.4 | 12.1 | 9.5 |  | --> |  | N/A | cow cross |  | 51.8555 | -8.3121
Cow Cross [T142] | COW CROSS (908000) 110 kV STATION | Cow Cross [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 8.8 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 27.9 | 0 | 0 |  | --> |  | Transmission Source | COW CROSS |  | 51.8555 | -8.3121
Crane [T122] | CRANE (886000) 110 kV STATION | Crane [T122] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 4.4 | N/A, consult Eirgrid |  | --> | 19 | 0 | 12.3 | 3.6 | 0 |  | --> |  | Transmission Source | CRANE |  | 52.5377 | -6.502
Marina [T105,T106] | MARINA (794000) 110 kV STATION | Marina [T105,T106] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 4.7 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 1.7 | 18.8 | 9.579 |  | --> |  | Transmission Source | MARINA |  | 51.9025 | -8.4411
Crane [T141] | CRANE (886000) 110 kV STATION | Crane [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 3.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 38.8 | 0 | 0 |  | --> |  | Transmission Source | CRANE |  | 52.5377 | -6.502
Crory [T121] | CRORY (473000) 110 kV STATION | Crory [T121] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 55.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 60.2 | 0 | 0 |  | --> |  | Transmission Source | CRORY |  | 52.569 | -6.5458
Dunfirth [T122] | DUNFIRTH (771000) 110 kV STATION | Dunfirth [T122] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 15 | 3.5 | N/A, consult Eirgrid |  | --> | 13.3 | 0 | 28.3 | 0 | 0 |  | --> |  | Transmission Source | DUNFIRTH |  | 53.3838 | -6.815
Mallow [T141,T142] | MALLOW (689000) 110 kV STATION | Mallow [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 18.1 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 32 | 0 | 0 |  | --> |  | Transmission Source | MALLOW |  | 52.1463 | -8.6155
Coomataggart [T141] | COOMATAGGART (877000) 110 kV STATION | Coomataggart [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 42.6 | 17.5 | 0 |  | --> |  | Transmission Source | COOMATAGGART |  | 51.8805 | -9.324
Macroom [T142] | MACROOM (630000) 110 kV STATION | Macroom [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 16.1 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 55.3 | 0 | 0 |  | --> |  | Transmission Source | MACROOM |  | 51.8936 | -8.8878
Macetown [T101,T102] | MACETOWN (652000) 110 kV STATION | Macetown [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 7.4 | 5.2 | 10.089 |  | --> |  | Transmission Source | MACETOWN |  | 53.4109 | -6.409
Dalton [T141] | DALTON (909000) 110 kV STATION | Dalton [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.5 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 47.5 | 12.5 | 0 |  | --> |  | Transmission Source | DALTON |  | 53.7163 | -8.9756
Dalton [T142] | DALTON (909000) 110 kV STATION | Dalton [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 20.5 | 0 | 0 |  | --> |  | Transmission Source | DALTON |  | 53.7163 | -8.9756
Derryiron [T141] | DERRYIRON (724000) 110 kV STATION | Derryiron [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 37.5 | 22.4 | 0 |  | --> |  | Transmission Source | DERRYIRON |  | 53.3508 | -7.2002
Drumline [T141,T142] | DRUMLINE (629000) 110 kV STATION | Drumline [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0.4 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 19.7 | 4.9 | 0 |  | --> |  | Transmission Source | DRUMLINE |  | 52.7309 | -8.8496
Drybridge [T141,T142] | DRYBRIDGE (064000) 110 kV STATION | Drybridge [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 80.6 | 0 | 0 |  | --> |  | Transmission Source | DRYBRIDGE |  | 53.7274 | -6.394
Drybridge [T143] | DRYBRIDGE (064000) 110 kV STATION | Drybridge [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 0 | 59.8 | 0 |  | --> |  | Transmission Source | DRYBRIDGE |  | 53.7274 | -6.394
Killoteran [T101,T102] | KILLOTERAN (911000) 110 kV STATION | Killoteran [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.6 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 0.6 | 19.4 | 9.603 |  | --> |  | Transmission Source | KILLOTERAN |  | 52.2539 | -7.1523
Crory [T122] | CRORY (473000) 110 kV STATION | Crory [T122] | 110 kV | _ | MV | 1x31.5 MVA @ 20 kV | 31.5 | --> | 28.35 | 28.4 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 15.6 | 14.3 | 0 |  | --> |  | Transmission Source | CRORY |  | 52.569 | -6.5458
Carlow [T141,T142] | CARLOW (669000) 110 kV STATION | Carlow [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 22 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 105.5 | 0 | 0 |  | --> |  | Transmission Source | CARLOW |  | 52.8373 | -6.848
Carrowbeg [T142] | CARROWBEG (699000) 110 kV STATION | Carrowbeg [T142] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 7.9 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 7.1 | 13.4 | 0 |  | --> |  | Transmission Source | CARROWBEG |  | 53.8048 | -9.5016
Castlebar [T141,T142] | CASTLEBAR (520000) 110 kV STATION | Castlebar [T141,T142] | 110 kV | _ | 38 kV | 1x31.5,1x63 MVA @ 38 kV | 94.5 | --> | 66.15 | 25 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 61.3 | 0 | 0 |  | --> |  | Transmission Source | CASTLEBAR |  | 53.8701 | -9.2747
Castleview [T101,T102] | CASTLEVIEW (600000) 110 kV STATION | Castleview [T101,T102] | 110 kV | _ | MV | 2x31.5 MVA @ 10 kV | 63 | --> | 47.25 | 6.8 | N/A, consult Eirgrid |  | --> | 38.9 | 14.9625 | 19.9 | 5 | 15.486 |  | --> |  | Transmission Source | CASTLEVIEW |  | 51.8922 | -8.3586
Cathaleens Fall [T141] | CATHALEENS FALL (143000) 110 kV STATION | Cathaleens Fall [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 22.05 | 1.6 | N/A, consult Eirgrid |  | --> | 20.9 | 0 | 94.8 | 0 | 0 |  | --> |  | Transmission Source | CATHALEENS FALL |  | 54.4967 | -8.1841
Cauteen [T141] | CAUTEEN (573000) 110 kV STATION | Cauteen [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 60.7 | 0 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
Cauteen [T142] | CAUTEEN (573000) 110 kV STATION | Cauteen [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 66 | 0 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
Carrickmines [T2101,T2103,T2104] | CARRICKMINES (649000) 220 kV STATION | Carrickmines [T2101,T2103,T2104] | 220 kV | _ | 110 kV | 3x250 MVA @ 110 kV | 750 | --> | 525 | 198.6 | N/A, consult Eirgrid |  | --> | 712.5 | 0 | 81.5 | 542.8 | 0 |  | --> |  | Transmission Source | CARRICKMINES |  | 53.2549 | -6.1921
Cauteen [T143] | CAUTEEN (573000) 110 kV STATION | Cauteen [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 0 | 59.8 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
Cauteen [T144] | CAUTEEN (573000) 110 kV STATION | Cauteen [T144] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.6 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 52 | 8.1 | 0 |  | --> |  | Transmission Source | CAUTEEN |  | 52.5293 | -8.1839
Corderry [T121] | CORDERRY (972000) 110 kV STATION | Corderry [T121] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 17.6 | N/A, consult Eirgrid |  | --> | 19 | 0 | 38.8 | 0 | 0 |  | --> |  | Transmission Source | CORDERRY |  | 54.204 | -8.1807
Charleville [T141] | CHARLEVILLE (456000) 110 kV STATION | Charleville [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 53.9 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 51.4 | 8.8 | 0 |  | --> |  | Transmission Source | CHARLEVILLE |  | 52.325 | -8.7025
Cordal [T141] | CORDAL (865000) 110 kV STATION | Cordal [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.3 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 57.8 | 2.4 | 0 |  | --> |  | Transmission Source | CORDAL |  | 52.2248 | -9.2712
Carlow [T121] | CARLOW (669000) 110 kV STATION | Carlow [T121] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 0 | 59.8 | 0 |  | --> |  | Transmission Source | CARLOW |  | 52.8373 | -6.848
Charleville [T142] | CHARLEVILLE (456000) 110 kV STATION | Charleville [T142] | 110 kV | _ | 38 kV | 1x30 MVA @ 38 kV | 30 | --> | 27 | 7.9 | N/A, consult Eirgrid |  | --> | 28.5 | 0 | 44.6 | 0 | 0 |  | --> |  | Transmission Source | CHARLEVILLE |  | 52.325 | -8.7025
Cloghboola [T122] | CLOGHBOOLA (875000) 110 kV STATION | Cloghboola [T122] | 110 kV | _ | MV | 1x63 MVA @ 20 kV | 63 | --> | 56.7 | 54.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 54.5 | 5.6 | 0 |  | --> |  | Transmission Source | CLOGHBOOLA |  | 52.3209 | -9.4472
Cahir [T141,T142] | CAHIR (668000) 110 kV STATION | Cahir [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 18.2 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 47.9 | 0 | 0 |  | --> |  | Transmission Source | CAHIR |  | 52.3824 | -7.8857
Cloon [T122] | CLOON (907000) 110 kV STATION | Cloon [T122] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 18 | N/A, consult Eirgrid |  | --> | 19 | 0 | 0 | 19 | 0 |  | --> |  | Transmission Source | CLOON |  | 53.4879 | -8.8539
Butlerstown [T141,T142] | BUTLERSTOWN (667000) 110 kV STATION | Butlerstown [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 68.7 | 0 | 0 |  | --> |  | Transmission Source | BUTLERSTOWN |  | 52.2225 | -7.1624
Cloon [T141,T142] | CLOON (907000) 110 kV STATION | Cloon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 10.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 36.2 | 0 | 0 |  | --> |  | Transmission Source | CLOON |  | 53.4879 | -8.8539
College Park [T101,T102,T103] | COLLEGE PARK (670000) 110 kV STATION | College Park [T101,T102,T103] | 110 kV | _ | MV | 3x20 MVA @ 10 kV | 60 | --> | 54 | 0 | N/A, consult Eirgrid |  | --> | 57 | 9.5 | 10 | 21.4 | 10.104 |  | --> |  | Transmission Source | COLLEGE PARK |  | 53.4148 | -6.3727
Coolroe [T121,T122] | COOLROE (131000) 110 kV STATION | Coolroe [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 17.5 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 2.7 | 17.9 | 9.578 |  | --> |  | Transmission Source | COOLROE |  | 51.8881 | -8.631
Dungarvan [T141,T142] | DUNGARVAN (675000) 110 kV STATION | Dungarvan [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 64.4 | 0 | 0 |  | --> |  | Transmission Source | DUNGARVAN |  | 52.1109 | -7.6481
Carrick On Shannon [T141,T142] | CARRICK ON SHANNON (074000) 110 kV STATION | Carrick On Shannon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 11.5 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 31.4 | 0 | 0 |  | --> |  | Transmission Source | CARRICK ON SHANNON |  | 53.9295 | -8.1261
Kilkenny [T141,T142] | KILKENNY (683000) 110 kV STATION | Kilkenny [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 10.4 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 84.6 | 0 | 0 |  | --> |  | Transmission Source | KILKENNY |  | 52.6427 | -7.1662
Griffinrath [T141,T142] | GRIFFINRATH (681000) 110 kV STATION | Griffinrath [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 96.3 | 0 | 0 |  | --> |  | Transmission Source | GRIFFINRATH |  | 53.3448 | -6.5619
Kilpaddoge [T122] | KILPADDOGE (921000) 220 kV STATION | Kilpaddoge [T122] | 220 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 17.4 | N/A, consult Eirgrid |  | --> | 19 | 0 | 18 | 1.3 | 0 |  | --> |  | Transmission Source | KILPADDOGE |  | 52.5867 | -9.3854
Hartnetts Cross [T121,T422] | HARTNETTS CROSS (939000) 110 kV STATION | Hartnetts Cross [T121,T422] | 110 kV | _ | MV | 1x10,1x20 MVA @ 20 kV | 30 | --> | 22.5 | 18.8 | N/A, consult Eirgrid |  | --> | 12.4 | 9.5 | 4.8 | 6.9 | 9.507 |  | --> |  | Transmission Source | HARTNETTS CROSS |  | 51.9028 | -8.9308
Ikerrin [T141] | IKERRIN (682000) 110 kV STATION | Ikerrin [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 52.3 | 0 | 0 |  | --> |  | Transmission Source | IKERRIN |  | 52.9228 | -7.7875
Binbane [T141,T142] | BINBANE (666000) 110 kV STATION | Binbane [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 66.6 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 96.6 | 0 | 0 |  | --> |  | Transmission Source | BINBANE |  | 54.7253 | -8.2757
Inchicore City 220/110 kV [T2102,T2104] | INCHICORE 220KV (964000) 220 kV STATION | Inchicore City 220/110 kV [T2102,T2104] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 113 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 57.7 | 171.1 | 0 |  | --> |  | Transmission Source | INCHICORE 220KV |  | 53.3313 | -6.3371
Bellacorick [T142] | BELLACORICK (896000) 110 kV STATION | Bellacorick [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 33.9 | 26.2 | 0 |  | --> |  | Transmission Source | BELLACORICK |  | 54.1261 | -9.5683
Bellacorick [T141] | BELLACORICK (896000) 110 kV STATION | Bellacorick [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 51.8 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 46.4 | 12.7 | 0 |  | --> |  | Transmission Source | BELLACORICK |  | 54.1261 | -9.5683
Bellacorick [T122] | BELLACORICK (896000) 110 kV STATION | Bellacorick [T122] | 110 kV | _ | MV | 1x10 MVA @ 20 kV | 10 | --> | 9 | 7.6 | N/A, consult Eirgrid |  | --> | 9.5 | 0 | 10.6 | 0 | 0 |  | --> |  | Transmission Source | BELLACORICK |  | 54.1261 | -9.5683
Dundalk [T141,T142] | DUNDALK (062000) 110 kV STATION | Dundalk [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 21 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 96.6 | 0 | 0 |  | --> |  | Transmission Source | DUNDALK |  | 54.0085 | -6.4194
Kilbarry [T142,T143] | KILBARRY (021000) 110 kV STATION | Kilbarry [T142,T143] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 55.7 | 1.3 | 0 |  | --> |  | Transmission Source | KILBARRY |  | 51.926 | -8.4858
Glenree [T142] | GLENREE (894000) 110 kV STATION | Glenree [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 64.8 | 0 | 0 |  | --> |  | Transmission Source | GLENREE |  | 54.1135 | -9.0022
Doon [T141,T142] | DOON (674000) 110 kV STATION | Doon [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 11.6 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 56.9 | 0 | 0 |  | --> |  | Transmission Source | DOON |  | 52.3931 | -7.6602
Barrymore [T141] | BARRYMORE (905000) 110 kV STATION | Barrymore [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 67.8 | 0 | 0 |  | --> |  | Transmission Source | BARRYMORE |  | 52.0912 | -8.2595
Barnahely [T141,T142] | BARNAHELY (772000) 110 kV STATION | Barnahely [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 20.5 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 22.7 | 6.1 | 0 |  | --> |  | Transmission Source | BARNAHELY |  | 51.8251 | -8.3485
Barnahely [T121,T122,T124] | BARNAHELY (772000) 110 kV STATION | Barnahely [T121,T122,T124] | 110 kV | _ | MV | 3x20 MVA @ 20 kV | 60 | --> | 54 | 18.2 | N/A, consult Eirgrid |  | --> | 57 | 9.5 | 13.3 | 26 | 9.811 |  | --> |  | Transmission Source | BARNAHELY |  | 51.8251 | -8.3485
Banoge [T121,T122] | BANOGE (809000) 110 kV STATION | Banoge [T121,T122] | 110 kV | _ | MV | 2x20 MVA @ 20 kV | 40 | --> | 30 | 17.8 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 16.4 | 5.2 | 9.548 |  | --> |  | Transmission Source | BANOGE |  | 52.6528 | -6.2647
Midleton [T101,T102] | MIDLETON (775000) 110 kV STATION | Midleton [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 11.2 | 4.7 | 9.827 |  | --> |  | Transmission Source | MIDLETON |  | 51.9336 | -8.1835
Midleton [T141] | MIDLETON (775000) 110 kV STATION | Midleton [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 0 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 30 | 0 | 0 |  | --> |  | Transmission Source | MIDLETON |  | 51.9336 | -8.1835
Booltiagh [T143] | BOOLTIAGH (887000) 110 kV STATION | Booltiagh [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 64.1 | 0 | 0 |  | --> |  | Transmission Source | BOOLTIAGH |  | 52.7667 | -9.2556
Booltiagh [T141] | BOOLTIAGH (887000) 110 kV STATION | Booltiagh [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 54.9 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 57.2 | 2.9 | 0 |  | --> |  | Transmission Source | BOOLTIAGH |  | 52.7667 | -9.2556
Kilbarry [T101,T43] | KILBARRY (021000) 110 kV STATION | Kilbarry [T101,T43] | 110 kV | _ | MV | 1x15,1x20 MVA @ 10 kV | 35 | --> | 26.25 | 0 | N/A, consult Eirgrid |  | --> | 23.3 | 0 | 3.1 | 14.8 | 0 |  | --> |  | Transmission Source | KILBARRY |  | 51.926 | -8.4858
Lanesboro [T141] | LANESBORO (686000) 110 kV STATION | Lanesboro [T141] | 110 kV | _ | 38 kV | 1x31.5 MVA @ 38 kV | 31.5 | --> | 28.35 | 9.2 | N/A, consult Eirgrid |  | --> | 29.9 | 0 | 25.6 | 0 | 0 |  | --> |  | Transmission Source | LANESBORO |  | 53.6689 | -7.9718
Dungarvan [T143] | DUNGARVAN (675000) 110 kV STATION | Dungarvan [T143] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 37.4 | 22.4 | 0 |  | --> |  | Transmission Source | DUNGARVAN |  | 52.1109 | -7.6481
Lisheen [T142] | LISHEEN (792000) 110 kV STATION | Lisheen [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 39.6 | 20.5 | 0 |  | --> |  | Transmission Source | LISHEEN |  | 52.7447 | -7.6715
Dunmanway [T124] | DUNMANWAY (676000) 110 kV STATION | Dunmanway [T124] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 18 | N/A, consult Eirgrid |  | --> | 19 | 0 | 13.8 | 5.5 | 0 |  | --> |  | Transmission Source | DUNMANWAY |  | 51.7167 | -9.0773
Lisdrum [T141,T142] | LISDRUM (624000) 110 kV STATION | Lisdrum [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 5.9 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 61.8 | 0 | 0 |  | --> |  | Transmission Source | LISDRUM |  | 54.2488 | -6.9279
Limerick [T141,T142] | LIMERICK (688000) 110 kV STATION | Limerick [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 21.7 | 22.4 | 0 |  | --> |  | Transmission Source | LIMERICK |  | 52.6325 | -8.647
Dunmanway [T141,T142] | DUNMANWAY (676000) 110 kV STATION | Dunmanway [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 43.9 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 77.9 | 0 | 0 |  | --> |  | Transmission Source | DUNMANWAY |  | 51.7167 | -9.0773
Liberty Street [T101,T102] | LIBERTY STREET (309000) 110 kV STATION | Liberty Street [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 7.9 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 1.3 | 17.3 | 9.666 |  | --> |  | Transmission Source | LIBERTY STREET |  | 51.9015 | -8.4693
Letterkenny [T141,T142] | LETTERKENNY (687000) 110 kV STATION | Letterkenny [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 13.2 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 131.3 | 0 | 0 |  | --> |  | Transmission Source | LETTERKENNY |  | 54.9284 | -7.7024
Ennis [T101,T102] | ENNIS (677000) 110 kV STATION | Ennis [T101,T102] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 13.1 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 12.5 | 9 | 9.55 |  | --> |  | Transmission Source | ENNIS |  | 52.8555 | -8.9311
Great Island [T141,T142] | GREAT ISLAND (680000) 220 kV STATION | Great Island [T141,T142] | 220 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 21.5 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 92.1 | 0 | 0 |  | --> |  | Transmission Source | GREAT ISLAND |  | 52.2837 | -6.9761
Finglas Urban 220/110 kV [T2103,T2104] | FINGLAS (318000) 220 kV STATION | Finglas Urban 220/110 kV [T2103,T2104] | 220 kV | _ | 110 kV | 2x250 MVA @ 110 kV | 500 | --> | 350 | 87.1 | N/A, consult Eirgrid |  | --> | 308.8 | 0 | 30.4 | 222.7 | 0 |  | --> |  | Transmission Source | FINGLAS |  | 53.4075 | -6.3161
Gortawee [T142] | GORTAWEE (815000) 110 kV STATION | Gortawee [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 44.4 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 9.1 | 46.5 | 0 |  | --> |  | Transmission Source | GORTAWEE |  | 54.1214 | -7.5927
Galway 110kv [T102,T103] | GALWAY 110KV (679000) 110 kV STATION | Galway 110kv [T102,T103] | 110 kV | _ | MV | 2x20 MVA @ 10 kV | 40 | --> | 30 | 0 | N/A, consult Eirgrid |  | --> | 24.7 | 9.5 | 3.3 | 14.9 | 9.686 |  | --> |  | Transmission Source | GALWAY 110KV |  | 53.2951 | -9.0181
Galway 110kv [T141,T142] | GALWAY 110KV (679000) 110 kV STATION | Galway 110kv [T141,T142] | 110 kV | _ | 38 kV | 2x63 MVA @ 38 kV | 126 | --> | 88.2 | 0 | N/A, consult Eirgrid |  | --> | 77.8 | 0 | 49.2 | 0 | 0 |  | --> |  | Transmission Source | GALWAY 110KV |  | 53.2951 | -9.0181
Knockearagh [T141,T142] | KNOCKEARAGH (685000) 110 kV STATION | Knockearagh [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0.8 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 42.3 | 0 | 0 |  | --> |  | Transmission Source | KNOCKEARAGH |  | 52.08 | -9.4423
Garrow [T121] | GARROW (992000) 110 kV STATION | Garrow [T121] | 110 kV | _ | MV | 1x15 MVA @ 20 kV | 15 | --> | 13.5 | 13.3 | N/A, consult Eirgrid |  | --> | 14.2 | 0 | 15 | 0 | 0 |  | --> |  | Transmission Source | GARROW |  | 52.0112 | -9.1445
Garvagh [T141] | GARVAGH (570000) 110 kV STATION | Garvagh [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.2 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 34 | 26.2 | 0 |  | --> |  | Transmission Source | GARVAGH |  | 54.1612 | -8.1779
Glenlara [T141] | GLENLARA (936000) 110 kV STATION | Glenlara [T141] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 56.1 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 40.8 | 19.3 | 0 |  | --> |  | Transmission Source | GLENLARA |  | 52.2035 | -9.0207
Glenlara [T142] | GLENLARA (936000) 110 kV STATION | Glenlara [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 38.7 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 54.3 | 0.2 | 0 |  | --> |  | Transmission Source | GLENLARA |  | 52.2035 | -9.0207
Glenree [T121] | GLENREE (894000) 110 kV STATION | Glenree [T121] | 110 kV | _ | MV | 1x20 MVA @ 20 kV | 20 | --> | 18 | 17.7 | N/A, consult Eirgrid |  | --> | 19 | 0 | 17.2 | 2.2 | 0 |  | --> |  | Transmission Source | GLENREE |  | 54.1135 | -9.0022
Kilteel [T141,T142] | KILTEEL (684000) 110 kV STATION | Kilteel [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 45.5 | 0 | 0 |  | --> |  | Transmission Source | KILTEEL |  | 53.2569 | -6.53
Boggeragh [T142] | BOGGERAGH (572000) 110 kV STATION | Boggeragh [T142] | 110 kV | _ | 38 kV | 1x63 MVA @ 38 kV | 63 | --> | 56.7 | 55.6 | N/A, consult Eirgrid |  | --> | 59.8 | 0 | 43.4 | 16.8 | 0 |  | --> |  | Transmission Source | BOGGERAGH |  | 52.0315 | -8.8926
Ennis [T141,T142] | ENNIS (677000) 110 kV STATION | Ennis [T141,T142] | 110 kV | _ | 38 kV | 2x31.5 MVA @ 38 kV | 63 | --> | 44.1 | 0 | N/A, consult Eirgrid |  | --> | 38.9 | 0 | 47.3 | 0 | 0 |  | --> |  | Transmission Source | ENNIS |  | 52.8555 | -8.9311
_LV Header | _ESB Networks Capacity Heat Map Publication. LV asset data from Aug 2025. Load data derived from revenue metering Jan 25, Generation and demand commitments up to 08 Oct 2025. |  | Report compiled 31/10/2025

## Disclaimer
Disclaimer
This capacity heatmap provides an indication of the available transformer capacity at substations. The map indicates transformer capacity only. It does not guarantee the same capacity is available in the upstream networks. The heatmap is a snapshot, representing a moment in time, of a continually changing network system. It cannot be relied upon in isolation to assess the viability of a connection to a premises. Whilst we use reasonable endeavours to ensure that the capacity map and related information is accurate, we do not warrant, and do not accept any responsibility or liability for, the accuracy or completeness of the content or for any consequence or loss which may arise from reliance on the capacity heatmap or related information. The data provided must be considered in conjunction with explanations in ‘Important details about the Heatmap’ section. The available capacity figures will be periodically updated, and you should check the webpage routinely for the latest version. The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.
The legal disclaimer terms and conditions for use of our website apply to the capacity heatmap and related information.

## Notes & FAQs
What is the Available Capacity Heatmap?
At ESB Networks we are committed to improving the experience of our customers. As part of this commitment, we have developed our interactive Capacity Heatmap. It contains capacity information on all our 3-phase LV, MV and HV DSO substations. It provides an interface that enables the easy identification of potential transformer capacity in the vicinity of your site. An excel file is available to download from the download section on this page.
We envisage that the map will be used to inform initial discussion between ourselves and our customers. Although we have taken steps to ensure the accuracy of the map, it cannot replicate the level of accuracy provided by the detailed assessment carried out as part of the formal application process. Please read the accompanying notes and important details section to understand what the map does and does not provide.
If the Available Capacity Heatmap indicates that there is insufficient capacity to accommodate your development, please contact us to discuss the next steps. We will always work with customers to find solutions.
Generation customer queries should be directed to DSOgenerators@esb.ie.
Demand customer queries should be directed to innovationfeedback@esbnetworks.ie.
Map Preparation Date: 15 Oct 2025
What can I learn from the map?
The Capacity Heatmap provides an indication of available transformer capacity, at substation level and at all voltage levels, for new demand and generation customers. It is a user-friendly and interactive map that shows how much demand or generation could be added into a substation without reinforcement. It empowers potential customers and helps them have a better understanding as to where connection is possible.
In the map HV substations are classified into three categories corresponding to the connection voltage i.e., 110kV, 38kV or Medium Voltage (MV).
The map also gives the location and available demand capacity for all 3 phase Medium Voltage to Low Voltage (MV/LV) substations.The LV data capacity is in the range of customers looking to connect demand less than 500kVA. This scale would be of most interest to small businesses, farming, and small community projects. If the indicated capacity meets your needs, then you can be reasonably assured no new substation development is required. However, site specific detail such as proximity and physical access could still be an overarching limiting factor.
Available capacity for LV generation is not specified because of additional considerations that are mainly site specific, see point No 5 below.
The pins on the map are colour coded by ranges of available capacity which can be separately filtered. Filtering can also be independently applied by voltage level.
How do I know which substation to review for my site?
We recommend using the Location Finder tool by clicking on the icon to the right of the map. Look for this symbol
Here you can type your place name, or Eircode and it will show the stations closest to the location. Please ensure you have selected the relevant connection voltages and available ranges in the filters section on the left or it may not return results.
For LV substations, use the map to locate your own site and then find the nearest LV substation to it. Typically, a substation must be within 300m or less to be suitable for connecting at LV otherwise a new substation must be provided nearer to you. The pop-up box also shows the parent HV substation that supplies the LV substation. Also check this for available capacity.
For MV connection (greater than or equal to 500kVA) locate the nearest LV station as in the previous paragraph and the parent capacity will also be shown.
Does the Capacity Available value mean I can connect the amount shown?
Not necessarily. There are many site-specific issues and detailed technical checks that must be completed to give that assurance and they can only be completed as part of an application. Below are some of the factors that influence the answer:
Am I the first to apply? All connection offers are provided on a first come first served basis so other customers may have applied ahead and used a proportion of the available capacity.
Proximity to the substation: typically for LV, you must be a maximum of 300m from the substation and much closer for the higher level of LV capacity. For 38kV and MV circuits, capacity is not assured, and new lines may need to be constructed or existing one upgraded.
HV substations are sometimes a parent supply to other downstream substations. In cases where the parent substation has limited capacity then all child substations will be curtailed by that limit. Furthermore, if just one child substation absorbs all the available capacity then that will result in no spare capacity for the other child stations. This form of interaction requires continual re-assessment to ensure no system overload occur.
A similar interaction can occur on circuits where apparently available capacity cannot be contracted because of customer increases on other circuits which share a common source with a capacity limit.
Generation, at all voltages, is particularly onerous due to the limited latitude to accommodate the associated voltage rise. This has an acute effect on the necessary proximity to a substation.
For ECP generation connections, the capacity available may differ depending on customers accepting or withdrawing their connection study offers during each batch of studies.
Capacity available is also influenced by disturbing load such as flicker and harmonic emissions.
The stated available capacity may exceed the maximum rating for an individual network component for example standard circuit connection capacity. In such cases, aconnection will be constrained by the network component and therefore will not be able to avail of the full value indicated.
How has the data been produced?
The data has been produced by an analysis of the available transformer capacity, existing loads, and contractual commitments to new customers. Detailed assessment aspects, necessary for connection offers, such as upstream circuit capacity and service contingency requirement are not included.
What are the available capacity figures based on?
Station capacity, as of Oct 2025.
Base load information comes from Special Load Readings, 2024/2025 which include 2024 Summer Valley load used in the Generation capacity preparation.
Demand calculation incorporates demand contracts and offers up to end Aug 2025
Generation calculations incorporates generation contracts and offers up to early Oct 2025.
How often is the Network Capacity Map updated?
As part of ESB Networks strategy, the objective is to update the map quarterly.
Are the substation locations accurate?
HV substation locations are only indicative. The exact locations of MV/LV substations are provided.
How long does a connection take?
In general, where HV substation capacity is adequate, MV connections up to a maximum of 10MVA will entail construction of overhead line or new underground cable network, associated civil works and minor station works only and typically do not require planning permission. These would not be expected to take longer than 6-9 months. However, any instances requiring significant station work such as the installation of a new transformer or MV switchgear will require increased time, and possibly planning permission or necessary permits and would typically be expected to take approximately 2-3 years.
LV connections alone are usually completed within 6 months of application.
Generation connection information: Enduring Connection Policy (ECP) (esbnetworks.ie)
What other important points should be kept in mind about the data in the map?
The map does not replace a full formal application in determining network capacity.
The map does not provide capacity figures for the final connection from HV substation to customer premises. Such connections will need to tap into the existing MV (10kV or 20kV) network. Capacity availability is subject to many variables and an assessment is necessary.
In some cases, the available capacity shown in the Demand Map may already be contracted to individual customers but is not currently being fully utilised.
The information provided in the Generation and Demand Maps does not guarantee the same capacity is available in the upstream DSO networks.
Any increased load on the Distribution System will impact on the upstream Transmission System and reinforcements may be required on the Transmission System in order to cater for these loads. This will be separately assessed by the TSO.
An individual connection cannot be greater than the capacity of an individual transformer. In the case of 38kV and MV, the available capacity shown is the total of all transformers in the substation at the respective voltage. Therefore, full capacity utilisation may, sometimes, only be possible with more than one connection. (Note, a single premises cannot have more than one connection).