## NC6 Bulk Upload Template
ESB Microgeneration Notification - NC6
Project/Site Name:
Submission Date:
Total Units:
Revision:
Important: For correct upload functionality, please enter all the required inputs. Do not change the template.
Geneneral - Site Address | [9 empty] | NC6 | [19 empty] | Protection Settings
[10 empty] | Phase | Energy Source |  | Manufacturer |  | Manufacturer Model/ Reference No. |  | Inverter Capacity (kVA) |  | Rated Current (Amps) as per Type Test |  | Generator Capacity (kVA) |  | Storage Capacity (kVA) |  | Will interface have Type Test certification to DTIS-230206-BRL? |  | Were Interface Settings Installed to DTIS-230206-BRL? |  | First Micro-generator at these premises? | When was the Microgeneration Unit Installed? |  | What kind of Type Test Certificate do you have? |  | Have the protection settings as per DTIS-230206-BRL been applied?
Customer Name / Company Name | Customer's Email Address | MPRN | House Name / Number | Street Address | Townland / Area | Townland / City | County | Eircode (Optional) | Total Inverter Capacity (kVA) | Applicable for both units | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | 1st unit | 2nd unit | Applicable for both units | 1st Unit | 2nd Unit | 1st Unit | 2nd Unit | Applicable for both units
Required Customer Name / Company Name | Required Provide Customer's Email Address. If not applicable, enter N/A | Required Please provide the 11 digit MPRN number for existing connection | Required Enter your house name / number | Required Enter your street address | Required Enter your townland or area | Required Enter your townland or city | Required Enter your county | Enter your Eircode if you know it | Required Enter the combined capacity of all existing or new Inverters | Required Single or Three Phase | Required Enter Energy Source for the 1st microgeneration Unit Energy Source P - Solar/Photovoltaic W - Wind H - Hydro C - Combined heating and power B - Battery O - Other | Enter Energy Source for the 2nd microgeneration Unit (if applicable) Energy Source P - Solar/Photovoltaic W - Wind H - Hydro C - Combined heating and power B - Battery O - Other | Required Enter Manufacturer for the 1st microgeneration unit | Enter Manufacturer for the 2nd microgeneration unit (if applicable) | Required Enter Model Number for the 1st microgeneration unit | Enter Model Number for the 2nd microgeneration unit (if applicable) | Required Enter Inverter Capacity for the 1st microgeneration unit. Not to exceed 6 kVA on Single Phase or 11 kVA for Three Phase | Enter Inverter Capacity for the 2nd microgeneration unit (if applicable). Not to exceed 6 kVA on Single Phase or 11 kVA for Three Phase | Required Enter Rated Current for the 1st microgeneration unit. Not to exceed 25A on Single Phase equipment or 16A/phase on three phase equipment | Enter Rated Current for the 2nd microgeneration unit (if applicable). Not to exceed 25A on Single Phase equipment or 16A/phase on three phase equipment | Required Installed behind each inverter. Enter Generator Capacity in kVA for the 1st microgeneration unit | Installed behind each inverter. Enter Generator Capacity in kVA for the 2nd microgeneration unit (if applicable) | Required Installed behind each inverter. Enter Storage Capacity in kVA for the 1st microgeneration unit. If you do not have Storage, enter 0 | Installed behind each inverter. Enter Storage Capacity in kVA for the 2nd microgeneration unit (if applicable). If you do not have Storage, enter 0. | Required Please Confirm for the 1st microgeneration unit - Yes or No | Please Confirm for the 2nd microgeneration unit (if applicable) - Yes or No | Required Please Confirm for the 1st microgeneration unit - Yes or No | Please Confirm for the 2nd microgeneration unit (if applicable) - Yes or No | Required Please Confirm - Yes or No | Required Before January 28th 2022 or After January 28th 2022 | Before January 28th 2022 or After January 28th 2022 | Required EN 50549 (Settings set by Installer) or EN 50438 (Settings set by Manufacturer) | EN 50549 (Settings set by Installer) or EN 50438 (Settings set by Manufacturer) | Required Please confirm. Refer to additional tabs/ DTIS-230206-BRL Conditions Governing the Connection and Operation of Micro-Generation (esbnetworks.ie)

## Protection Settings Post Jan 22
Parameter | Trip Setting | Clearance Time | Note
Pre I.S. EN 50549-1 Single Stage Voltage Setting | 269 V / 468 V | 0.7 s
I.S EN 50549-1 Two Stage Voltage Settings Stage 1 | 269 V / 468 V | 70 s
I.S EN 50549-1 Two Stage Voltage Settings Stage 2 | 281 V / 488 V | 0.7 s
Under Voltage | 191 V / 332 V | 0.7 s
Over Frequency | 52 Hz | 0.5 s | For relays that have a setting step of 0.1 Hz then the frequency should be set to 52.1 Hz and 49.9 Hz respectively.
Under Frequency | 47 Hz | 0.5s | For relays that have a setting step of 0.1 Hz then the frequency should be set to 52.1 Hz and 49.9 Hz respectively.
ROCOF | 1.0 Hz/s | 0.6 s | Reset interval should be set to >0.6 seconds to detect step changes
Vector Shift | Not Permitted
Important Note: No deviations from the protection settings in the above Table shall be allowed without permission in writing from ESB Networks. If a deviation exists, please provide correspondence from ESB Networks confirming acceptance of this deviation to networkservicesbureau@esb.ie.
Conditions Governing the Connection and Operation of MicroGeneration

## Protection Settings Pre Jan 22
Parameter | Trip Setting | Clearance Time | Note
Over Voltage | 230 V + 10% | 0.5 s
Under Voltage | 230 V - 10% | 0.5 s
Over Frequency | 52 Hz | 0.5 s | For relays that have a setting step of 0.1 Hz then the frequency should be set to 52.1 Hz and 49.9 Hz respectively.
Under Frequency | 47 Hz | 20 s | For relays that have a setting step of 0.1 Hz then the frequency should be set to 52.1 Hz and 49.9 Hz respectively.
ROCOF (where used) | 1.0 Hz/s | 0.6 s | Reset interval should be set to >0.6 seconds to detect step changes
Vector Shift (where used) | 6 degrees | 0.5 s
Important Note: No deviations from the protection settings in the above Table shall be allowed without permission in writing from ESB Networks. If a deviation exists, please provide correspondence from ESB Networks confirming acceptance of this deviation to networkservicesbureau@esb.ie.
Conditions Governing the Connection and Operation of MicroGeneration

## Input Options (hidden)
Protection Settings | Phase | Energy Source | Installed | Certificate
Yes | Single Phase | P | After January 28, 2022 | EN 50549 Settings set by Installer
No | Three Phase | W | Before January 28, 2022 | EN 50438 Settings set by Manufacturer
H
C
B
O